## Huntington Beach North (MFL) 1
Features List
Crimson Pipeline (Crimson Midstream)
NPS6x8 CPIG ( MFL/CAL/IMU ) Metal Loss Inspection
CSFM 825 (Huntington Beach Crude System 6”)
CSFM 1305 (#3-6" Dry Gas Line)
CSFM 39 (HB – 8” Crude Oil Line)
|  |  |  | From: CRC Huntington Beach, To: Northam Station |  |  |  | Projection: | UTM
|  |  |  | ( 10.59 recorded miles out of 15.75 miles ) |  |  |  | Datum: | World Geodetic System 1984
450710_08A |  |  |  | Inspection Date: June 20, 2018 |  |  |  | Zone: | 11
Issue_A_Section 1 |  |  |  | Report Release Date: September 27, 2018 |  |  |  | Central Meridian: | -117
BHI Identifier | Pipeline Feature | INT/EXT (ID/OD) | Odometer (ft) | Distance to Next Pipeline Feature (ft) | W.T. (in) | Pipe Grade (psi) | Pipe Description | Pipe Diameter (in) | MOP (psi) | Depth [%] | Depth [in] | Length [in] | Width [in] | O'Clock Orientation [hh:mm] | mB31.G Burst (psi) | ERF | Eff. Depth (%) | Eff. Length (in) | Eff. Area Burst (psi) | Upstream (U/S) Reference Name | Distance To U/S Reference [ft] | Downstream (D/S) Reference Name | Distance From D/S Reference [ft] | Distance to U/S Weld (ft) | Distance to D/S Weld (ft) | Length, 2nd U/S Joint (ft) | Length, U/S Joint (ft) | Length, Defect Joint (ft) | Defect Joint Number | Length, D/S Joint (ft) | Length, 2nd D/S Joint (ft) | XYZ Information NAD 83 Latitude (°) | XYZ Information NAD 83 Longitude (°) | XYZ Information NAVD 88 Elevation (ft) | Comments
AGM 1 | Above Ground Marker |  | -0.56 | 0 | 0.219 | 35000 | ERW | 6.625 | 715 | [12 empty] | AGM 1 | 1752.33 |  | 0 |  |  |  |  | 1.38 | 3.16 | 33.6722 | -118.0193 | 39.674 | Launcher Door 10' 6: U/S of Launcher Valve
GWD 10 | Girth Weld |  | -0.56 | 0.65 | 0.219 | 35000 | ERW | 8.625 | 715 | [10 empty] | Launcher Door | 0 | AGM 1 | 1752.33 |  | 1.38 |  |  | 1.38 | 10 | 3.16 | 4.9 | 33.6722 | -118.0193 | 39.674 | First Recorded Girth Weld
TEE 1 | Tee |  | 0.08 | 0.73 | 0.219 | 35000 | ERW | 8.625 | 715 |  |  | 9.863 | 9.863 | 3:00 | [5 empty] | Launcher Door | 0.65 | AGM 1 | 1751.68 | 0.65 | 0.73 |  |  | 1.38 | 10 | 3.16 | 4.9 | 33.6722 | -118.0193 | 39.677 | Start Section CSFM 825
GWD 20 | Girth Weld |  | 0.82 | 1.8 | 0.219 | 35000 | ERW | 8.625 | 715 | [10 empty] | Launcher Door | 1.38 | AGM 1 | 1750.95 | 1.38 | 3.16 |  | 1.38 | 3.16 | 20 | 4.9 | 3.27 | 33.6722 | -118.0193 | 39.664
BND 1 | Bend |  | 2.62 | 1.36 | 0.219 | 35000 | ERW | 8.625 | 715 |  |  | 39.077 | [7 empty] | Launcher Door | 3.18 | AGM 1 | 1749.15 | 1.8 | 1.36 |  | 1.38 | 3.16 | 20 | 4.9 | 3.27 | 33.6722 | -118.0193 | 39 | 3.0D 90.3 deg right turn over bend
GWD 30 | Girth Weld |  | 3.97 | 4.9 | 0.219 | 35000 | ERW | 8.625 | 715 | [10 empty] | Launcher Door | 4.54 | AGM 1 | 1747.79 | 3.16 | 4.9 | 1.38 | 3.16 | 4.9 | 30 | 3.27 | 1.63 | 33.6722 | -118.0193 | 37.81
GWD 40 | Girth Weld |  | 8.87 | 1.8 | 0.219 | 35000 | ERW | 8.625 | 715 | [10 empty] | Launcher Door | 9.44 | AGM 1 | 1742.89 | 4.9 | 3.27 | 3.16 | 4.9 | 3.27 | 40 | 1.63 | 3.83 | 33.6722 | -118.0193 | 33.053
BND 2 | Bend |  | 10.68 | 1.47 | 0.219 | 35000 | ERW | 8.625 | 715 |  |  | 38.867 | [7 empty] | Launcher Door | 11.24 | AGM 1 | 1741.09 | 1.8 | 1.46 | 3.16 | 4.9 | 3.27 | 40 | 1.63 | 3.83 | 33.6722 | -118.0193 | 31.428 | 3.0D 89.1 deg left turn sag bend
GWD 50 | Girth Weld |  | 12.14 | 1.63 | 0.219 | 35000 | ERW | 8.625 | 715 | [10 empty] | Launcher Door | 12.71 | AGM 1 | 1739.62 | 3.27 | 1.63 | 4.9 | 3.27 | 1.63 | 50 | 3.83 | 39.24 | 33.6722 | -118.0193 | 30.774
GWD 60 | Girth Weld |  | 13.78 | 1.35 | 0.28 | 35000 | ERW | 8.625 | 715 | [10 empty] | Launcher Door | 14.34 | AGM 1 | 1737.99 | 1.63 | 3.83 | 3.27 | 1.63 | 3.83 | 60 | 39.24 | 37.84 | 33.6722 | -118.0193 | 30.691
TAP 1 | TAP |  | 15.13 | 2.48 | 0.28 | 35000 | ERW | 8.625 | 715 |  |  |  |  | 11:44 | [5 empty] | Launcher Door | 15.7 | AGM 1 | 1736.63 | 1.35 | 2.48 | 3.27 | 1.63 | 3.83 | 60 | 39.24 | 37.84 | 33.6722 | -118.0193 | 30.648
GWD 70 | Girth Weld |  | 17.61 | 26.52 | 0.28 | 35000 | ERW | 8.625 | 715 | [10 empty] | Launcher Door | 18.17 | AGM 1 | 1734.16 | 3.83 | 39.24 | 1.63 | 3.83 | 39.24 | 70 | 37.84 | 1.14 | 33.6722 | -118.0192 | 30.572
BND 3 | Bend |  | 44.12 | 12.72 | 0.28 | 35000 | ERW | 8.625 | 715 |  |  | 46.996 | [7 empty] | Launcher Door | 44.69 | AGM 1 | 1707.64 | 26.52 | 12.72 | 1.63 | 3.83 | 39.24 | 70 | 37.84 | 1.14 | 33.6723 | -118.0192 | 29.096 | 48.5D 5.7 deg sag bend
GWD 80 | Girth Weld |  | 56.85 | 37.84 | 0.28 | 35000 | ERW | 8.625 | 715 | [10 empty] | Launcher Door | 57.41 | AGM 1 | 1694.92 | 39.24 | 37.84 | 3.83 | 39.24 | 37.84 | 80 | 1.14 | 1.57 | 33.6723 | -118.0192 | 29.276
GWD 90 | Girth Weld |  | 94.68 | 1.14 | 0.28 | 35000 | ERW | 8.625 | 715 | [10 empty] | Launcher Door | 95.25 | AGM 1 | 1657.08 | 37.84 | 1.14 | 39.24 | 37.84 | 1.14 | 90 | 1.57 | 1.83 | 33.6724 | -118.0191 | 29.149
GWD 100 | Girth Weld |  | 95.82 | 0.89 | 0.28 | 35000 | ERW | 8.625 | 715 | [10 empty] | Launcher Door | 96.39 | AGM 1 | 1655.94 | 1.14 | 1.57 | 37.84 | 1.14 | 1.57 | 100 | 1.83 | 3.27 | 33.6724 | -118.0191 | 29.086
BND 4 | Bend |  | 96.71 | 0.68 | 0.28 | 35000 | ERW | 8.625 | 715 |  |  | 24.774 | [7 empty] | Launcher Door | 97.27 | AGM 1 | 1655.06 | 0.89 | 0.69 | 37.84 | 1.14 | 1.57 | 100 | 1.83 | 3.27 | 33.6724 | -118.0191 | 29.22 | 3.0D 45.4 deg left turn sag bend
GWD 110 | Girth Weld |  | 97.39 | 1.83 | 0.28 | 35000 | ERW | 8.625 | 715 | [10 empty] | Launcher Door | 97.96 | AGM 1 | 1654.37 | 1.57 | 1.83 | 1.14 | 1.57 | 1.83 | 110 | 3.27 | 0.94 | 33.6724 | -118.0191 | 29.543
GWD 120 | Girth Weld |  | 99.22 | 1.51 | 0.28 | 35000 | ERW | 8.625 | 715 | [10 empty] | Launcher Door | 99.79 | AGM 1 | 1652.54 | 1.83 | 3.27 | 1.57 | 1.83 | 3.27 | 120 | 0.94 | 36.57 | 33.6724 | -118.0191 | 30.741
BND 5 | Bend |  | 100.73 | 1.76 | 0.28 | 35000 | ERW | 8.625 | 715 |  |  | 36.202 | [7 empty] | Launcher Door | 101.29 | AGM 1 | 1651.03 | 1.51 | 1.76 | 1.57 | 1.83 | 3.27 | 120 | 0.94 | 36.57 | 33.6724 | -118.0191 | 31.685 | 3.0D 89.7 deg right turn over bend
GWD 130 | Girth Weld |  | 102.49 | 0.94 | 0.28 | 35000 | ERW | 8.625 | 715 | [10 empty] | Launcher Door | 103.06 | AGM 1 | 1649.27 | 3.27 | 0.94 | 1.83 | 3.27 | 0.94 | 130 | 36.57 | 40.93 | 33.6724 | -118.0191 | 32.144
GWD 140 | Girth Weld |  | 103.44 | 36.57 | 0.28 | 35000 | ERW | 8.625 | 715 | [10 empty] | Launcher Door | 104 | AGM 1 | 1648.33 | 0.94 | 36.57 | 3.27 | 0.94 | 36.57 | 140 | 40.93 | 40.57 | 33.6724 | -118.0191 | 32.175
GWD 150 | Girth Weld |  | 140.01 | 40.93 | 0.28 | 35000 | ERW | 8.625 | 715 | [10 empty] | Launcher Door | 140.57 | AGM 1 | 1611.76 | 36.57 | 40.93 | 0.94 | 36.57 | 40.93 | 150 | 40.57 | 40.98 | 33.6723 | -118.019 | 32.451
GWD 160 | Girth Weld |  | 180.94 | 40.57 | 0.28 | 35000 | ERW | 8.625 | 715 | [10 empty] | Launcher Door | 181.5 | AGM 1 | 1570.83 | 40.93 | 40.57 | 36.57 | 40.93 | 40.57 | 160 | 40.98 | 41.01 | 33.6723 | -118.0189 | 32.125
GWD 170 | Girth Weld |  | 221.51 | 40.98 | 0.28 | 35000 | ERW | 8.625 | 715 | [10 empty] | Launcher Door | 222.07 | AGM 1 | 1530.26 | 40.57 | 40.98 | 40.93 | 40.57 | 40.98 | 170 | 41.01 | 40.88 | 33.6722 | -118.0188 | 32.288
GWD 180 | Girth Weld |  | 262.49 | 41.01 | 0.28 | 35000 | ERW | 8.625 | 715 | [10 empty] | Launcher Door | 263.05 | AGM 1 | 1489.28 | 40.98 | 41.01 | 40.57 | 40.98 | 41.01 | 180 | 40.88 | 40.9 | 33.6721 | -118.0187 | 32.403
GWD 190 | Girth Weld |  | 303.5 | 40.88 | 0.28 | 35000 | ERW | 8.625 | 715 | [10 empty] | Launcher Door | 304.06 | AGM 1 | 1448.27 | 41.01 | 40.88 | 40.98 | 41.01 | 40.88 | 190 | 40.9 | 40.91 | 33.672 | -118.0186 | 32.495
GWD 200 | Girth Weld |  | 344.38 | 40.9 | 0.28 | 35000 | ERW | 8.625 | 715 | [10 empty] | Launcher Door | 344.95 | AGM 1 | 1407.38 | 40.88 | 40.9 | 41.01 | 40.88 | 40.9 | 200 | 40.91 | 40.92 | 33.672 | -118.0185 | 32.789
GWD 210 | Girth Weld |  | 385.29 | 0.43 | 0.28 | 35000 | ERW | 8.625 | 715 | [10 empty] | Launcher Door | 385.85 | AGM 1 | 1366.48 | 40.9 | 40.91 | 40.88 | 40.9 | 40.91 | 210 | 40.92 | 36.26 | 33.6719 | -118.0184 | 32.729
DMA 1 | Metal Loss | Ext | 385.71 | 10.5 | 0.28 | 35000 | ERW | 8.625 | 715 | 41.9183 | 0.117 | 0.86 | 0.602 | 5:32 | 2792 | 0.35568 | 42 | 0.86 | 2755 | Launcher Door | 386.28 | AGM 1 | 1366.05 | 0.43 | 40.48 | 40.88 | 40.9 | 40.91 | 210 | 40.92 | 36.26 | 33.6719 | -118.0184 | 32.723
DMA 2 | Metal Loss | Ext | 396.22 | 29.98 | 0.28 | 35000 | ERW | 8.625 | 715 | 20.5601 | 0.058 | 0.633 | 0.581 | 6:08 | 2892 | 0.34338 | 21 | 0.63 | 2886 | Launcher Door | 396.78 | AGM 1 | 1355.55 | 10.93 | 29.98 | 40.88 | 40.9 | 40.91 | 210 | 40.92 | 36.26 | 33.6719 | -118.0183 | 32.581
GWD 220 | Girth Weld |  | 426.19 | 40.92 | 0.28 | 35000 | ERW | 8.625 | 715 | [10 empty] | Launcher Door | 426.76 | AGM 1 | 1325.57 | 40.91 | 40.92 | 40.9 | 40.91 | 40.92 | 220 | 36.26 | 3.03 | 33.6719 | -118.0182 | 32.078
GWD 230 | Girth Weld |  | 467.11 | 36.26 | 0.28 | 35000 | ERW | 8.625 | 715 | [10 empty] | Launcher Door | 467.68 | AGM 1 | 1284.65 | 40.92 | 36.26 | 40.91 | 40.92 | 36.26 | 230 | 3.03 | 40.97 | 33.6718 | -118.0181 | 31.394
GWD 240 | Girth Weld |  | 503.38 | 1.51 | 0.28 | 35000 | ERW | 8.625 | 715 | [10 empty] | Launcher Door | 503.94 | AGM 1 | 1248.39 | 36.26 | 3.03 | 40.92 | 36.26 | 3.03 | 240 | 40.97 | 40.97 | 33.6717 | -118.018 | 30.555
BND 6 | Bend |  | 504.88 | 1.52 | 0.28 | 35000 | ERW | 8.625 | 715 |  |  | 35.717 | [7 empty] | Launcher Door | 505.45 | AGM 1 | 1246.88 | 1.51 | 1.52 | 40.92 | 36.26 | 3.03 | 240 | 40.97 | 40.97 | 33.6717 | -118.018 | 30.454 | 3.0D 83.1 deg left turn over bend
GWD 250 | Girth Weld |  | 506.4 | 40.97 | 0.28 | 35000 | ERW | 8.625 | 715 | [10 empty] | Launcher Door | 506.97 | AGM 1 | 1245.36 | 3.03 | 40.97 | 36.26 | 3.03 | 40.97 | 250 | 40.97 | 41.09 | 33.6717 | -118.018 | 30.303
GWD 260 | Girth Weld |  | 547.38 | 7.58 | 0.28 | 35000 | ERW | 8.625 | 715 | [10 empty] | Launcher Door | 547.94 | AGM 1 | 1204.39 | 40.97 | 40.97 | 3.03 | 40.97 | 40.97 | 260 | 41.09 | 40.6 | 33.6718 | -118.0179 | 29.331
BND 7 | Bend |  | 554.96 | 24.85 | 0.28 | 35000 | ERW | 8.625 | 715 |  |  | 86.749 | [7 empty] | Launcher Door | 555.52 | AGM 1 | 1196.81 | 7.58 | 33.39 | 3.03 | 40.97 | 40.97 | 260 | 41.09 | 40.6 | 33.6718 | -118.0179 | 29.586 | 50.2D 8.0 deg sag bend
BND 8 | Bend |  | 579.81 | 8.54 | 0.28 | 35000 | ERW | 8.625 | 715 |  |  | 131.338 | [7 empty] | Launcher Door | 580.37 | AGM 1 | 1171.96 | 32.43 | 8.54 | 3.03 | 40.97 | 40.97 | 260 | 41.09 | 40.6 | 33.6719 | -118.0179 | 34.254 | 69.3D 10.6 deg over bend
GWD 270 | Girth Weld |  | 588.35 | 41.09 | 0.28 | 35000 | ERW | 8.625 | 715 | [10 empty] | Launcher Door | 588.91 | AGM 1 | 1163.42 | 40.97 | 41.09 | 40.97 | 40.97 | 41.09 | 270 | 40.6 | 40.97 | 33.6719 | -118.0179 | 34.767
GWD 280 | Girth Weld |  | 629.44 | 40.6 | 0.28 | 35000 | ERW | 8.625 | 715 | [10 empty] | Launcher Door | 630 | AGM 1 | 1122.33 | 41.09 | 40.6 | 40.97 | 41.09 | 40.6 | 280 | 40.97 | 40.95 | 33.672 | -118.0178 | 35.786
GWD 290 | Girth Weld |  | 670.04 | 40.97 | 0.28 | 35000 | ERW | 8.625 | 715 | [10 empty] | Launcher Door | 670.6 | AGM 1 | 1081.72 | 40.6 | 40.97 | 41.09 | 40.6 | 40.97 | 290 | 40.95 | 40.89 | 33.672 | -118.0177 | 36.314
GWD 300 | Girth Weld |  | 711.01 | 40.95 | 0.28 | 35000 | ERW | 8.625 | 715 | [10 empty] | Launcher Door | 711.57 | AGM 1 | 1040.76 | 40.97 | 40.95 | 40.6 | 40.97 | 40.95 | 300 | 40.89 | 40.6 | 33.6721 | -118.0175 | 37.044
GWD 310 | Girth Weld |  | 751.96 | 40.89 | 0.28 | 35000 | ERW | 8.625 | 715 | [10 empty] | Launcher Door | 752.52 | AGM 1 | 999.8 | 40.95 | 40.89 | 40.97 | 40.95 | 40.89 | 310 | 40.6 | 40.99 | 33.6722 | -118.0174 | 37.99
GWD 320 | Girth Weld |  | 792.85 | 40.6 | 0.28 | 35000 | ERW | 8.625 | 715 | [10 empty] | Launcher Door | 793.42 | AGM 1 | 958.91 | 40.89 | 40.6 | 40.95 | 40.89 | 40.6 | 320 | 40.99 | 41.04 | 33.6722 | -118.0173 | 38.456
GWD 330 | Girth Weld |  | 833.46 | 40.99 | 0.28 | 35000 | ERW | 8.625 | 715 | [10 empty] | Launcher Door | 834.02 | AGM 1 | 918.31 | 40.6 | 40.99 | 40.89 | 40.6 | 40.99 | 330 | 41.04 | 9.53 | 33.6723 | -118.0172 | 39.073
GWD 340 | Girth Weld |  | 874.44 | 41.05 | 0.28 | 35000 | ERW | 8.625 | 715 | [10 empty] | Launcher Door | 875.01 | AGM 1 | 877.32 | 40.99 | 41.04 | 40.6 | 40.99 | 41.04 | 340 | 9.53 | 2.69 | 33.6723 | -118.0171 | 39.238
GWD 350 | Girth Weld |  | 915.49 | 9.52 | 0.28 | 35000 | ERW | 8.625 | 715 | [10 empty] | Launcher Door | 916.05 | AGM 1 | 836.28 | 41.04 | 9.53 | 40.99 | 41.04 | 9.53 | 350 | 2.69 | 40.95 | 33.6724 | -118.017 | 38.738
GWD 360 | Girth Weld |  | 925.01 | 1.69 | 0.28 | 35000 | ERW | 8.625 | 715 | [10 empty] | Launcher Door | 925.58 | AGM 1 | 826.75 | 9.53 | 2.69 | 41.04 | 9.53 | 2.69 | 360 | 40.95 | 40.6 | 33.6724 | -118.0169 | 38.642
BND 9 | Bend |  | 926.7 | 1 | 0.28 | 35000 | ERW | 8.625 | 715 |  |  | 33.44 | [7 empty] | Launcher Door | 927.27 | AGM 1 | 825.06 | 1.69 | 1 | 41.04 | 9.53 | 2.69 | 360 | 40.95 | 40.6 | 33.6724 | -118.0169 | 38.636 | 3.0D 74.2 deg left turn sag bend
GWD 370 | Girth Weld |  | 927.71 | 40.95 | 0.28 | 35000 | ERW | 8.625 | 715 | [10 empty] | Launcher Door | 928.27 | AGM 1 | 824.06 | 2.69 | 40.95 | 9.53 | 2.69 | 40.95 | 370 | 40.6 | 27.18 | 33.6724 | -118.0169 | 38.659
GWD 380 | Girth Weld |  | 968.65 | 40.6 | 0.28 | 35000 | ERW | 8.625 | 715 | [10 empty] | Launcher Door | 969.22 | AGM 1 | 783.11 | 40.95 | 40.6 | 2.69 | 40.95 | 40.6 | 380 | 27.18 | 40.89 | 33.6725 | -118.0169 | 39.627
GWD 390 | Girth Weld |  | 1009.26 | 27.18 | 0.28 | 35000 | ERW | 8.625 | 715 | [10 empty] | Launcher Door | 1009.82 | AGM 1 | 742.51 | 40.6 | 27.18 | 40.95 | 40.6 | 27.18 | 390 | 40.89 | 21.86 | 33.6726 | -118.017 | 39.217
GWD 400 | Girth Weld |  | 1036.43 | 40.89 | 0.28 | 35000 | ERW | 8.625 | 715 | [10 empty] | Launcher Door | 1037 | AGM 1 | 715.33 | 27.18 | 40.89 | 40.6 | 27.18 | 40.89 | 400 | 21.86 | 1.62 | 33.6727 | -118.017 | 39.182
GWD 410 | Girth Weld |  | 1077.32 | 21.86 | 0.28 | 35000 | ERW | 8.625 | 715 | [10 empty] | Launcher Door | 1077.89 | AGM 1 | 674.44 | 40.89 | 21.86 | 27.18 | 40.89 | 21.86 | 410 | 1.62 | 27.42 | 33.6728 | -118.017 | 38.742
GWD 420 | Girth Weld |  | 1099.18 | 0.99 | 0.28 | 35000 | ERW | 8.625 | 715 | [10 empty] | Launcher Door | 1099.74 | AGM 1 | 652.59 | 21.86 | 1.62 | 40.89 | 21.86 | 1.62 | 420 | 27.42 | 1.59 | 33.6728 | -118.017 | 38.384
BND 10 | Bend |  | 1100.17 | 0.63 | 0.28 | 35000 | ERW | 8.625 | 715 |  |  | 25.72 | [7 empty] | Launcher Door | 1100.73 | AGM 1 | 651.6 | 0.99 | 0.63 | 40.89 | 21.86 | 1.62 | 420 | 27.42 | 1.59 | 33.6728 | -118.017 | 38.333 | 3.0D 47.1 deg right turn over bend
GWD 430 | Girth Weld |  | 1100.8 | 27.42 | 0.28 | 35000 | ERW | 8.625 | 715 | [10 empty] | Launcher Door | 1101.36 | AGM 1 | 650.97 | 1.62 | 27.42 | 21.86 | 1.62 | 27.42 | 430 | 1.59 | 40.58 | 33.6728 | -118.017 | 38.271
GWD 440 | Girth Weld |  | 1128.21 | 0.82 | 0.28 | 35000 | ERW | 8.625 | 715 | [10 empty] | Launcher Door | 1128.78 | AGM 1 | 623.55 | 27.42 | 1.59 | 1.62 | 27.42 | 1.59 | 440 | 40.58 | 23.56 | 33.6729 | -118.017 | 34.897
BND 11 | Bend |  | 1129.03 | 0.77 | 0.28 | 35000 | ERW | 8.625 | 715 |  |  | 25.811 | [7 empty] | Launcher Door | 1129.59 | AGM 1 | 622.74 | 0.82 | 0.77 | 1.62 | 27.42 | 1.59 | 440 | 40.58 | 23.56 | 33.6729 | -118.017 | 34.879 | 3.0D 46.6 deg left turn sag bend
GWD 450 | Girth Weld |  | 1129.8 | 40.57 | 0.28 | 35000 | ERW | 8.625 | 715 | [10 empty] | Launcher Door | 1130.37 | AGM 1 | 621.96 | 1.59 | 40.58 | 27.42 | 1.59 | 40.58 | 450 | 23.56 | 0.63 | 33.6729 | -118.017 | 34.923
GWD 460 | Girth Weld |  | 1170.38 | 12.91 | 0.28 | 35000 | ERW | 8.625 | 715 | [10 empty] | Launcher Door | 1170.94 | AGM 1 | 581.39 | 40.58 | 23.56 | 1.59 | 40.58 | 23.56 | 460 | 0.63 | 40.7 | 33.673 | -118.017 | 39.64
BND 12 | Bend |  | 1183.29 | 10.65 | 0.28 | 35000 | ERW | 8.625 | 715 |  |  | 107.61 | [7 empty] | Launcher Door | 1183.85 | AGM 1 | 568.48 | 12.91 | 10.65 | 1.59 | 40.58 | 23.56 | 460 | 0.63 | 40.7 | 33.6731 | -118.017 | 40.818 | 77.0D 8.2 deg over bend
GWD 470 | Girth Weld |  | 1193.94 | 0.35 | 0.28 | 35000 | ERW | 8.625 | 715 | [10 empty] | Launcher Door | 1194.51 | AGM 1 | 557.82 | 23.56 | 0.63 | 40.58 | 23.56 | 0.63 | 470 | 40.7 | 40.94 | 33.6731 | -118.017 | 40.516
BND 13 | Bend |  | 1194.29 | 0.28 | 0.28 | 35000 | ERW | 8.625 | 715 |  |  | 23.743 | [7 empty] | Launcher Door | 1194.85 | AGM 1 | 557.48 | 0.35 | 0.28 | 40.58 | 23.56 | 0.63 | 470 | 40.7 | 40.94 | 33.6731 | -118.017 | 40.507 | 8.0D 19.4 deg right turn sag bend
GWD 480 | Girth Weld |  | 1194.57 | 40.7 | 0.28 | 35000 | ERW | 8.625 | 715 | [10 empty] | Launcher Door | 1195.13 | AGM 1 | 557.2 | 0.63 | 40.7 | 23.56 | 0.63 | 40.7 | 480 | 40.94 | 40.91 | 33.6731 | -118.017 | 40.501
GWD 490 | Girth Weld |  | 1235.27 | 40.94 | 0.28 | 35000 | ERW | 8.625 | 715 | [10 empty] | Launcher Door | 1235.84 | AGM 1 | 516.49 | 40.7 | 40.94 | 0.63 | 40.7 | 40.94 | 490 | 40.91 | 40.98 | 33.6732 | -118.017 | 40.454
GWD 500 | Girth Weld |  | 1276.21 | 40.91 | 0.28 | 35000 | ERW | 8.625 | 715 | [10 empty] | Launcher Door | 1276.78 | AGM 1 | 475.55 | 40.94 | 40.91 | 40.7 | 40.94 | 40.91 | 500 | 40.98 | 28.36 | 33.6733 | -118.0169 | 40.948
GWD 510 | Girth Weld |  | 1317.12 | 40.98 | 0.28 | 35000 | ERW | 8.625 | 715 | [10 empty] | Launcher Door | 1317.68 | AGM 1 | 434.65 | 40.91 | 40.98 | 40.94 | 40.91 | 40.98 | 510 | 28.36 | 39.46 | 33.6734 | -118.0169 | 39.93
GWD 520 | Girth Weld |  | 1358.1 | 28.36 | 0.28 | 35000 | ERW | 8.625 | 715 | [10 empty] | Launcher Door | 1358.67 | AGM 1 | 393.66 | 40.98 | 28.36 | 40.91 | 40.98 | 28.36 | 520 | 39.46 | 26.73 | 33.6735 | -118.0169 | 39.206
GWD 530 | Girth Weld |  | 1386.46 | 10.17 | 0.28 | 35000 | ERW | 8.625 | 715 | [10 empty] | Launcher Door | 1387.03 | AGM 1 | 365.3 | 28.36 | 39.46 | 40.98 | 28.36 | 39.46 | 530 | 26.73 | 42.69 | 33.6736 | -118.0169 | 38.397
BND 14 | Bend |  | 1396.63 | 29.29 | 0.28 | 35000 | ERW | 8.625 | 715 |  |  | 98.091 | [7 empty] | Launcher Door | 1397.19 | AGM 1 | 355.14 | 10.17 | 29.29 | 40.98 | 28.36 | 39.46 | 530 | 26.73 | 42.69 | 33.6736 | -118.0169 | 37.971 | 70.4D 8.0 deg sag bend
GWD 540 | Girth Weld |  | 1425.92 | 4.73 | 0.28 | 35000 | ERW | 8.625 | 715 | [10 empty] | Launcher Door | 1426.49 | AGM 1 | 325.84 | 39.46 | 26.73 | 28.36 | 39.46 | 26.73 | 540 | 42.69 | 39.31 | 33.6737 | -118.0169 | 39.519
BND 15 | Bend |  | 1430.65 | 14.46 | 0.28 | 35000 | ERW | 8.625 | 715 |  |  | 34.697 | [7 empty] | Launcher Door | 1431.21 | AGM 1 | 321.12 | 4.73 | 22 | 28.36 | 39.46 | 26.73 | 540 | 42.69 | 39.31 | 33.6737 | -118.0168 | 39.624 | 37.8D 5.7 deg left turn sag bend
BND 16 | Bend |  | 1445.11 | 7.54 | 0.28 | 35000 | ERW | 8.625 | 715 |  |  | 31.837 | [7 empty] | Launcher Door | 1445.67 | AGM 1 | 306.66 | 19.18 | 7.54 | 28.36 | 39.46 | 26.73 | 540 | 42.69 | 39.31 | 33.6738 | -118.0168 | 41.166 | 35.6D 5.6 deg right turn over bend
GWD 550 | Girth Weld |  | 1452.65 | 42.69 | 0.28 | 35000 | ERW | 8.625 | 715 | [10 empty] | Launcher Door | 1453.21 | AGM 1 | 299.12 | 26.73 | 42.69 | 39.46 | 26.73 | 42.69 | 550 | 39.31 | 40.54 | 33.6738 | -118.0168 | 41.253
GWD 560 | Girth Weld |  | 1495.34 | 39.31 | 0.28 | 35000 | ERW | 8.625 | 715 | [10 empty] | Launcher Door | 1495.91 | AGM 1 | 256.42 | 42.69 | 39.31 | 26.73 | 42.69 | 39.31 | 560 | 40.54 | 42.56 | 33.6739 | -118.0168 | 41.388
GWD 570 | Girth Weld |  | 1534.66 | 14.97 | 0.28 | 35000 | ERW | 8.625 | 715 | [10 empty] | Launcher Door | 1535.22 | AGM 1 | 217.11 | 39.31 | 40.54 | 42.69 | 39.31 | 40.54 | 570 | 42.56 | 1.85 | 33.674 | -118.0168 | 40.974
BND 17 | Bend |  | 1549.62 | 15.79 | 0.28 | 35000 | ERW | 8.625 | 715 |  |  | 33.611 | [7 empty] | Launcher Door | 1550.19 | AGM 1 | 202.14 | 14.97 | 25.58 | 42.69 | 39.31 | 40.54 | 570 | 42.56 | 1.85 | 33.674 | -118.0168 | 40.782 | 41.2D 5.2 deg left turn over bend
BND 18 | Bend |  | 1565.41 | 9.79 | 0.28 | 35000 | ERW | 8.625 | 715 |  |  | 38.035 | [7 empty] | Launcher Door | 1565.97 | AGM 1 | 186.36 | 30.75 | 9.79 | 42.69 | 39.31 | 40.54 | 570 | 42.56 | 1.85 | 33.6741 | -118.0168 | 39.333 | 25.6D 9.0 deg right turn sag bend
GWD 580 | Girth Weld |  | 1575.2 | 4.37 | 0.28 | 35000 | ERW | 8.625 | 715 | [10 empty] | Launcher Door | 1575.76 | AGM 1 | 176.57 | 40.54 | 42.56 | 39.31 | 40.54 | 42.56 | 580 | 1.85 | 1.27 | 33.6741 | -118.0168 | 39.867
BND 19 | Bend |  | 1579.57 | 24.29 | 0.28 | 35000 | ERW | 8.625 | 715 |  |  | 30.856 | [7 empty] | Launcher Door | 1580.14 | AGM 1 | 172.19 | 4.37 | 38.19 | 39.31 | 40.54 | 42.56 | 580 | 1.85 | 1.27 | 33.6741 | -118.0168 | 40.125 | 32.3D 6.1 deg left turn over bend
BND 20 | Bend |  | 1603.86 | 13.9 | 0.28 | 35000 | ERW | 8.625 | 715 |  |  | 33.24 | [7 empty] | Launcher Door | 1604.43 | AGM 1 | 147.9 | 28.67 | 13.9 | 39.31 | 40.54 | 42.56 | 580 | 1.85 | 1.27 | 33.6742 | -118.0168 | 39.321 | 37.2D 5.8 deg right turn sag bend
GWD 590 | Girth Weld |  | 1617.76 | 0.98 | 0.28 | 35000 | ERW | 8.625 | 715 | [10 empty] | Launcher Door | 1618.33 | AGM 1 | 134 | 42.56 | 1.85 | 40.54 | 42.56 | 1.85 | 590 | 1.27 | 33.5 | 33.6742 | -118.0168 | 40.23
BND 21 | Bend |  | 1618.74 | 0.87 | 0.28 | 35000 | ERW | 8.625 | 715 |  |  | 26.626 | [7 empty] | Launcher Door | 1619.3 | AGM 1 | 133.03 | 0.98 | 0.87 | 40.54 | 42.56 | 1.85 | 590 | 1.27 | 33.5 | 33.6742 | -118.0168 | 40.278 | 3.0D 54.9 deg right turn over bend
GWD 600 | Girth Weld |  | 1619.61 | 1.27 | 0.28 | 35000 | ERW | 8.625 | 715 | [10 empty] | Launcher Door | 1620.17 | AGM 1 | 132.16 | 1.85 | 1.27 | 42.56 | 1.85 | 1.27 | 600 | 33.5 | 45.87 | 33.6742 | -118.0168 | 40.281
GWD 610 | Girth Weld |  | 1620.88 | 1.06 | 0.25 | 35000 | SMLS | 8.625 | 715 | [10 empty] | Launcher Door | 1621.44 | AGM 1 | 130.89 | 1.27 | 33.5 | 1.85 | 1.27 | 33.5 | 610 | 45.87 | 13.07 | 33.6742 | -118.0168 | 40.254 | Estimated WT 0.250
TAP 2 | TAP |  | 1621.94 | 32.43 | 0.25 | 35000 | SMLS | 8.625 | 715 |  |  |  |  | 11:50 | [5 empty] | Launcher Door | 1622.51 | AGM 1 | 129.82 | 1.06 | 32.43 | 1.85 | 1.27 | 33.5 | 610 | 45.87 | 13.07 | 33.6742 | -118.0168 | 40.241
GWD 620 | Girth Weld |  | 1654.37 | 45.87 | 0.25 | 35000 | SMLS | 8.625 | 715 | [10 empty] | Launcher Door | 1654.94 | AGM 1 | 97.39 | 33.5 | 45.87 | 1.27 | 33.5 | 45.87 | 620 | 13.07 | 1.01 | 33.6743 | -118.0167 | 39.701
GWD 630 | Girth Weld |  | 1700.24 | 13.07 | 0.25 | 35000 | SMLS | 8.625 | 715 | [10 empty] | Launcher Door | 1700.81 | AGM 1 | 51.52 | 45.87 | 13.07 | 33.5 | 45.87 | 13.07 | 630 | 1.01 | 1.94 | 33.6743 | -118.0166 | 38.509
GWD 640 | Girth Weld |  | 1713.31 | 1.01 | 0.219 | 35000 | ERW | 8.625 | 715 | [10 empty] | Launcher Door | 1713.88 | AGM 1 | 38.45 | 13.07 | 1.01 | 45.87 | 13.07 | 1.01 | 640 | 1.94 | 26.95 | 33.6744 | -118.0165 | 37.972
GWD 650 | Girth Weld |  | 1714.32 | 0.94 | 0.219 | 35000 | ERW | 8.625 | 715 | [10 empty] | Launcher Door | 1714.88 | AGM 1 | 37.45 | 1.01 | 1.94 | 13.07 | 1.01 | 1.94 | 650 | 26.95 | 40.99 | 33.6744 | -118.0165 | 37.913
BND 22 | Bend |  | 1715.27 | 1 | 0.219 | 35000 | ERW | 8.625 | 715 |  |  | 26.955 | [7 empty] | Launcher Door | 1715.83 | AGM 1 | 36.5 | 0.95 | 1 | 13.07 | 1.01 | 1.94 | 650 | 26.95 | 40.99 | 33.6744 | -118.0165 | 37.838 | 3.0D 56.6 deg left turn over bend
GWD 660 | Girth Weld |  | 1716.26 | 18.33 | 0.219 | 35000 | ERW | 8.625 | 715 | [10 empty] | Launcher Door | 1716.83 | AGM 1 | 35.5 | 1.94 | 26.95 | 1.01 | 1.94 | 26.95 | 660 | 40.99 | 40.96 | 33.6744 | -118.0165 | 37.73
DMA 3 | Metal Loss | Ext | 1734.59 | 8.63 | 0.219 | 35000 | ERW | 8.625 | 715 | 12.6821 | 0.028 | 0.626 | 0.754 | 2:38 | 2269 | 0.43766 | 13 | 0.63 | 2266 | Launcher Door | 1735.15 | AGM 1 | 17.18 | 18.33 | 8.63 | 1.01 | 1.94 | 26.95 | 660 | 40.99 | 40.96 | 33.6744 | -118.0165 | 35.707
GWD 670 | Girth Weld |  | 1743.22 | 8.55 | 0.219 | 35000 | ERW | 8.625 | 715 | [10 empty] | Launcher Door | 1743.78 | AGM 1 | 8.55 | 26.95 | 40.99 | 1.94 | 26.95 | 40.99 | 670 | 40.96 | 3.21 | 33.6744 | -118.0165 | 34.948
MRK 1 | Marker |  | 1751.77 | 32.44 | 0.219 | 35000 | ERW | 8.625 | 715 |  |  |  |  | 11:37 | [5 empty] | Launcher Door | 1752.33 | AGM 2 | 3196.52 | 8.55 | 32.44 | 1.94 | 26.95 | 40.99 | 670 | 40.96 | 3.21 | 33.6745 | -118.0165 | 34.342 | AGM 1 64' D/S of Morning Tide Drive - 2' U/S of Metal Fence
GWD 680 | Girth Weld |  | 1784.21 | 40.96 | 0.219 | 35000 | ERW | 8.625 | 715 | [10 empty] | AGM 1 | 32.44 | AGM 2 | 3164.08 | 40.99 | 40.96 | 26.95 | 40.99 | 40.96 | 680 | 3.21 | 6.74 | 33.6746 | -118.0165 | 32.933
GWD 690 | Girth Weld |  | 1825.17 | 1.61 | 0.219 | 35000 | ERW | 8.625 | 715 | [10 empty] | AGM 1 | 73.4 | AGM 2 | 3123.12 | 40.96 | 3.21 | 40.99 | 40.96 | 3.21 | 690 | 6.74 | 40.5 | 33.6747 | -118.0165 | 31.064
BND 23 | Bend |  | 1826.77 | 1.6 | 0.219 | 35000 | ERW | 8.625 | 715 |  |  | 37.195 | [7 empty] | AGM 1 | 75.01 | AGM 2 | 3121.51 | 1.61 | 1.6 | 40.99 | 40.96 | 3.21 | 690 | 6.74 | 40.5 | 33.6747 | -118.0165 | 31.011 | 3.0D 90.2 deg right turn sag bend
GWD 700 | Girth Weld |  | 1828.38 | 6.74 | 0.219 | 35000 | ERW | 8.625 | 715 | [10 empty] | AGM 1 | 76.61 | AGM 2 | 3119.91 | 3.21 | 6.74 | 40.96 | 3.21 | 6.74 | 700 | 40.5 | 40.91 | 33.6747 | -118.0165 | 31.001
GWD 710 | Girth Weld |  | 1835.12 | 40.5 | 0.219 | 35000 | ERW | 8.625 | 715 | [10 empty] | AGM 1 | 83.35 | AGM 2 | 3113.17 | 6.74 | 40.5 | 3.21 | 6.74 | 40.5 | 710 | 40.91 | 41.02 | 33.6747 | -118.0165 | 31.04
GWD 720 | Girth Weld |  | 1875.62 | 40.91 | 0.219 | 35000 | ERW | 8.625 | 715 | [10 empty] | AGM 1 | 123.85 | AGM 2 | 3072.67 | 40.5 | 40.91 | 6.74 | 40.5 | 40.91 | 720 | 41.02 | 21.64 | 33.6747 | -118.0164 | 31.386
GWD 730 | Girth Weld |  | 1916.53 | 41.02 | 0.219 | 35000 | ERW | 8.625 | 715 | [10 empty] | AGM 1 | 164.76 | AGM 2 | 3031.76 | 40.91 | 41.02 | 40.5 | 40.91 | 41.02 | 730 | 21.64 | 1.3 | 33.6747 | -118.0162 | 32.492
GWD 740 | Girth Weld |  | 1957.54 | 21.64 | 0.219 | 35000 | ERW | 8.625 | 715 | [10 empty] | AGM 1 | 205.78 | AGM 2 | 2990.74 | 41.02 | 21.64 | 40.91 | 41.02 | 21.64 | 740 | 1.3 | 1.05 | 33.6746 | -118.0161 | 32.92
GWD 750 | Girth Weld |  | 1979.18 | 0.66 | 0.219 | 35000 | ERW | 8.625 | 715 | [10 empty] | AGM 1 | 227.42 | AGM 2 | 2969.1 | 21.64 | 1.3 | 41.02 | 21.64 | 1.3 | 750 | 1.05 | 11.38 | 33.6746 | -118.016 | 33.534
BND 24 | Bend |  | 1979.85 | 0.63 | 0.219 | 35000 | ERW | 8.625 | 715 |  |  | 24.21 | [7 empty] | AGM 1 | 228.09 | AGM 2 | 2968.44 | 0.67 | 0.63 | 41.02 | 21.64 | 1.3 | 750 | 1.05 | 11.38 | 33.6746 | -118.016 | 33.557 | 5.0D 38.5 deg left turn over bend
GWD 760 | Girth Weld |  | 1980.48 | 1.05 | 0.219 | 35000 | ERW | 8.625 | 715 | [10 empty] | AGM 1 | 228.72 | AGM 2 | 2967.81 | 1.3 | 1.05 | 21.64 | 1.3 | 1.05 | 760 | 11.38 | 45.88 | 33.6746 | -118.016 | 33.57
GWD 770 | Girth Weld |  | 1981.53 | 11.39 | 0.28 | 35000 | SMLS | 8.625 | 715 | [10 empty] | AGM 1 | 229.76 | AGM 2 | 2966.76 | 1.05 | 11.38 | 1.3 | 1.05 | 11.38 | 770 | 45.88 | 45.07 | 33.6746 | -118.016 | 33.58
GWD 780 | Girth Weld |  | 1992.91 | 45.88 | 0.28 | 35000 | SMLS | 8.625 | 715 | [10 empty] | AGM 1 | 241.15 | AGM 2 | 2955.38 | 11.38 | 45.88 | 1.05 | 11.38 | 45.88 | 780 | 45.07 | 20.04 | 33.6747 | -118.016 | 33.519
GWD 790 | Girth Weld |  | 2038.79 | 7.67 | 0.28 | 35000 | SMLS | 8.625 | 715 | [10 empty] | AGM 1 | 287.03 | AGM 2 | 2909.49 | 45.88 | 45.07 | 11.38 | 45.88 | 45.07 | 790 | 20.04 | 21.84 | 33.6747 | -118.0159 | 32.845
CLS 1 | Cluster | Ext | 2046.46 | 0.38 | 0.28 | 35000 | SMLS | 8.625 | 715 | 12.2685 | 0.034 | 2.565 | 2.738 | 4:58 | 2795 | 0.3553 | 10 | 2.57 | 2799 | AGM 1 | 294.69 | AGM 2 | 2901.83 | 7.66 | 37.4 | 11.38 | 45.88 | 45.07 | 790 | 20.04 | 21.84 | 33.6747 | -118.0158 | 32.7 | CLS C
DMA 6 | Metal Loss | Ext | 2046.84 | 0.25 | 0.28 | 35000 | SMLS | 8.625 | 715 | 16.8651 | 0.047 | 1.46 | 0.644 | 6:37 | 2828 | 0.35115 | 17 | 1.46 | 2809 | AGM 1 | 295.08 | AGM 2 | 2901.45 | 8.05 | 37.02 | 11.38 | 45.88 | 45.07 | 790 | 20.04 | 21.84 | 33.6747 | -118.0158 | 32.693
CLS 2 | Cluster | Ext | 2047.1 | 0.73 | 0.28 | 35000 | SMLS | 8.625 | 715 | 18.493 | 0.052 | 2.112 | 3.109 | 7:01 | 2758 | 0.36006 | 16 | 2.11 | 2752 | AGM 1 | 295.33 | AGM 2 | 2901.19 | 8.3 | 36.77 | 11.38 | 45.88 | 45.07 | 790 | 20.04 | 21.84 | 33.6747 | -118.0158 | 32.689 | CLS C
CLS 3 | Cluster | Ext | 2047.82 | 0.34 | 0.28 | 35000 | SMLS | 8.625 | 715 | 17.6253 | 0.049 | 2.041 | 0.652 | 7:38 | 2773 | 0.35812 | 9 | 2.04 | 2834 | AGM 1 | 296.06 | AGM 2 | 2900.46 | 9.03 | 36.04 | 11.38 | 45.88 | 45.07 | 790 | 20.04 | 21.84 | 33.6747 | -118.0158 | 32.675 | CLS C
CLS 4 | Cluster | Ext | 2048.17 | 0.06 | 0.28 | 35000 | SMLS | 8.625 | 715 | 15.7859 | 0.044 | 3.93 | 3.981 | 6:08 | 2693 | 0.36875 | 13 | 3.93 | 2705 | AGM 1 | 296.4 | AGM 2 | 2900.12 | 9.37 | 35.69 | 11.38 | 45.88 | 45.07 | 790 | 20.04 | 21.84 | 33.6747 | -118.0158 | 32.667 | CLS C
DMA 15 | Metal Loss | Ext | 2048.23 | 0.33 | 0.28 | 35000 | SMLS | 8.625 | 715 | 15.8401 | 0.044 | 0.781 | 0.616 | 11:34 | 2890 | 0.34362 | 16 | 0.78 | 2883 | AGM 1 | 296.46 | AGM 2 | 2900.06 | 9.43 | 35.63 | 11.38 | 45.88 | 45.07 | 790 | 20.04 | 21.84 | 33.6747 | -118.0158 | 32.667
DMA 17 | Metal Loss | Ext | 2048.56 | 0.75 | 0.28 | 35000 | SMLS | 8.625 | 715 | 11.3865 | 0.032 | 0.805 | 0.606 | 3:40 | 2899 | 0.34255 | 11 | 0.81 | 2894 | AGM 1 | 296.8 | AGM 2 | 2899.73 | 9.77 | 35.3 | 11.38 | 45.88 | 45.07 | 790 | 20.04 | 21.84 | 33.6747 | -118.0158 | 32.661
DMA 18 | Metal Loss | Ext | 2049.31 | 1.78 | 0.28 | 35000 | SMLS | 8.625 | 715 | 24.9868 | 0.07 | 0.677 | 0.586 | 11:36 | 2879 | 0.34493 | 25 | 0.68 | 2870 | AGM 1 | 297.55 | AGM 2 | 2898.98 | 10.52 | 34.55 | 11.38 | 45.88 | 45.07 | 790 | 20.04 | 21.84 | 33.6747 | -118.0158 | 32.647
DMA 19 | Metal Loss | Ext | 2051.09 | 1.13 | 0.28 | 35000 | SMLS | 8.625 | 715 | 20.896 | 0.059 | 0.501 | 0.549 | 11:23 | 2902 | 0.3422 | 21 | 0.5 | 2898 | AGM 1 | 299.32 | AGM 2 | 2897.2 | 12.3 | 32.77 | 11.38 | 45.88 | 45.07 | 790 | 20.04 | 21.84 | 33.6747 | -118.0158 | 32.614
DMA 20 | Metal Loss | Ext | 2052.22 | 0.71 | 0.28 | 35000 | SMLS | 8.625 | 715 | 17.1685 | 0.048 | 0.678 | 0.571 | 7:22 | 2895 | 0.34302 | 17 | 0.68 | 2889 | AGM 1 | 300.46 | AGM 2 | 2896.06 | 13.43 | 31.64 | 11.38 | 45.88 | 45.07 | 790 | 20.04 | 21.84 | 33.6747 | -118.0158 | 32.595
DMA 21 | Metal Loss | Ext | 2052.93 | 30.93 | 0.28 | 35000 | SMLS | 8.625 | 715 | 24.4229 | 0.068 | 0.738 | 0.49 | 6:19 | 2874 | 0.34553 | 24 | 0.74 | 2863 | AGM 1 | 301.17 | AGM 2 | 2895.36 | 14.14 | 30.93 | 11.38 | 45.88 | 45.07 | 790 | 20.04 | 21.84 | 33.6747 | -118.0158 | 32.577
GWD 800 | Girth Weld |  | 2083.86 | 20.05 | 0.28 | 35000 | SMLS | 8.625 | 715 | [10 empty] | AGM 1 | 332.1 | AGM 2 | 2864.43 | 45.07 | 20.04 | 45.88 | 45.07 | 20.04 | 800 | 21.84 | 18.79 | 33.6748 | -118.0157 | 32.222
GWD 810 | Girth Weld |  | 2103.91 | 5.79 | 0.28 | 35000 | SMLS | 8.625 | 715 | [10 empty] | AGM 1 | 352.14 | AGM 2 | 2844.38 | 20.04 | 21.84 | 45.07 | 20.04 | 21.84 | 810 | 18.79 | 3.42 | 33.6748 | -118.0157 | 31.904
CLS 5 | Cluster | Ext | 2109.7 | 2.9 | 0.28 | 35000 | SMLS | 8.625 | 715 | 16.3191 | 0.046 | 2.291 | 1.87 | 3:45 | 2767 | 0.35889 | 9 | 2.29 | 2822 | AGM 1 | 357.94 | AGM 2 | 2838.59 | 5.8 | 16.05 | 45.07 | 20.04 | 21.84 | 810 | 18.79 | 3.42 | 33.6748 | -118.0157 | 31.791 | CLS C
DMA 24 | Metal Loss | Ext | 2112.6 | 13.15 | 0.28 | 35000 | SMLS | 8.625 | 715 | 30.022 | 0.084 | 0.687 | 0.843 | 2:24 | 2867 | 0.34637 | 30 | 0.69 | 2853 | AGM 1 | 360.83 | AGM 2 | 2835.69 | 8.69 | 13.15 | 45.07 | 20.04 | 21.84 | 810 | 18.79 | 3.42 | 33.6748 | -118.0157 | 31.742
GWD 820 | Girth Weld |  | 2125.75 | 18.79 | 0.28 | 35000 | ERW | 8.625 | 715 | [10 empty] | AGM 1 | 373.98 | AGM 2 | 2822.54 | 21.84 | 18.79 | 20.04 | 21.84 | 18.79 | 820 | 3.42 | 4.62 | 33.6749 | -118.0156 | 31.48
GWD 830 | Girth Weld |  | 2144.54 | 1.16 | 0.28 | 35000 | SMLS | 8.625 | 715 | [10 empty] | AGM 1 | 392.77 | AGM 2 | 2803.75 | 18.79 | 3.42 | 21.84 | 18.79 | 3.42 | 830 | 4.62 | 0.4 | 33.6749 | -118.0156 | 31.097
PMA 1 | Pipe Mill | Ext | 2145.69 | 2.26 | 0.28 | 35000 | SMLS | 8.625 | 715 | 11.3448 | 0.032 | 0.795 | 1.453 | 3:34 | [5 empty] | AGM 1 | 393.93 | AGM 2 | 2802.59 | 1.16 | 2.26 | 21.84 | 18.79 | 3.42 | 830 | 4.62 | 0.4 | 33.6749 | -118.0156 | 31.077
GWD 840 | Girth Weld |  | 2147.96 | 4.62 | 0.28 | 35000 | ERW | 8.625 | 715 | [10 empty] | AGM 1 | 396.19 | AGM 2 | 2800.33 | 3.42 | 4.62 | 18.79 | 3.42 | 4.62 | 840 | 0.4 | 8.42 | 33.6749 | -118.0156 | 31.044
GWD 850 | Girth Weld |  | 2152.58 | 0.18 | 0.28 | 35000 | ERW | 8.625 | 715 | [10 empty] | AGM 1 | 400.82 | AGM 2 | 2795.71 | 4.62 | 0.4 | 3.42 | 4.62 | 0.4 | 850 | 8.42 | 17.91 | 33.6749 | -118.0156 | 30.946
BND 25 | Bend |  | 2152.76 | 0.22 | 0.28 | 35000 | ERW | 8.625 | 715 |  |  | 23.764 | [7 empty] | AGM 1 | 401 | AGM 2 | 2795.53 | 0.18 | 0.22 | 3.42 | 4.62 | 0.4 | 850 | 8.42 | 17.91 | 33.6749 | -118.0156 | 30.934 | 6.7D 22.9 deg left turn over bend
GWD 860 | Girth Weld |  | 2152.98 | 8.42 | 0.28 | 35000 | ERW | 8.625 | 715 | [10 empty] | AGM 1 | 401.22 | AGM 2 | 2795.3 | 0.4 | 8.42 | 4.62 | 0.4 | 8.42 | 860 | 17.91 | 42.63 | 33.6749 | -118.0156 | 30.917
GWD 870 | Girth Weld |  | 2161.41 | 8.2 | 0.28 | 35000 | SMLS | 8.625 | 715 | [10 empty] | AGM 1 | 409.64 | AGM 2 | 2786.88 | 8.42 | 17.91 | 0.4 | 8.42 | 17.91 | 870 | 42.63 | 41.52 | 33.6749 | -118.0155 | 29.999
PMA 2 | Pipe Mill | Ext | 2169.61 | 9.71 | 0.28 | 35000 | SMLS | 8.625 | 715 | 10.8783 | 0.03 | 1.268 | 3.942 | 3:51 | [5 empty] | AGM 1 | 417.85 | AGM 2 | 2778.68 | 8.2 | 9.71 | 0.4 | 8.42 | 17.91 | 870 | 42.63 | 41.52 | 33.6749 | -118.0155 | 29.235
GWD 880 | Girth Weld |  | 2179.32 | 42.63 | 0.28 | 35000 | SMLS | 8.625 | 715 | [10 empty] | AGM 1 | 427.56 | AGM 2 | 2768.97 | 17.91 | 42.63 | 8.42 | 17.91 | 42.63 | 880 | 41.52 | 43.26 | 33.675 | -118.0155 | 28.516
GWD 890 | Girth Weld |  | 2221.95 | 0.16 | 0.28 | 35000 | SMLS | 8.625 | 715 | [10 empty] | AGM 1 | 470.18 | AGM 2 | 2726.34 | 42.63 | 41.52 | 17.91 | 42.63 | 41.52 | 890 | 43.26 | 43.3 | 33.6751 | -118.0154 | 26.087
DMA 25 | Metal Loss | Ext | 2222.11 | 41.36 | 0.28 | 35000 | SMLS | 8.625 | 715 | 36.1771 | 0.101 | 0.864 | 0.925 | 3:57 | 2816 | 0.35265 | 36 | 0.86 | 2788 | AGM 1 | 470.35 | AGM 2 | 2726.18 | 0.16 | 41.36 | 17.91 | 42.63 | 41.52 | 890 | 43.26 | 43.3 | 33.6751 | -118.0154 | 26.08
GWD 900 | Girth Weld |  | 2263.47 | 7.1 | 0.28 | 35000 | SMLS | 8.625 | 715 | [10 empty] | AGM 1 | 511.71 | AGM 2 | 2684.82 | 41.52 | 43.26 | 42.63 | 41.52 | 43.26 | 900 | 43.3 | 38.69 | 33.6752 | -118.0154 | 25.256
DMA 26 | Metal Loss | Ext | 2270.57 | 0.46 | 0.28 | 35000 | SMLS | 8.625 | 715 | 13.8998 | 0.039 | 0.87 | 0.687 | 12:45 | 2889 | 0.34374 | 14 | 0.87 | 2882 | AGM 1 | 518.8 | AGM 2 | 2677.72 | 7.1 | 36.17 | 42.63 | 41.52 | 43.26 | 900 | 43.3 | 38.69 | 33.6752 | -118.0153 | 25.188
CLS 6 | Cluster | Ext | 2271.03 | 35.71 | 0.28 | 35000 | SMLS | 8.625 | 715 | 21.67 | 0.061 | 1.857 | 1.524 | 11:56 | 2752 | 0.36085 | 17 | 1.86 | 2762 | AGM 1 | 519.26 | AGM 2 | 2677.26 | 7.56 | 35.7 | 42.63 | 41.52 | 43.26 | 900 | 43.3 | 38.69 | 33.6752 | -118.0153 | 25.185 | CLS C
GWD 910 | Girth Weld |  | 2306.73 | 43.3 | 0.28 | 35000 | SMLS | 8.625 | 715 | [10 empty] | AGM 1 | 554.97 | AGM 2 | 2641.55 | 43.26 | 43.3 | 41.52 | 43.26 | 43.3 | 910 | 38.69 | 1.05 | 33.6753 | -118.0153 | 25.496
GWD 920 | Girth Weld |  | 2350.03 | 35.46 | 0.28 | 35000 | SMLS | 8.625 | 715 | [10 empty] | AGM 1 | 598.27 | AGM 2 | 2598.26 | 43.3 | 38.69 | 43.26 | 43.3 | 38.69 | 920 | 1.05 | 0.74 | 33.6754 | -118.0152 | 26.074
DMA 29 | Metal Loss | Ext | 2385.49 | 0.12 | 0.28 | 35000 | SMLS | 8.625 | 715 | 10.4483 | 0.029 | 1.275 | 2.059 | 11:14 | 2877 | 0.34517 | 10 | 1.28 | 2868 | AGM 1 | 633.73 | AGM 2 | 2562.79 | 35.46 | 3.23 | 43.26 | 43.3 | 38.69 | 920 | 1.05 | 0.74 | 33.6754 | -118.0151 | 26.84
DMA 30 | Metal Loss | Ext | 2385.61 | 0.45 | 0.28 | 35000 | SMLS | 8.625 | 715 | 21.2356 | 0.059 | 1.393 | 0.775 | 7:42 | 2808 | 0.35365 | 21 | 1.39 | 2784 | AGM 1 | 633.85 | AGM 2 | 2562.68 | 35.58 | 3.11 | 43.26 | 43.3 | 38.69 | 920 | 1.05 | 0.74 | 33.6754 | -118.0151 | 26.839
CLS 7 | Cluster | Ext | 2386.06 | 0.24 | 0.28 | 35000 | SMLS | 8.625 | 715 | 17.1541 | 0.048 | 2.686 | 2.386 | 7:16 | 2732 | 0.36349 | 16 | 2.69 | 2718 | AGM 1 | 634.29 | AGM 2 | 2562.23 | 36.02 | 2.67 | 43.26 | 43.3 | 38.69 | 920 | 1.05 | 0.74 | 33.6754 | -118.0151 | 26.851 | CLS C
DMA 33 | Metal Loss | Ext | 2386.3 | 0.32 | 0.28 | 35000 | SMLS | 8.625 | 715 | 10.6299 | 0.03 | 0.673 | 1.157 | 6:15 | 2906 | 0.34173 | 11 | 0.67 | 2903 | AGM 1 | 634.54 | AGM 2 | 2561.99 | 36.27 | 2.42 | 43.26 | 43.3 | 38.69 | 920 | 1.05 | 0.74 | 33.6754 | -118.0151 | 26.859
DMA 34 | Metal Loss | Ext | 2386.63 | 0.95 | 0.28 | 35000 | SMLS | 8.625 | 715 | 11.2191 | 0.031 | 1.087 | 2.101 | 7:14 | 2884 | 0.34433 | 11 | 1.09 | 2876 | AGM 1 | 634.86 | AGM 2 | 2561.66 | 36.59 | 2.1 | 43.26 | 43.3 | 38.69 | 920 | 1.05 | 0.74 | 33.6754 | -118.0151 | 26.868
DMA 35 | Metal Loss | Ext | 2387.57 | 0.73 | 0.28 | 35000 | SMLS | 8.625 | 715 | 23.6242 | 0.066 | 0.473 | 0.512 | 6:30 | 2901 | 0.34231 | 24 | 0.47 | 2897 | AGM 1 | 635.81 | AGM 2 | 2560.72 | 37.54 | 1.15 | 43.26 | 43.3 | 38.69 | 920 | 1.05 | 0.74 | 33.6754 | -118.0151 | 26.897
DMA 36 | Metal Loss | Ext | 2388.3 | 0.42 | 0.28 | 35000 | SMLS | 8.625 | 715 | 13.7178 | 0.038 | 0.816 | 0.791 | 7:40 | 2893 | 0.34326 | 14 | 0.82 | 2887 | AGM 1 | 636.54 | AGM 2 | 2559.99 | 38.27 | 0.42 | 43.26 | 43.3 | 38.69 | 920 | 1.05 | 0.74 | 33.6754 | -118.0151 | 26.918
GWD 930 | Girth Weld |  | 2388.72 | 1.05 | 0.28 | 35000 | ERW | 8.625 | 715 | [10 empty] | AGM 1 | 636.96 | AGM 2 | 2559.56 | 38.69 | 1.05 | 43.3 | 38.69 | 1.05 | 930 | 0.74 | 1.89 | 33.6754 | -118.0151 | 26.927
GWD 940 | Girth Weld |  | 2389.78 | 0.27 | 0.28 | 35000 | ERW | 8.625 | 715 | [10 empty] | AGM 1 | 638.01 | AGM 2 | 2558.51 | 1.05 | 0.74 | 38.69 | 1.05 | 0.74 | 940 | 1.89 | 4.24 | 33.6754 | -118.0151 | 26.946
BND 26 | Bend |  | 2390.05 | 0.47 | 0.28 | 35000 | ERW | 8.625 | 715 |  |  | 23.388 | [7 empty] | AGM 1 | 638.29 | AGM 2 | 2558.24 | 0.28 | 0.47 | 38.69 | 1.05 | 0.74 | 940 | 1.89 | 4.24 | 33.6754 | -118.0151 | 26.953 | 3.0D 40.5 deg right turn over bend
GWD 950 | Girth Weld |  | 2390.52 | 1.89 | 0.28 | 35000 | ERW | 8.625 | 715 | [10 empty] | AGM 1 | 638.75 | AGM 2 | 2557.77 | 0.74 | 1.89 | 1.05 | 0.74 | 1.89 | 950 | 4.24 | 36.87 | 33.6754 | -118.0151 | 26.956
GWD 960 | Girth Weld |  | 2392.41 | 4.24 | 0.28 | 35000 | ERW | 8.625 | 715 | [10 empty] | AGM 1 | 640.64 | AGM 2 | 2555.88 | 1.89 | 4.24 | 0.74 | 1.89 | 4.24 | 960 | 36.87 | 42.96 | 33.6755 | -118.0151 | 26.956
GWD 970 | Girth Weld |  | 2396.65 | 0.16 | 0.28 | 35000 | SMLS | 8.625 | 715 | [10 empty] | AGM 1 | 644.89 | AGM 2 | 2551.64 | 4.24 | 36.87 | 1.89 | 4.24 | 36.87 | 970 | 42.96 | 40.85 | 33.6755 | -118.0151 | 26.975
DMA 37 | Metal Loss | Ext | 2396.81 | 0.29 | 0.28 | 35000 | SMLS | 8.625 | 715 | 18.3951 | 0.052 | 1.522 | 1.004 | 3:40 | 2813 | 0.35302 | 18 | 1.52 | 2790 | AGM 1 | 645.04 | AGM 2 | 2551.48 | 0.15 | 36.72 | 1.89 | 4.24 | 36.87 | 970 | 42.96 | 40.85 | 33.6755 | -118.0151 | 26.975
DMA 38 | Metal Loss | Ext | 2397.1 | 0.08 | 0.28 | 35000 | SMLS | 8.625 | 715 | 14.2328 | 0.04 | 1.885 | 1.389 | 2:48 | 2814 | 0.3529 | 14 | 1.88 | 2793 | AGM 1 | 645.33 | AGM 2 | 2551.19 | 0.45 | 36.43 | 1.89 | 4.24 | 36.87 | 970 | 42.96 | 40.85 | 33.6755 | -118.0151 | 26.978
DMA 39 | Metal Loss | Ext | 2397.17 | 0.03 | 0.28 | 35000 | SMLS | 8.625 | 715 | 20.8498 | 0.058 | 0.687 | 0.674 | 7:17 | 2887 | 0.34397 | 21 | 0.69 | 2879 | AGM 1 | 645.41 | AGM 2 | 2551.11 | 0.52 | 36.35 | 1.89 | 4.24 | 36.87 | 970 | 42.96 | 40.85 | 33.6755 | -118.0151 | 26.982
DMA 40 | Metal Loss | Ext | 2397.2 | 0.13 | 0.28 | 35000 | SMLS | 8.625 | 715 | 27.7753 | 0.078 | 1.128 | 0.667 | 5:48 | 2807 | 0.35378 | 28 | 1.13 | 2780 | AGM 1 | 645.44 | AGM 2 | 2551.08 | 0.55 | 36.32 | 1.89 | 4.24 | 36.87 | 970 | 42.96 | 40.85 | 33.6755 | -118.0151 | 26.981
DMA 41 | Metal Loss | Ext | 2397.33 | 0.03 | 0.28 | 35000 | SMLS | 8.625 | 715 | 16.9655 | 0.048 | 1.823 | 2.47 | 12:28 | 2796 | 0.35517 | 17 | 1.82 | 2771 | AGM 1 | 645.57 | AGM 2 | 2550.95 | 0.68 | 36.19 | 1.89 | 4.24 | 36.87 | 970 | 42.96 | 40.85 | 33.6755 | -118.0151 | 26.982
DMA 42 | Metal Loss | Ext | 2397.36 | 0.46 | 0.28 | 35000 | SMLS | 8.625 | 715 | 17.092 | 0.048 | 0.896 | 0.51 | 2:11 | 2878 | 0.34505 | 17 | 0.9 | 2868 | AGM 1 | 645.59 | AGM 2 | 2550.93 | 0.71 | 36.16 | 1.89 | 4.24 | 36.87 | 970 | 42.96 | 40.85 | 33.6755 | -118.0151 | 26.982
DMA 43 | Metal Loss | Ext | 2397.82 | 0.04 | 0.28 | 35000 | SMLS | 8.625 | 715 | 38.0215 | 0.106 | 1.937 | 0.897 | 5:41 | 2570 | 0.3864 | 38 | 1.94 | 2484 | AGM 1 | 646.05 | AGM 2 | 2550.47 | 1.17 | 35.71 | 1.89 | 4.24 | 36.87 | 970 | 42.96 | 40.85 | 33.6755 | -118.0151 | 26.988
DMA 44 | Metal Loss | Ext | 2397.86 | 0.12 | 0.28 | 35000 | SMLS | 8.625 | 715 | 45.0997 | 0.126 | 0.583 | 0.579 | 3:54 | 2848 | 0.34869 | 45 | 0.58 | 2826 | AGM 1 | 646.09 | AGM 2 | 2550.43 | 1.21 | 35.66 | 1.89 | 4.24 | 36.87 | 970 | 42.96 | 40.85 | 33.6755 | -118.0151 | 26.988
DMA 45 | Metal Loss | Ext | 2397.98 | 0.19 | 0.28 | 35000 | SMLS | 8.625 | 715 | 16.8339 | 0.047 | 0.805 | 0.741 | 2:06 | 2886 | 0.34409 | 17 | 0.81 | 2878 | AGM 1 | 646.21 | AGM 2 | 2550.31 | 1.33 | 35.55 | 1.89 | 4.24 | 36.87 | 970 | 42.96 | 40.85 | 33.6755 | -118.0151 | 26.991
CLS 8 | Cluster | Ext | 2398.17 | 35.35 | 0.28 | 35000 | SMLS | 8.625 | 715 | 27.8812 | 0.078 | 1.517 | 2.144 | 2:35 | 2744 | 0.3619 | 25 | 1.52 | 2730 | AGM 1 | 646.4 | AGM 2 | 2550.12 | 1.52 | 35.35 | 1.89 | 4.24 | 36.87 | 970 | 42.96 | 40.85 | 33.6755 | -118.0151 | 26.995 | CLS C
GWD 980 | Girth Weld |  | 2433.52 | 39.93 | 0.28 | 35000 | SMLS | 8.625 | 715 | [10 empty] | AGM 1 | 681.76 | AGM 2 | 2514.76 | 36.87 | 42.96 | 4.24 | 36.87 | 42.96 | 980 | 40.85 | 42.95 | 33.6755 | -118.015 | 27.1
DMA 48 | Metal Loss | Ext | 2473.45 | 0.58 | 0.28 | 35000 | SMLS | 8.625 | 715 | 12.5027 | 0.035 | 0.826 | 0.607 | 8:06 | 2895 | 0.34302 | 13 | 0.83 | 2889 | AGM 1 | 721.69 | AGM 2 | 2474.84 | 39.93 | 3.03 | 4.24 | 36.87 | 42.96 | 980 | 40.85 | 42.95 | 33.6755 | -118.0149 | 27.647
CLS 9 | Cluster | Ext | 2474.03 | 0.2 | 0.28 | 35000 | SMLS | 8.625 | 715 | 15.1086 | 0.042 | 0.8 | 2.303 | 6:21 | 2890 | 0.34362 | 15 | 0.8 | 2884 | AGM 1 | 722.26 | AGM 2 | 2474.26 | 40.5 | 2.45 | 4.24 | 36.87 | 42.96 | 980 | 40.85 | 42.95 | 33.6755 | -118.0149 | 27.663 | CLS C
DMA 51 | Metal Loss | Ext | 2474.23 | 0.16 | 0.28 | 35000 | SMLS | 8.625 | 715 | 18.7644 | 0.053 | 0.563 | 0.511 | 6:48 | 2900 | 0.34243 | 19 | 0.56 | 2896 | AGM 1 | 722.46 | AGM 2 | 2474.06 | 40.71 | 2.25 | 4.24 | 36.87 | 42.96 | 980 | 40.85 | 42.95 | 33.6755 | -118.0149 | 27.667
DMA 52 | Metal Loss | Ext | 2474.39 | 0.13 | 0.28 | 35000 | SMLS | 8.625 | 715 | 11.4862 | 0.032 | 0.383 | 0.572 | 8:38 | 2916 | 0.34055 | 11 | 0.38 | 2915 | AGM 1 | 722.63 | AGM 2 | 2473.9 | 40.87 | 2.09 | 4.24 | 36.87 | 42.96 | 980 | 40.85 | 42.95 | 33.6755 | -118.0149 | 27.67
DMA 53 | Metal Loss | Ext | 2474.52 | 1.97 | 0.28 | 35000 | SMLS | 8.625 | 715 | 14.3032 | 0.04 | 0.526 | 0.775 | 8:11 | 2908 | 0.34149 | 14 | 0.53 | 2905 | AGM 1 | 722.75 | AGM 2 | 2473.77 | 40.99 | 1.97 | 4.24 | 36.87 | 42.96 | 980 | 40.85 | 42.95 | 33.6755 | -118.0149 | 27.673
GWD 990 | Girth Weld |  | 2476.48 | 40.85 | 0.28 | 35000 | SMLS | 8.625 | 715 | [10 empty] | AGM 1 | 724.72 | AGM 2 | 2471.8 | 42.96 | 40.85 | 36.87 | 42.96 | 40.85 | 990 | 42.95 | 43.54 | 33.6755 | -118.0149 | 27.722
GWD 1000 | Girth Weld |  | 2517.34 | 42.95 | 0.28 | 35000 | SMLS | 8.625 | 715 | [10 empty] | AGM 1 | 765.57 | AGM 2 | 2430.95 | 40.85 | 42.95 | 42.96 | 40.85 | 42.95 | 1000 | 43.54 | 42.84 | 33.6756 | -118.0147 | 28.662
GWD 1010 | Girth Weld |  | 2560.28 | 43.54 | 0.28 | 35000 | SMLS | 8.625 | 715 | [10 empty] | AGM 1 | 808.52 | AGM 2 | 2388 | 42.95 | 43.54 | 40.85 | 42.95 | 43.54 | 1010 | 42.84 | 43.74 | 33.6756 | -118.0146 | 30.045
GWD 1020 | Girth Weld |  | 2603.83 | 42.84 | 0.28 | 35000 | SMLS | 8.625 | 715 | [10 empty] | AGM 1 | 852.06 | AGM 2 | 2344.46 | 43.54 | 42.84 | 42.95 | 43.54 | 42.84 | 1020 | 43.74 | 41.96 | 33.6757 | -118.0145 | 31.659
GWD 1030 | Girth Weld |  | 2646.66 | 43.74 | 0.28 | 35000 | SMLS | 8.625 | 715 | [10 empty] | AGM 1 | 894.9 | AGM 2 | 2301.62 | 42.84 | 43.74 | 43.54 | 42.84 | 43.74 | 1030 | 41.96 | 25.8 | 33.6757 | -118.0144 | 32.614
GWD 1040 | Girth Weld |  | 2690.4 | 41.96 | 0.28 | 35000 | SMLS | 8.625 | 715 | [10 empty] | AGM 1 | 938.64 | AGM 2 | 2257.88 | 43.74 | 41.96 | 42.84 | 43.74 | 41.96 | 1040 | 25.8 | 8.41 | 33.6757 | -118.0142 | 34.106
GWD 1050 | Girth Weld |  | 2732.37 | 0.27 | 0.28 | 35000 | SMLS | 8.625 | 715 | [10 empty] | AGM 1 | 980.6 | AGM 2 | 2215.92 | 41.96 | 25.8 | 43.74 | 41.96 | 25.8 | 1050 | 8.41 | 9.01 | 33.6758 | -118.0141 | 35.307
DMA 54 | Metal Loss | Ext | 2732.63 | 0.08 | 0.28 | 35000 | SMLS | 8.625 | 715 | 17.404 | 0.049 | 0.723 | 0.575 | 10:31 | 2891 | 0.3435 | 17 | 0.72 | 2884 | AGM 1 | 980.87 | AGM 2 | 2215.66 | 0.27 | 25.53 | 43.74 | 41.96 | 25.8 | 1050 | 8.41 | 9.01 | 33.6758 | -118.0141 | 35.321
DMA 55 | Metal Loss | Ext | 2732.71 | 0 | 0.28 | 35000 | SMLS | 8.625 | 715 | 23.8168 | 0.067 | 1.213 | 1.192 | 5:14 | 2815 | 0.35277 | 24 | 1.21 | 2792 | AGM 1 | 980.95 | AGM 2 | 2215.57 | 0.35 | 25.45 | 43.74 | 41.96 | 25.8 | 1050 | 8.41 | 9.01 | 33.6758 | -118.0141 | 35.321
DMA 56 | Metal Loss | Ext | 2732.72 | 0.12 | 0.28 | 35000 | SMLS | 8.625 | 715 | 13.4498 | 0.038 | 1.068 | 0.857 | 3:18 | 2877 | 0.34517 | 13 | 1.07 | 2868 | AGM 1 | 980.95 | AGM 2 | 2215.57 | 0.35 | 25.45 | 43.74 | 41.96 | 25.8 | 1050 | 8.41 | 9.01 | 33.6758 | -118.0141 | 35.32
CLS 10 | Cluster | Ext | 2732.83 | 0.11 | 0.28 | 35000 | SMLS | 8.625 | 715 | 20.6547 | 0.058 | 1.664 | 3.882 | 11:38 | 2782 | 0.35696 | 20 | 1.66 | 2755 | AGM 1 | 981.07 | AGM 2 | 2215.46 | 0.47 | 25.33 | 43.74 | 41.96 | 25.8 | 1050 | 8.41 | 9.01 | 33.6758 | -118.0141 | 35.327 | CLS C
DMA 59 | Metal Loss | Ext | 2732.94 | 24.16 | 0.28 | 35000 | SMLS | 8.625 | 715 | 28.488 | 0.08 | 0.723 | 0.573 | 6:44 | 2865 | 0.34662 | 28 | 0.72 | 2852 | AGM 1 | 981.17 | AGM 2 | 2215.35 | 0.57 | 25.23 | 43.74 | 41.96 | 25.8 | 1050 | 8.41 | 9.01 | 33.6758 | -118.0141 | 35.331
SLV 1 | Sleeve Start |  | 2757.1 | 1.06 | 0.28 | 35000 | SMLS | 8.625 | 715 |  |  | 27.242 | [7 empty] | AGM 1 | 1005.33 | AGM 2 | 2191.19 | 24.73 | 1.07 | 43.74 | 41.96 | 25.8 | 1050 | 8.41 | 9.01 | 33.6758 | -118.014 | 36.555 | Repair Sleeve - Start
GWD 1060 | Girth Weld |  | 2758.17 | 0.08 | 0.28 | 35000 | SMLS | 8.625 | 715 | [10 empty] | AGM 1 | 1006.4 | AGM 2 | 2190.12 | 25.8 | 8.41 | 41.96 | 25.8 | 8.41 | 1060 | 9.01 | 1.1 | 33.6758 | -118.014 | 36.63
BND 27 | Bend |  | 2758.25 | 1.12 | 0.28 | 35000 | SMLS | 8.625 | 715 |  |  | 23.386 | [7 empty] | AGM 1 | 1006.48 | AGM 2 | 2190.04 | 0.08 | 8.33 | 41.96 | 25.8 | 8.41 | 1060 | 9.01 | 1.1 | 33.6758 | -118.014 | 36.637 | 9.8D 15.4 deg left turn bend
SLV 2 | Sleeve End |  | 2759.37 | 6.45 | 0.28 | 35000 | SMLS | 8.625 | 715 | [10 empty] | AGM 1 | 1007.61 | AGM 2 | 2188.92 | 1.21 | 7.2 | 41.96 | 25.8 | 8.41 | 1060 | 9.01 | 1.1 | 33.6758 | -118.014 | 36.711 | Repair Sleeve - End
SLV 3 | Sleeve Start |  | 2765.82 | 0.76 | 0.28 | 35000 | SMLS | 8.625 | 715 |  |  | 13.244 | [7 empty] | AGM 1 | 1014.05 | AGM 2 | 2182.47 | 7.65 | 0.76 | 41.96 | 25.8 | 8.41 | 1060 | 9.01 | 1.1 | 33.6758 | -118.014 | 37.096 | Repair Sleeve - Start
GWD 1070 | Girth Weld |  | 2766.58 | 0.35 | 0.28 | 35000 | SMLS | 8.625 | 715 | [10 empty] | AGM 1 | 1014.81 | AGM 2 | 2181.71 | 8.41 | 9.01 | 25.8 | 8.41 | 9.01 | 1070 | 1.1 | 1.83 | 33.6758 | -118.014 | 37.137
SLV 4 | Sleeve End |  | 2766.92 | 1.42 | 0.28 | 35000 | SMLS | 8.625 | 715 | [10 empty] | AGM 1 | 1015.16 | AGM 2 | 2181.37 | 0.35 | 8.66 | 25.8 | 8.41 | 9.01 | 1070 | 1.1 | 1.83 | 33.6758 | -118.014 | 37.155 | Repair Sleeve - End
SLV 5 | Sleeve Start |  | 2768.34 | 1.25 | 0.28 | 35000 | SMLS | 8.625 | 715 |  |  | 19.295 | [7 empty] | AGM 1 | 1016.57 | AGM 2 | 2179.95 | 1.76 | 7.25 | 25.8 | 8.41 | 9.01 | 1070 | 1.1 | 1.83 | 33.6758 | -118.014 | 37.234 | Repair Sleeve - Start
DNT 1 | Deformation |  | 2769.59 | 0.36 | 0.28 | 35000 | SMLS | 8.625 | 715 | 1.914 | 0.165 | 1.938 | 1.854 | 2:18 | [5 empty] | AGM 1 | 1017.83 | AGM 2 | 2178.7 | 3.02 | 5.99 | 25.8 | 8.41 | 9.01 | 1070 | 1.1 | 1.83 | 33.6758 | -118.014 | 37.306 | Under SLV
SLV 6 | Sleeve End |  | 2769.95 | 5.64 | 0.28 | 35000 | SMLS | 8.625 | 715 | [10 empty] | AGM 1 | 1018.18 | AGM 2 | 2178.34 | 3.37 | 5.64 | 25.8 | 8.41 | 9.01 | 1070 | 1.1 | 1.83 | 33.6758 | -118.014 | 37.324 | Repair Sleeve - End
GWD 1080 | Girth Weld |  | 2775.58 | 1.1 | 0.219 | 35000 | ERW | 8.625 | 715 | [10 empty] | AGM 1 | 1023.82 | AGM 2 | 2172.7 | 9.01 | 1.1 | 8.41 | 9.01 | 1.1 | 1080 | 1.83 | 38.72 | 33.6758 | -118.014 | 37.621
GWD 1090 | Girth Weld |  | 2776.68 | 0.99 | 0.219 | 35000 | ERW | 8.625 | 715 | [10 empty] | AGM 1 | 1024.92 | AGM 2 | 2171.6 | 1.1 | 1.83 | 9.01 | 1.1 | 1.83 | 1090 | 38.72 | 40.38 | 33.6758 | -118.014 | 37.671
BND 28 | Bend |  | 2777.68 | 0.84 | 0.219 | 35000 | ERW | 8.625 | 715 |  |  | 26.139 | [7 empty] | AGM 1 | 1025.91 | AGM 2 | 2170.61 | 1 | 0.84 | 9.01 | 1.1 | 1.83 | 1090 | 38.72 | 40.38 | 33.6758 | -118.014 | 37.693 | 3.0D 53.1 deg left turn over bend
GWD 1100 | Girth Weld |  | 2778.52 | 38.72 | 0.219 | 35000 | ERW | 8.625 | 715 | [10 empty] | AGM 1 | 1026.75 | AGM 2 | 2169.77 | 1.83 | 38.72 | 1.1 | 1.83 | 38.72 | 1100 | 40.38 | 2.1 | 33.6758 | -118.014 | 37.686
GWD 1110 | Girth Weld |  | 2817.24 | 40.38 | 0.219 | 35000 | ERW | 8.625 | 715 | [10 empty] | AGM 1 | 1065.47 | AGM 2 | 2131.05 | 38.72 | 40.38 | 1.83 | 38.72 | 40.38 | 1110 | 2.1 | 28.4 | 33.6759 | -118.0139 | 36.741
GWD 1120 | Girth Weld |  | 2857.62 | 1.18 | 0.219 | 35000 | ERW | 8.625 | 715 | [10 empty] | AGM 1 | 1105.86 | AGM 2 | 2090.67 | 40.38 | 2.1 | 38.72 | 40.38 | 2.1 | 1120 | 28.4 | 40.89 | 33.6761 | -118.0139 | 37.218
BND 29 | Bend |  | 2858.8 | 0.92 | 0.219 | 35000 | ERW | 8.625 | 715 |  |  | 27.763 | [7 empty] | AGM 1 | 1107.03 | AGM 2 | 2089.49 | 1.18 | 0.92 | 38.72 | 40.38 | 2.1 | 1120 | 28.4 | 40.89 | 33.6761 | -118.0139 | 37.244 | 3.0D 60.7 deg right turn bend
GWD 1130 | Girth Weld |  | 2859.72 | 28.39 | 0.219 | 35000 | ERW | 8.625 | 715 | [10 empty] | AGM 1 | 1107.95 | AGM 2 | 2088.57 | 2.1 | 28.4 | 40.38 | 2.1 | 28.4 | 1130 | 40.89 | 40.62 | 33.6761 | -118.0139 | 37.275
GWD 1140 | Girth Weld |  | 2888.11 | 40.89 | 0.219 | 35000 | ERW | 8.625 | 715 | [10 empty] | AGM 1 | 1136.35 | AGM 2 | 2060.17 | 28.4 | 40.89 | 2.1 | 28.4 | 40.89 | 1140 | 40.62 | 1.88 | 33.6761 | -118.0139 | 37.767
GWD 1150 | Girth Weld |  | 2929 | 40.62 | 0.219 | 35000 | ERW | 8.625 | 715 | [10 empty] | AGM 1 | 1177.24 | AGM 2 | 2019.29 | 40.89 | 40.62 | 28.4 | 40.89 | 40.62 | 1150 | 1.88 | 9.42 | 33.6761 | -118.0137 | 37.461
GWD 1160 | Girth Weld |  | 2969.62 | 1.13 | 0.219 | 35000 | ERW | 8.625 | 715 | [10 empty] | AGM 1 | 1217.86 | AGM 2 | 1978.66 | 40.62 | 1.88 | 40.89 | 40.62 | 1.88 | 1160 | 9.42 | 0.99 | 33.6762 | -118.0136 | 36.762
BND 30 | Bend |  | 2970.76 | 0.74 | 0.219 | 35000 | ERW | 8.625 | 715 |  |  | 26.59 | [7 empty] | AGM 1 | 1218.99 | AGM 2 | 1977.53 | 1.13 | 0.74 | 40.89 | 40.62 | 1.88 | 1160 | 9.42 | 0.99 | 33.6762 | -118.0136 | 36.743 | 3.0D 52.7 deg left turn over bend
GWD 1170 | Girth Weld |  | 2971.5 | 9.42 | 0.219 | 35000 | ERW | 8.625 | 715 | [10 empty] | AGM 1 | 1219.74 | AGM 2 | 1976.78 | 1.88 | 9.42 | 40.62 | 1.88 | 9.42 | 1170 | 0.99 | 20.02 | 33.6762 | -118.0136 | 36.714
GWD 1180 | Girth Weld |  | 2980.92 | 0.56 | 0.219 | 35000 | ERW | 8.625 | 715 | [10 empty] | AGM 1 | 1229.16 | AGM 2 | 1967.37 | 9.42 | 0.99 | 1.88 | 9.42 | 0.99 | 1180 | 20.02 | 0.93 | 33.6762 | -118.0136 | 36.208
BND 31 | Bend |  | 2981.49 | 0.43 | 0.219 | 35000 | ERW | 8.625 | 715 |  |  | 11.929 | [7 empty] | AGM 1 | 1229.72 | AGM 2 | 1966.8 | 0.56 | 0.43 | 1.88 | 9.42 | 0.99 | 1180 | 20.02 | 0.93 | 33.6762 | -118.0136 | 36.258 | 3.0D 30.1 deg left turn sag bend
GWD 1190 | Girth Weld |  | 2981.92 | 20.02 | 0.219 | 35000 | ERW | 8.625 | 715 | [10 empty] | AGM 1 | 1230.15 | AGM 2 | 1966.37 | 0.99 | 20.02 | 9.42 | 0.99 | 20.02 | 1190 | 0.93 | 3.03 | 33.6762 | -118.0136 | 36.364
GWD 1200 | Girth Weld |  | 3001.94 | 0.93 | 0.219 | 35000 | ERW | 8.625 | 715 | [10 empty] | AGM 1 | 1250.17 | AGM 2 | 1946.35 | 20.02 | 0.93 | 0.99 | 20.02 | 0.93 | 1200 | 3.03 | 37.79 | 33.6763 | -118.0136 | 44.735
GWD 1210 | Girth Weld |  | 3002.87 | 1.39 | 0.219 | 35000 | ERW | 8.625 | 715 | [10 empty] | AGM 1 | 1251.1 | AGM 2 | 1945.42 | 0.93 | 3.03 | 20.02 | 0.93 | 3.03 | 1210 | 37.79 | 3.83 | 33.6763 | -118.0136 | 44.979
BND 32 | Bend |  | 3004.26 | 1.64 | 0.219 | 35000 | ERW | 8.625 | 715 |  |  | 45.054 | [7 empty] | AGM 1 | 1252.5 | AGM 2 | 1944.03 | 1.39 | 1.63 | 20.02 | 0.93 | 3.03 | 1210 | 37.79 | 3.83 | 33.6763 | -118.0136 | 44.997 | 3.0D 81.4 deg right turn over bend
GWD 1220 | Girth Weld |  | 3005.9 | 37.79 | 0.219 | 35000 | ERW | 8.625 | 715 | [10 empty] | AGM 1 | 1254.13 | AGM 2 | 1942.39 | 3.03 | 37.79 | 0.93 | 3.03 | 37.79 | 1220 | 3.83 | 0.48 | 33.6763 | -118.0136 | 44.987
GWD 1230 | Girth Weld |  | 3043.69 | 3.83 | 0.219 | 35000 | ERW | 8.625 | 715 | [10 empty] | AGM 1 | 1291.92 | AGM 2 | 1904.6 | 37.79 | 3.83 | 3.03 | 37.79 | 3.83 | 1230 | 0.48 | 20.14 | 33.6763 | -118.0135 | 46.648
GWD 1240 | Girth Weld |  | 3047.52 | 0.28 | 0.219 | 35000 | ERW | 8.625 | 715 | [10 empty] | AGM 1 | 1295.76 | AGM 2 | 1900.76 | 3.83 | 0.48 | 37.79 | 3.83 | 0.48 | 1240 | 20.14 | 40.86 | 33.6763 | -118.0134 | 46.945
BND 33 | Bend |  | 3047.8 | 0.2 | 0.219 | 35000 | ERW | 8.625 | 715 |  |  | 5.787 | [7 empty] | AGM 1 | 1296.04 | AGM 2 | 1900.48 | 0.28 | 0.2 | 37.79 | 3.83 | 0.48 | 1240 | 20.14 | 40.86 | 33.6763 | -118.0134 | 46.965 | 3.0D 14.0 deg left turn bend
GWD 1250 | Girth Weld |  | 3048.01 | 20.14 | 0.219 | 35000 | ERW | 8.625 | 715 | [10 empty] | AGM 1 | 1296.24 | AGM 2 | 1900.28 | 0.48 | 20.14 | 3.83 | 0.48 | 20.14 | 1250 | 40.86 | 0.41 | 33.6763 | -118.0134 | 46.98
GWD 1260 | Girth Weld |  | 3068.15 | 40.86 | 0.219 | 35000 | ERW | 8.625 | 715 | [10 empty] | AGM 1 | 1316.38 | AGM 2 | 1880.14 | 20.14 | 40.86 | 0.48 | 20.14 | 40.86 | 1260 | 0.41 | 36.99 | 33.6763 | -118.0134 | 48.589
GWD 1270 | Girth Weld |  | 3109.01 | 0.19 | 0.219 | 35000 | ERW | 8.625 | 715 | [10 empty] | AGM 1 | 1357.24 | AGM 2 | 1839.28 | 40.86 | 0.41 | 20.14 | 40.86 | 0.41 | 1270 | 36.99 | 40.83 | 33.6763 | -118.0132 | 51.641
BND 34 | Bend |  | 3109.2 | 0.22 | 0.219 | 35000 | ERW | 8.625 | 715 |  |  | 4.961 | [7 empty] | AGM 1 | 1357.43 | AGM 2 | 1839.09 | 0.19 | 0.22 | 20.14 | 40.86 | 0.41 | 1270 | 36.99 | 40.83 | 33.6763 | -118.0132 | 51.648 | 3.0D 10.2 deg left turn bend
GWD 1280 | Girth Weld |  | 3109.42 | 36.99 | 0.219 | 35000 | ERW | 8.625 | 715 | [10 empty] | AGM 1 | 1357.66 | AGM 2 | 1838.86 | 0.41 | 36.99 | 40.86 | 0.41 | 36.99 | 1280 | 40.83 | 0.41 | 33.6763 | -118.0132 | 51.654
GWD 1290 | Girth Weld |  | 3146.42 | 40.83 | 0.219 | 35000 | ERW | 8.625 | 715 | [10 empty] | AGM 1 | 1394.65 | AGM 2 | 1801.87 | 36.99 | 40.83 | 0.41 | 36.99 | 40.83 | 1290 | 0.41 | 1.13 | 33.6763 | -118.0131 | 52.4
GWD 1300 | Girth Weld |  | 3187.24 | 0.2 | 0.219 | 35000 | ERW | 8.625 | 715 | [10 empty] | AGM 1 | 1435.48 | AGM 2 | 1761.04 | 40.83 | 0.41 | 36.99 | 40.83 | 0.41 | 1300 | 1.13 | 4.12 | 33.6764 | -118.013 | 52.806
BND 35 | Bend |  | 3187.44 | 0.21 | 0.219 | 35000 | ERW | 8.625 | 715 |  |  | 4.961 | [7 empty] | AGM 1 | 1435.68 | AGM 2 | 1760.84 | 0.2 | 0.21 | 36.99 | 40.83 | 0.41 | 1300 | 1.13 | 4.12 | 33.6764 | -118.013 | 52.808 | 3.0D 15.3 deg left turn sag bend
GWD 1310 | Girth Weld |  | 3187.66 | 1.13 | 0.219 | 35000 | ERW | 8.625 | 715 | [10 empty] | AGM 1 | 1435.89 | AGM 2 | 1760.63 | 0.41 | 1.13 | 40.83 | 0.41 | 1.13 | 1310 | 4.12 | 19.51 | 33.6764 | -118.013 | 52.812
GWD 1320 | Girth Weld |  | 3188.79 | 4.12 | 0.28 | 35000 | SMLS | 8.625 | 715 | [10 empty] | AGM 1 | 1437.03 | AGM 2 | 1759.5 | 1.13 | 4.12 | 0.41 | 1.13 | 4.12 | 1320 | 19.51 | 20.47 | 33.6764 | -118.013 | 52.85
GWD 1330 | Girth Weld |  | 3192.91 | 19.51 | 0.28 | 35000 | SMLS | 8.625 | 715 | [10 empty] | AGM 1 | 1441.15 | AGM 2 | 1755.37 | 4.12 | 19.51 | 1.13 | 4.12 | 19.51 | 1330 | 20.47 | 20.41 | 33.6764 | -118.013 | 53.005
GWD 1340 | Girth Weld |  | 3212.43 | 3.21 | 0.28 | 35000 | SMLS | 8.625 | 715 | [10 empty] | AGM 1 | 1460.66 | AGM 2 | 1735.86 | 19.51 | 20.47 | 4.12 | 19.51 | 20.47 | 1340 | 20.41 | 17.24 | 33.6764 | -118.0129 | 53.632
DMA 60 | Metal Loss | Ext | 3215.64 | 17.26 | 0.28 | 35000 | SMLS | 8.625 | 715 | 19.5425 | 0.055 | 0.841 | 0.744 | 12:50 | 2875 | 0.34541 | 20 | 0.84 | 2865 | AGM 1 | 1463.87 | AGM 2 | 1732.65 | 3.21 | 17.26 | 4.12 | 19.51 | 20.47 | 1340 | 20.41 | 17.24 | 33.6764 | -118.0129 | 53.734
GWD 1350 | Girth Weld |  | 3232.89 | 16.24 | 0.28 | 35000 | SMLS | 8.625 | 715 | [10 empty] | AGM 1 | 1481.13 | AGM 2 | 1715.4 | 20.47 | 20.41 | 19.51 | 20.47 | 20.41 | 1350 | 17.24 | 19.53 | 33.6764 | -118.0129 | 54.289
DMA 61 | Metal Loss | Ext | 3249.14 | 1.31 | 0.28 | 35000 | SMLS | 8.625 | 715 | 20.8991 | 0.059 | 1.091 | 0.632 | 2:36 | 2844 | 0.34918 | 21 | 1.09 | 2828 | AGM 1 | 1497.37 | AGM 2 | 1699.15 | 16.25 | 4.17 | 19.51 | 20.47 | 20.41 | 1350 | 17.24 | 19.53 | 33.6764 | -118.0128 | 55.016
DMA 62 | Metal Loss | Ext | 3250.45 | 2.86 | 0.28 | 35000 | SMLS | 8.625 | 715 | 23.9715 | 0.067 | 0.725 | 0.6 | 8:41 | 2876 | 0.34529 | 24 | 0.73 | 2866 | AGM 1 | 1498.68 | AGM 2 | 1697.84 | 17.56 | 2.86 | 19.51 | 20.47 | 20.41 | 1350 | 17.24 | 19.53 | 33.6765 | -118.0128 | 55.062
GWD 1360 | Girth Weld |  | 3253.3 | 17.24 | 0.28 | 35000 | SMLS | 8.625 | 715 | [10 empty] | AGM 1 | 1501.54 | AGM 2 | 1694.98 | 20.41 | 17.24 | 20.47 | 20.41 | 17.24 | 1360 | 19.53 | 17.75 | 33.6765 | -118.0128 | 55.15
GWD 1370 | Girth Weld |  | 3270.55 | 19.53 | 0.28 | 35000 | SMLS | 8.625 | 715 | [10 empty] | AGM 1 | 1518.78 | AGM 2 | 1677.74 | 17.24 | 19.53 | 20.41 | 17.24 | 19.53 | 1370 | 17.75 | 20.93 | 33.6765 | -118.0128 | 55.908
GWD 1380 | Girth Weld |  | 3290.08 | 17.75 | 0.28 | 35000 | SMLS | 8.625 | 715 | [10 empty] | AGM 1 | 1538.32 | AGM 2 | 1658.2 | 19.53 | 17.75 | 17.24 | 19.53 | 17.75 | 1380 | 20.93 | 19.55 | 33.6765 | -118.0127 | 56.913
GWD 1390 | Girth Weld |  | 3307.83 | 7.31 | 0.28 | 35000 | SMLS | 8.625 | 715 | [10 empty] | AGM 1 | 1556.07 | AGM 2 | 1640.45 | 17.75 | 20.93 | 19.53 | 17.75 | 20.93 | 1390 | 19.55 | 21.28 | 33.6765 | -118.0127 | 57.563
PMA 3 | Pipe Mill | Int | 3315.15 | 7.92 | 0.28 | 35000 | SMLS | 8.625 | 715 | 36.7925 | 0.103 | 0.615 | 0.677 | 9:46 | [5 empty] | AGM 1 | 1563.38 | AGM 2 | 1633.14 | 7.31 | 13.61 | 19.53 | 17.75 | 20.93 | 1390 | 19.55 | 21.28 | 33.6765 | -118.0127 | 57.631
PMA 4 | Pipe Mill | Int | 3323.07 | 5.69 | 0.28 | 35000 | SMLS | 8.625 | 715 | 12.0077 | 0.034 | 0.934 | 1.598 | 10:10 | [5 empty] | AGM 1 | 1571.3 | AGM 2 | 1625.22 | 15.23 | 5.69 | 19.53 | 17.75 | 20.93 | 1390 | 19.55 | 21.28 | 33.6766 | -118.0126 | 57.727
GWD 1400 | Girth Weld |  | 3328.76 | 19.55 | 0.28 | 35000 | SMLS | 8.625 | 715 | [10 empty] | AGM 1 | 1576.99 | AGM 2 | 1619.53 | 20.93 | 19.55 | 17.75 | 20.93 | 19.55 | 1400 | 21.28 | 21.36 | 33.6766 | -118.0126 | 57.851
GWD 1410 | Girth Weld |  | 3348.31 | 21.28 | 0.28 | 35000 | SMLS | 8.625 | 715 | [10 empty] | AGM 1 | 1596.54 | AGM 2 | 1599.98 | 19.55 | 21.28 | 20.93 | 19.55 | 21.28 | 1410 | 21.36 | 22.47 | 33.6766 | -118.0126 | 58.559
GWD 1420 | Girth Weld |  | 3369.59 | 21.35 | 0.28 | 35000 | SMLS | 8.625 | 715 | [10 empty] | AGM 1 | 1617.82 | AGM 2 | 1578.7 | 21.28 | 21.36 | 19.55 | 21.28 | 21.36 | 1420 | 22.47 | 20.64 | 33.6766 | -118.0125 | 59.307
GWD 1430 | Girth Weld |  | 3390.94 | 22.47 | 0.25 | 35000 | SMLS | 8.625 | 715 | [10 empty] | AGM 1 | 1639.18 | AGM 2 | 1557.35 | 21.36 | 22.47 | 21.28 | 21.36 | 22.47 | 1430 | 20.64 | 19.09 | 33.6767 | -118.0124 | 60.218 | Estimated WT 0.250
GWD 1440 | Girth Weld |  | 3413.41 | 20.64 | 0.25 | 35000 | SMLS | 8.625 | 715 | [10 empty] | AGM 1 | 1661.65 | AGM 2 | 1534.88 | 22.47 | 20.64 | 21.36 | 22.47 | 20.64 | 1440 | 19.09 | 19.07 | 33.6767 | -118.0124 | 61.253
GWD 1450 | Girth Weld |  | 3434.05 | 19.09 | 0.28 | 35000 | SMLS | 8.625 | 715 | [10 empty] | AGM 1 | 1682.29 | AGM 2 | 1514.23 | 20.64 | 19.09 | 22.47 | 20.64 | 19.09 | 1450 | 19.07 | 18.61 | 33.6767 | -118.0123 | 62.115
GWD 1460 | Girth Weld |  | 3453.14 | 19.07 | 0.28 | 35000 | SMLS | 8.625 | 715 | [10 empty] | AGM 1 | 1701.38 | AGM 2 | 1495.15 | 19.09 | 19.07 | 20.64 | 19.09 | 19.07 | 1460 | 18.61 | 20.09 | 33.6768 | -118.0123 | 62.745
GWD 1470 | Girth Weld |  | 3472.21 | 18.61 | 0.25 | 35000 | ERW | 8.625 | 715 | [10 empty] | AGM 1 | 1720.44 | AGM 2 | 1476.08 | 19.07 | 18.61 | 19.09 | 19.07 | 18.61 | 1470 | 20.09 | 19.38 | 33.6768 | -118.0122 | 63.158 | Estimated WT 0.250
GWD 1480 | Girth Weld |  | 3490.82 | 20.09 | 0.25 | 35000 | ERW | 8.625 | 715 | [10 empty] | AGM 1 | 1739.05 | AGM 2 | 1457.47 | 18.61 | 20.09 | 19.07 | 18.61 | 20.09 | 1480 | 19.38 | 19.53 | 33.6768 | -118.0122 | 63.562
GWD 1490 | Girth Weld |  | 3510.91 | 19.38 | 0.28 | 35000 | ERW | 8.625 | 715 | [10 empty] | AGM 1 | 1759.14 | AGM 2 | 1437.38 | 20.09 | 19.38 | 18.61 | 20.09 | 19.38 | 1490 | 19.53 | 20.12 | 33.6768 | -118.0121 | 63.909
GWD 1500 | Girth Weld |  | 3530.29 | 19.53 | 0.28 | 35000 | ERW | 8.625 | 715 | [10 empty] | AGM 1 | 1778.53 | AGM 2 | 1418 | 19.38 | 19.53 | 20.09 | 19.38 | 19.53 | 1500 | 20.12 | 21.04 | 33.6769 | -118.0121 | 64.377
GWD 1510 | Girth Weld |  | 3549.82 | 2.03 | 0.28 | 35000 | SMLS | 8.625 | 715 | [10 empty] | AGM 1 | 1798.06 | AGM 2 | 1398.47 | 19.53 | 20.12 | 19.38 | 19.53 | 20.12 | 1510 | 21.04 | 19.67 | 33.6769 | -118.012 | 64.936
PMA 5 | Pipe Mill | Ext | 3551.86 | 0.23 | 0.28 | 35000 | SMLS | 8.625 | 715 | 13.6419 | 0.038 | 0.962 | 0.763 | 7:58 | [5 empty] | AGM 1 | 1800.09 | AGM 2 | 1396.43 | 2.03 | 18.09 | 19.38 | 19.53 | 20.12 | 1510 | 21.04 | 19.67 | 33.6769 | -118.012 | 64.976
PMA 6 | Pipe Mill | Ext | 3552.09 | 17.85 | 0.28 | 35000 | SMLS | 8.625 | 715 | 10.9297 | 0.031 | 0.673 | 0.788 | 7:11 | [5 empty] | AGM 1 | 1800.33 | AGM 2 | 1396.2 | 2.27 | 17.85 | 19.38 | 19.53 | 20.12 | 1510 | 21.04 | 19.67 | 33.6769 | -118.012 | 64.982
GWD 1520 | Girth Weld |  | 3569.94 | 6.68 | 0.28 | 35000 | SMLS | 8.625 | 715 | [10 empty] | AGM 1 | 1818.18 | AGM 2 | 1378.34 | 20.12 | 21.04 | 19.53 | 20.12 | 21.04 | 1520 | 19.67 | 21.14 | 33.6769 | -118.012 | 65.194
PMA 7 | Pipe Mill | Ext | 3576.62 | 5.81 | 0.28 | 35000 | SMLS | 8.625 | 715 | 12.1755 | 0.034 | 0.972 | 1.336 | 8:03 | [5 empty] | AGM 1 | 1824.86 | AGM 2 | 1371.67 | 6.68 | 14.36 | 19.53 | 20.12 | 21.04 | 1520 | 19.67 | 21.14 | 33.6769 | -118.0119 | 65.398
PMA 8 | Pipe Mill | Ext | 3582.43 | 8.55 | 0.28 | 35000 | SMLS | 8.625 | 715 | 15.8033 | 0.044 | 0.972 | 1.155 | 8:02 | [5 empty] | AGM 1 | 1830.66 | AGM 2 | 1365.86 | 12.49 | 8.55 | 19.53 | 20.12 | 21.04 | 1520 | 19.67 | 21.14 | 33.677 | -118.0119 | 65.659
GWD 1530 | Girth Weld |  | 3590.98 | 19.67 | 0.25 | 35000 | SMLS | 8.625 | 715 | [10 empty] | AGM 1 | 1839.21 | AGM 2 | 1357.31 | 21.04 | 19.67 | 20.12 | 21.04 | 19.67 | 1530 | 21.14 | 19.68 | 33.677 | -118.0119 | 65.918 | Estimated WT 0.250
GWD 1540 | Girth Weld |  | 3610.65 | 11.86 | 0.25 | 35000 | SMLS | 8.625 | 715 | [10 empty] | AGM 1 | 1858.88 | AGM 2 | 1337.64 | 19.67 | 21.14 | 21.04 | 19.67 | 21.14 | 1540 | 19.68 | 19.59 | 33.677 | -118.0118 | 66.292
DMA 63 | Metal Loss | Ext | 3622.5 | 0.94 | 0.25 | 35000 | SMLS | 8.625 | 715 | 11.4856 | 0.029 | 0.703 | 0.621 | 11:45 | 2591 | 0.38327 | 11 | 0.7 | 2587 | AGM 1 | 1870.74 | AGM 2 | 1325.78 | 11.86 | 9.28 | 21.04 | 19.67 | 21.14 | 1540 | 19.68 | 19.59 | 33.677 | -118.0118 | 66.648
DMA 64 | Metal Loss | Ext | 3623.44 | 4.33 | 0.25 | 35000 | SMLS | 8.625 | 715 | 14.0396 | 0.035 | 0.646 | 0.595 | 2:25 | 2589 | 0.38357 | 14 | 0.65 | 2585 | AGM 1 | 1871.68 | AGM 2 | 1324.84 | 12.8 | 8.35 | 21.04 | 19.67 | 21.14 | 1540 | 19.68 | 19.59 | 33.677 | -118.0118 | 66.671
CLS 11 | Cluster | Ext | 3627.77 | 0.63 | 0.25 | 35000 | SMLS | 8.625 | 715 | 11.8587 | 0.03 | 1.565 | 0.603 | 2:44 | 2542 | 0.39066 | 7 | 1.57 | 2561 | AGM 1 | 1876 | AGM 2 | 1320.52 | 17.12 | 4.02 | 21.04 | 19.67 | 21.14 | 1540 | 19.68 | 19.59 | 33.677 | -118.0118 | 66.769 | CLS C
DMA 67 | Metal Loss | Ext | 3628.4 | 0.29 | 0.25 | 35000 | SMLS | 8.625 | 715 | 10.147 | 0.025 | 0.695 | 0.657 | 2:39 | 2593 | 0.38298 | 10 | 0.69 | 2590 | AGM 1 | 1876.63 | AGM 2 | 1319.89 | 17.75 | 3.39 | 21.04 | 19.67 | 21.14 | 1540 | 19.68 | 19.59 | 33.677 | -118.0118 | 66.783
DMA 68 | Metal Loss | Ext | 3628.68 | 0.02 | 0.25 | 35000 | SMLS | 8.625 | 715 | 22.4195 | 0.056 | 1.088 | 0.516 | 12:16 | 2527 | 0.39298 | 22 | 1.09 | 2509 | AGM 1 | 1876.92 | AGM 2 | 1319.6 | 18.04 | 3.1 | 21.04 | 19.67 | 21.14 | 1540 | 19.68 | 19.59 | 33.677 | -118.0118 | 66.789
DNT 2 | Deformation |  | 3628.7 | 0.46 | 0.25 | 35000 | SMLS | 8.625 | 715 | 3.1303 | 0.27 | 2.593 | 2.601 | 6:58 | [5 empty] | AGM 1 | 1876.93 | AGM 2 | 1319.59 | 18.05 | 3.09 | 21.04 | 19.67 | 21.14 | 1540 | 19.68 | 19.59 | 33.677 | -118.0118 | 66.789
CLS 12 | Cluster | Ext | 3629.16 | 2.63 | 0.25 | 35000 | SMLS | 8.625 | 715 | 16.4937 | 0.041 | 6.972 | 1.171 | 12:08 | 2332 | 0.42584 | 10 | 5.43 | 2420 | AGM 1 | 1877.39 | AGM 2 | 1319.13 | 18.51 | 2.63 | 21.04 | 19.67 | 21.14 | 1540 | 19.68 | 19.59 | 33.677 | -118.0118 | 66.796 | CLS C
GWD 1550 | Girth Weld |  | 3631.79 | 19.68 | 0.25 | 35000 | SMLS | 8.625 | 715 | [10 empty] | AGM 1 | 1880.02 | AGM 2 | 1316.5 | 21.14 | 19.68 | 19.67 | 21.14 | 19.68 | 1550 | 19.59 | 18.68 | 33.677 | -118.0118 | 66.832
GWD 1560 | Girth Weld |  | 3651.47 | 19.58 | 0.25 | 35000 | SMLS | 8.625 | 715 | [10 empty] | AGM 1 | 1899.71 | AGM 2 | 1296.82 | 19.68 | 19.59 | 21.14 | 19.68 | 19.59 | 1560 | 18.68 | 0.52 | 33.6771 | -118.0117 | 66.717
GWD 1570 | Girth Weld |  | 3671.06 | 18.68 | 0.28 | 35000 | ERW | 8.625 | 715 | [10 empty] | AGM 1 | 1919.29 | AGM 2 | 1277.23 | 19.59 | 18.68 | 19.68 | 19.59 | 18.68 | 1570 | 0.52 | 19.3 | 33.6771 | -118.0117 | 66.378
GWD 1580 | Girth Weld |  | 3689.74 | 0.52 | 0.28 | 35000 | ERW | 8.625 | 715 | [10 empty] | AGM 1 | 1937.97 | AGM 2 | 1258.55 | 18.68 | 0.52 | 19.59 | 18.68 | 0.52 | 1580 | 19.3 | 19.88 | 33.6771 | -118.0116 | 66.057
GWD 1590 | Girth Weld |  | 3690.26 | 15.51 | 0.28 | 35000 | ERW | 8.625 | 715 | [10 empty] | AGM 1 | 1938.49 | AGM 2 | 1258.03 | 0.52 | 19.3 | 18.68 | 0.52 | 19.3 | 1590 | 19.88 | 18.72 | 33.6771 | -118.0116 | 66.053
DMA 74 | Metal Loss | Ext | 3705.77 | 3.79 | 0.28 | 35000 | ERW | 8.625 | 715 | 15.452 | 0.043 | 0.756 | 0.656 | 10:18 | 2893 | 0.34326 | 15 | 0.76 | 2886 | AGM 1 | 1954 | AGM 2 | 1242.52 | 15.51 | 3.79 | 18.68 | 0.52 | 19.3 | 1590 | 19.88 | 18.72 | 33.6771 | -118.0116 | 65.956
GWD 1600 | Girth Weld |  | 3709.56 | 19.88 | 0.28 | 35000 | ERW | 8.625 | 715 | [10 empty] | AGM 1 | 1957.79 | AGM 2 | 1238.73 | 19.3 | 19.88 | 0.52 | 19.3 | 19.88 | 1600 | 18.72 | 19.84 | 33.6771 | -118.0116 | 65.926
GWD 1610 | Girth Weld |  | 3729.44 | 1.31 | 0.28 | 35000 | ERW | 8.625 | 715 | [10 empty] | AGM 1 | 1977.67 | AGM 2 | 1218.85 | 19.88 | 18.72 | 19.3 | 19.88 | 18.72 | 1610 | 19.84 | 19.07 | 33.6772 | -118.0115 | 65.713
DMA 75 | Metal Loss | Ext | 3730.74 | 17.41 | 0.28 | 35000 | ERW | 8.625 | 715 | 18.2683 | 0.051 | 0.905 | 0.806 | 9:46 | 2873 | 0.34565 | 18 | 0.91 | 2863 | AGM 1 | 1978.98 | AGM 2 | 1217.55 | 1.3 | 17.41 | 19.3 | 19.88 | 18.72 | 1610 | 19.84 | 19.07 | 33.6772 | -118.0115 | 65.69
GWD 1620 | Girth Weld |  | 3748.16 | 19.84 | 0.28 | 35000 | ERW | 8.625 | 715 | [10 empty] | AGM 1 | 1996.39 | AGM 2 | 1200.13 | 18.72 | 19.84 | 19.88 | 18.72 | 19.84 | 1620 | 19.07 | 20.52 | 33.6772 | -118.0115 | 64.981
GWD 1630 | Girth Weld |  | 3768 | 19.07 | 0.28 | 35000 | ERW | 8.625 | 715 | [10 empty] | AGM 1 | 2016.23 | AGM 2 | 1180.29 | 19.84 | 19.07 | 18.72 | 19.84 | 19.07 | 1630 | 20.52 | 7.77 | 33.6772 | -118.0114 | 64.4
GWD 1640 | Girth Weld |  | 3787.06 | 20.52 | 0.375 | 35000 | ERW | 8.625 | 715 | [10 empty] | AGM 1 | 2035.3 | AGM 2 | 1161.22 | 19.07 | 20.52 | 19.84 | 19.07 | 20.52 | 1640 | 7.77 | 17.38 | 33.6773 | -118.0114 | 64.079 | Estimated WT 0.375
GWD 1650 | Girth Weld |  | 3807.58 | 7.77 | 0.375 | 35000 | ERW | 8.625 | 715 | [10 empty] | AGM 1 | 2055.82 | AGM 2 | 1140.71 | 20.52 | 7.77 | 19.07 | 20.52 | 7.77 | 1650 | 17.38 | 20.04 | 33.6773 | -118.0113 | 63.933
GWD 1660 | Girth Weld |  | 3815.35 | 17.38 | 0.375 | 35000 | ERW | 8.625 | 715 | [10 empty] | AGM 1 | 2063.59 | AGM 2 | 1132.94 | 7.77 | 17.38 | 20.52 | 7.77 | 17.38 | 1660 | 20.04 | 20.42 | 33.6773 | -118.0113 | 63.897
GWD 1670 | Girth Weld |  | 3832.73 | 20.04 | 0.28 | 35000 | SMLS | 8.625 | 715 | [10 empty] | AGM 1 | 2080.97 | AGM 2 | 1115.56 | 17.38 | 20.04 | 7.77 | 17.38 | 20.04 | 1670 | 20.42 | 20.22 | 33.6773 | -118.0112 | 63.876
GWD 1680 | Girth Weld |  | 3852.78 | 13.94 | 0.28 | 35000 | SMLS | 8.625 | 715 | [10 empty] | AGM 1 | 2101.01 | AGM 2 | 1095.51 | 20.04 | 20.42 | 17.38 | 20.04 | 20.42 | 1680 | 20.22 | 19.43 | 33.6774 | -118.0112 | 64.106
DMA 76 | Metal Loss | Ext | 3866.72 | 0.72 | 0.28 | 35000 | SMLS | 8.625 | 715 | 13.717 | 0.038 | 0.496 | 0.602 | 12:47 | 2910 | 0.34126 | 14 | 0.5 | 2908 | AGM 1 | 2114.95 | AGM 2 | 1081.57 | 13.94 | 6.48 | 17.38 | 20.04 | 20.42 | 1680 | 20.22 | 19.43 | 33.6774 | -118.0112 | 64.305
DMA 77 | Metal Loss | Ext | 3867.43 | 0.34 | 0.28 | 35000 | SMLS | 8.625 | 715 | 22.6858 | 0.064 | 0.731 | 0.55 | 3:33 | 2879 | 0.34493 | 23 | 0.73 | 2869 | AGM 1 | 2115.67 | AGM 2 | 1080.85 | 14.66 | 5.77 | 17.38 | 20.04 | 20.42 | 1680 | 20.22 | 19.43 | 33.6774 | -118.0112 | 64.313
DMA 78 | Metal Loss | Ext | 3867.77 | 0.35 | 0.28 | 35000 | SMLS | 8.625 | 715 | 13.2539 | 0.037 | 0.697 | 0.53 | 12:35 | 2900 | 0.34243 | 13 | 0.7 | 2896 | AGM 1 | 2116 | AGM 2 | 1080.52 | 14.99 | 5.43 | 17.38 | 20.04 | 20.42 | 1680 | 20.22 | 19.43 | 33.6774 | -118.0112 | 64.318
DMA 79 | Metal Loss | Ext | 3868.12 | 0.03 | 0.28 | 35000 | SMLS | 8.625 | 715 | 14.5977 | 0.041 | 0.89 | 0.649 | 3:37 | 2885 | 0.34421 | 15 | 0.89 | 2878 | AGM 1 | 2116.35 | AGM 2 | 1080.17 | 15.34 | 5.08 | 17.38 | 20.04 | 20.42 | 1680 | 20.22 | 19.43 | 33.6774 | -118.0112 | 64.322
DMA 80 | Metal Loss | Ext | 3868.15 | 0.6 | 0.28 | 35000 | SMLS | 8.625 | 715 | 10.5963 | 0.03 | 0.969 | 0.781 | 12:39 | 2892 | 0.34338 | 11 | 0.97 | 2886 | AGM 1 | 2116.39 | AGM 2 | 1080.14 | 15.38 | 5.05 | 17.38 | 20.04 | 20.42 | 1680 | 20.22 | 19.43 | 33.6774 | -118.0112 | 64.322
DMA 81 | Metal Loss | Ext | 3868.75 | 0.06 | 0.28 | 35000 | SMLS | 8.625 | 715 | 17.8246 | 0.05 | 1 | 0.743 | 3:34 | 2866 | 0.3465 | 18 | 1 | 2854 | AGM 1 | 2116.99 | AGM 2 | 1079.53 | 15.98 | 4.45 | 17.38 | 20.04 | 20.42 | 1680 | 20.22 | 19.43 | 33.6774 | -118.0111 | 64.329
DMA 82 | Metal Loss | Ext | 3868.82 | 0.23 | 0.28 | 35000 | SMLS | 8.625 | 715 | 10.9426 | 0.031 | 0.765 | 0.786 | 12:47 | 2901 | 0.34231 | 11 | 0.76 | 2897 | AGM 1 | 2117.05 | AGM 2 | 1079.47 | 16.04 | 4.38 | 17.38 | 20.04 | 20.42 | 1680 | 20.22 | 19.43 | 33.6774 | -118.0111 | 64.331
CLS 13 | Cluster | Ext | 3869.05 | 0.13 | 0.28 | 35000 | SMLS | 8.625 | 715 | 24.243 | 0.068 | 2.503 | 0.923 | 3:26 | 2659 | 0.37347 | 12 | 2.5 | 2776 | AGM 1 | 2117.28 | AGM 2 | 1079.24 | 16.27 | 4.15 | 17.38 | 20.04 | 20.42 | 1680 | 20.22 | 19.43 | 33.6774 | -118.0111 | 64.331 | CLS C
CLS 14 | Cluster | Ext | 3869.18 | 0.33 | 0.28 | 35000 | SMLS | 8.625 | 715 | 17.8439 | 0.05 | 2.464 | 2.385 | 12:09 | 2738 | 0.36269 | 15 | 2.46 | 2738 | AGM 1 | 2117.42 | AGM 2 | 1079.1 | 16.41 | 4.02 | 17.38 | 20.04 | 20.42 | 1680 | 20.22 | 19.43 | 33.6774 | -118.0111 | 64.333 | CLS C
DMA 88 | Metal Loss | Ext | 3869.52 | 0.1 | 0.28 | 35000 | SMLS | 8.625 | 715 | 10.2859 | 0.029 | 0.723 | 0.687 | 12:37 | 2905 | 0.34184 | 10 | 0.72 | 2901 | AGM 1 | 2117.75 | AGM 2 | 1078.77 | 16.74 | 3.68 | 17.38 | 20.04 | 20.42 | 1680 | 20.22 | 19.43 | 33.6774 | -118.0111 | 64.335
DMA 89 | Metal Loss | Ext | 3869.61 | 0.14 | 0.28 | 35000 | SMLS | 8.625 | 715 | 17.5982 | 0.049 | 0.579 | 0.594 | 3:29 | 2901 | 0.34231 | 18 | 0.58 | 2896 | AGM 1 | 2117.85 | AGM 2 | 1078.67 | 16.84 | 3.59 | 17.38 | 20.04 | 20.42 | 1680 | 20.22 | 19.43 | 33.6774 | -118.0111 | 64.336
DMA 90 | Metal Loss | Ext | 3869.76 | 0.07 | 0.28 | 35000 | SMLS | 8.625 | 715 | 10.0401 | 0.028 | 1.33 | 0.688 | 11:39 | 2876 | 0.34529 | 10 | 1.33 | 2867 | AGM 1 | 2117.99 | AGM 2 | 1078.53 | 16.98 | 3.44 | 17.38 | 20.04 | 20.42 | 1680 | 20.22 | 19.43 | 33.6774 | -118.0111 | 64.338
DMA 91 | Metal Loss | Ext | 3869.82 | 0.42 | 0.28 | 35000 | SMLS | 8.625 | 715 | 13.1014 | 0.037 | 1.246 | 0.691 | 3:29 | 2866 | 0.3465 | 13 | 1.25 | 2855 | AGM 1 | 2118.06 | AGM 2 | 1078.46 | 17.05 | 3.38 | 17.38 | 20.04 | 20.42 | 1680 | 20.22 | 19.43 | 33.6774 | -118.0111 | 64.338
DMA 92 | Metal Loss | Ext | 3870.24 | 0.29 | 0.28 | 35000 | SMLS | 8.625 | 715 | 11.0305 | 0.031 | 0.852 | 0.698 | 11:37 | 2897 | 0.34279 | 11 | 0.85 | 2892 | AGM 1 | 2118.48 | AGM 2 | 1078.05 | 17.47 | 2.96 | 17.38 | 20.04 | 20.42 | 1680 | 20.22 | 19.43 | 33.6774 | -118.0111 | 64.342
DMA 93 | Metal Loss | Ext | 3870.53 | 1.96 | 0.28 | 35000 | SMLS | 8.625 | 715 | 15.8534 | 0.044 | 0.737 | 0.565 | 3:33 | 2893 | 0.34326 | 16 | 0.74 | 2887 | AGM 1 | 2118.76 | AGM 2 | 1077.76 | 17.75 | 2.67 | 17.38 | 20.04 | 20.42 | 1680 | 20.22 | 19.43 | 33.6774 | -118.0111 | 64.345
DMA 95 | Metal Loss | Ext | 3872.49 | 0.05 | 0.28 | 35000 | SMLS | 8.625 | 715 | 15.4388 | 0.043 | 0.664 | 0.637 | 12:53 | 2899 | 0.34255 | 15 | 0.66 | 2894 | AGM 1 | 2120.72 | AGM 2 | 1075.8 | 19.71 | 0.71 | 17.38 | 20.04 | 20.42 | 1680 | 20.22 | 19.43 | 33.6774 | -118.0111 | 64.364
CLS 15 | Cluster | Ext | 3872.54 | 0.66 | 0.28 | 35000 | SMLS | 8.625 | 715 | 17.6275 | 0.049 | 3.414 | 1.141 | 3:28 | 2687 | 0.36958 | 9 | 3.41 | 2777 | AGM 1 | 2120.77 | AGM 2 | 1075.75 | 19.76 | 0.66 | 17.38 | 20.04 | 20.42 | 1680 | 20.22 | 19.43 | 33.6774 | -118.0111 | 64.366 | CLS C
GWD 1690 | Girth Weld |  | 3873.2 | 20.22 | 0.25 | 35000 | ERW | 8.625 | 715 | [10 empty] | AGM 1 | 2121.44 | AGM 2 | 1075.09 | 20.42 | 20.22 | 20.04 | 20.42 | 20.22 | 1690 | 19.43 | 16.53 | 33.6774 | -118.0111 | 64.368 | Estimated WT 0.250
GWD 1700 | Girth Weld |  | 3893.42 | 19.43 | 0.25 | 35000 | ERW | 8.625 | 715 | [10 empty] | AGM 1 | 2141.66 | AGM 2 | 1054.87 | 20.22 | 19.43 | 20.42 | 20.22 | 19.43 | 1700 | 16.53 | 19.92 | 33.6774 | -118.0111 | 64.138
GWD 1710 | Girth Weld |  | 3912.85 | 16.53 | 0.25 | 35000 | ERW | 8.625 | 715 | [10 empty] | AGM 1 | 2161.09 | AGM 2 | 1035.44 | 19.43 | 16.53 | 20.22 | 19.43 | 16.53 | 1710 | 19.92 | 19.52 | 33.6775 | -118.011 | 64.065
GWD 1720 | Girth Weld |  | 3929.38 | 12.43 | 0.25 | 35000 | ERW | 8.625 | 715 | [10 empty] | AGM 1 | 2177.62 | AGM 2 | 1018.91 | 16.53 | 19.92 | 19.43 | 16.53 | 19.92 | 1720 | 19.52 | 19.16 | 33.6775 | -118.011 | 63.996
DMA 99 | Metal Loss | Ext | 3941.81 | 6.28 | 0.25 | 35000 | ERW | 8.625 | 715 | 16.4759 | 0.041 | 0.696 | 0.637 | 12:43 | 2582 | 0.38461 | 16 | 0.7 | 2576 | AGM 1 | 2190.05 | AGM 2 | 1006.47 | 12.43 | 7.48 | 19.43 | 16.53 | 19.92 | 1720 | 19.52 | 19.16 | 33.6775 | -118.011 | 63.99
DMA 100 | Metal Loss | Ext | 3948.1 | 1.2 | 0.25 | 35000 | ERW | 8.625 | 715 | 29.1314 | 0.073 | 1.8 | 0.697 | 11:54 | 2388 | 0.41585 | 29 | 1.8 | 2339 | AGM 1 | 2196.33 | AGM 2 | 1000.19 | 18.72 | 1.2 | 19.43 | 16.53 | 19.92 | 1720 | 19.52 | 19.16 | 33.6775 | -118.0109 | 63.993
GWD 1730 | Girth Weld |  | 3949.3 | 2.29 | 0.25 | 35000 | ERW | 8.625 | 715 | [10 empty] | AGM 1 | 2197.53 | AGM 2 | 998.99 | 19.92 | 19.52 | 16.53 | 19.92 | 19.52 | 1730 | 19.16 | 20.79 | 33.6775 | -118.0109 | 63.994
PMA 9 | Pipe Mill | Ext | 3951.59 | 17.23 | 0.25 | 35000 | ERW | 8.625 | 715 | 11.8816 | 0.03 | 0.978 | 1 | 10:45 | [5 empty] | AGM 1 | 2199.82 | AGM 2 | 996.7 | 2.29 | 17.23 | 16.53 | 19.92 | 19.52 | 1730 | 19.16 | 20.79 | 33.6775 | -118.0109 | 63.991
GWD 1740 | Girth Weld |  | 3968.82 | 4.6 | 0.25 | 35000 | ERW | 8.625 | 715 | [10 empty] | AGM 1 | 2217.06 | AGM 2 | 979.47 | 19.52 | 19.16 | 19.92 | 19.52 | 19.16 | 1740 | 20.79 | 20.19 | 33.6775 | -118.0109 | 63.94
DMA 101 | Metal Loss | Ext | 3973.43 | 0.27 | 0.25 | 35000 | ERW | 8.625 | 715 | 12.0597 | 0.03 | 1.057 | 0.656 | 3:02 | 2570 | 0.3864 | 12 | 1.06 | 2563 | AGM 1 | 2221.66 | AGM 2 | 974.86 | 4.61 | 14.56 | 19.92 | 19.52 | 19.16 | 1740 | 20.79 | 20.19 | 33.6776 | -118.0109 | 63.951
DMA 102 | Metal Loss | Ext | 3973.7 | 14.28 | 0.25 | 35000 | ERW | 8.625 | 715 | 14.1469 | 0.035 | 1.864 | 0.965 | 3:50 | 2508 | 0.39596 | 14 | 1.86 | 2488 | AGM 1 | 2221.93 | AGM 2 | 974.59 | 4.88 | 14.28 | 19.92 | 19.52 | 19.16 | 1740 | 20.79 | 20.19 | 33.6776 | -118.0109 | 63.951
GWD 1750 | Girth Weld |  | 3987.98 | 20.79 | 0.25 | 35000 | ERW | 8.625 | 715 | [10 empty] | AGM 1 | 2236.22 | AGM 2 | 960.3 | 19.16 | 20.79 | 19.52 | 19.16 | 20.79 | 1750 | 20.19 | 9.99 | 33.6776 | -118.0108 | 64.128
GWD 1760 | Girth Weld |  | 4008.77 | 20.19 | 0.25 | 35000 | ERW | 8.625 | 715 | [10 empty] | AGM 1 | 2257.01 | AGM 2 | 939.52 | 20.79 | 20.19 | 19.16 | 20.79 | 20.19 | 1760 | 9.99 | 27.32 | 33.6776 | -118.0108 | 64.122
GWD 1770 | Girth Weld |  | 4028.96 | 9.99 | 0.28 | 35000 | SMLS | 8.625 | 715 | [10 empty] | AGM 1 | 2277.2 | AGM 2 | 919.32 | 20.19 | 9.99 | 20.79 | 20.19 | 9.99 | 1770 | 27.32 | 18.62 | 33.6776 | -118.0107 | 64.23
GWD 1780 | Girth Weld |  | 4038.96 | 27.32 | 0.28 | 35000 | SMLS | 8.625 | 715 | [10 empty] | AGM 1 | 2287.19 | AGM 2 | 909.33 | 9.99 | 27.32 | 20.19 | 9.99 | 27.32 | 1780 | 18.62 | 18.59 | 33.6777 | -118.0107 | 64.3
GWD 1790 | Girth Weld |  | 4066.28 | 18.62 | 0.28 | 35000 | ERW | 8.625 | 715 | [10 empty] | AGM 1 | 2314.51 | AGM 2 | 882.01 | 27.32 | 18.62 | 9.99 | 27.32 | 18.62 | 1790 | 18.59 | 14.54 | 33.6777 | -118.0106 | 64.294
GWD 1800 | Girth Weld |  | 4084.9 | 18.59 | 0.28 | 35000 | ERW | 8.625 | 715 | [10 empty] | AGM 1 | 2333.14 | AGM 2 | 863.38 | 18.62 | 18.59 | 27.32 | 18.62 | 18.59 | 1800 | 14.54 | 20.96 | 33.6777 | -118.0106 | 64.401
GWD 1810 | Girth Weld |  | 4103.49 | 3.15 | 0.28 | 35000 | ERW | 8.625 | 715 | [10 empty] | AGM 1 | 2351.73 | AGM 2 | 844.79 | 18.59 | 14.54 | 18.62 | 18.59 | 14.54 | 1810 | 20.96 | 12.37 | 33.6778 | -118.0105 | 64.473
DMA 103 | Metal Loss | Ext | 4106.64 | 7.79 | 0.28 | 35000 | ERW | 8.625 | 715 | 14.0724 | 0.039 | 2.158 | 3.158 | 11:09 | 2798 | 0.35492 | 14 | 2.16 | 2774 | AGM 1 | 2354.88 | AGM 2 | 841.64 | 3.15 | 11.39 | 18.62 | 18.59 | 14.54 | 1810 | 20.96 | 12.37 | 33.6778 | -118.0105 | 64.476
CLS 16 | Cluster | Ext | 4114.44 | 3.6 | 0.28 | 35000 | ERW | 8.625 | 715 | 16.4112 | 0.046 | 2.879 | 6.741 | 9:14 | 2730 | 0.36376 | 12 | 2.88 | 2760 | AGM 1 | 2362.67 | AGM 2 | 833.85 | 10.94 | 3.6 | 18.62 | 18.59 | 14.54 | 1810 | 20.96 | 12.37 | 33.6778 | -118.0105 | 64.43 | CLS C
GWD 1820 | Girth Weld |  | 4118.03 | 17.39 | 0.28 | 35000 | ERW | 8.625 | 715 | [10 empty] | AGM 1 | 2366.27 | AGM 2 | 830.25 | 14.54 | 20.96 | 18.59 | 14.54 | 20.96 | 1820 | 12.37 | 24.37 | 33.6778 | -118.0105 | 64.417
DNT 3 | Deformation |  | 4135.42 | 3.57 | 0.28 | 35000 | ERW | 8.625 | 715 | 2.4864 | 0.214 | 2.963 | 2.62 | 5:01 | [5 empty] | AGM 1 | 2383.66 | AGM 2 | 812.87 | 17.39 | 3.57 | 18.59 | 14.54 | 20.96 | 1820 | 12.37 | 24.37 | 33.6778 | -118.0104 | 64.257
GWD 1830 | Girth Weld |  | 4139 | 12.37 | 0.25 | 35000 | ERW | 8.625 | 715 | [10 empty] | AGM 1 | 2387.23 | AGM 2 | 809.29 | 20.96 | 12.37 | 14.54 | 20.96 | 12.37 | 1830 | 24.37 | 22.14 | 33.6778 | -118.0104 | 64.208 | Estimated WT 0.250
GWD 1840 | Girth Weld |  | 4151.37 | 24.37 | 0.25 | 35000 | ERW | 8.625 | 715 | [10 empty] | AGM 1 | 2399.6 | AGM 2 | 796.92 | 12.37 | 24.37 | 20.96 | 12.37 | 24.37 | 1840 | 22.14 | 16.21 | 33.6778 | -118.0104 | 64.071
GWD 1850 | Girth Weld |  | 4175.73 | 6.94 | 0.25 | 35000 | ERW | 8.625 | 715 | [10 empty] | AGM 1 | 2423.97 | AGM 2 | 772.55 | 24.37 | 22.14 | 12.37 | 24.37 | 22.14 | 1850 | 16.21 | 11.82 | 33.6779 | -118.0103 | 63.74
DMA 108 | Metal Loss | Ext | 4182.67 | 0.27 | 0.25 | 35000 | ERW | 8.625 | 715 | 12.4044 | 0.031 | 0.615 | 0.755 | 9:08 | 2593 | 0.38298 | 12 | 0.61 | 2590 | AGM 1 | 2430.91 | AGM 2 | 765.62 | 6.94 | 15.2 | 12.37 | 24.37 | 22.14 | 1850 | 16.21 | 11.82 | 33.6779 | -118.0103 | 63.576
DMA 109 | Metal Loss | Ext | 4182.94 | 0.27 | 0.25 | 35000 | ERW | 8.625 | 715 | 15.6049 | 0.039 | 1.067 | 1.169 | 9:15 | 2557 | 0.38837 | 16 | 1.07 | 2546 | AGM 1 | 2431.17 | AGM 2 | 765.35 | 7.21 | 14.93 | 12.37 | 24.37 | 22.14 | 1850 | 16.21 | 11.82 | 33.6779 | -118.0103 | 63.569
DMA 110 | Metal Loss | Ext | 4183.21 | 14.66 | 0.25 | 35000 | ERW | 8.625 | 715 | 13.8137 | 0.035 | 0.945 | 0.64 | 7:17 | 2571 | 0.38625 | 14 | 0.94 | 2564 | AGM 1 | 2431.44 | AGM 2 | 765.08 | 7.48 | 14.66 | 12.37 | 24.37 | 22.14 | 1850 | 16.21 | 11.82 | 33.6779 | -118.0103 | 63.563
GWD 1860 | Girth Weld |  | 4197.87 | 16.2 | 0.28 | 35000 | ERW | 8.625 | 715 | [10 empty] | AGM 1 | 2446.1 | AGM 2 | 750.42 | 22.14 | 16.21 | 24.37 | 22.14 | 16.21 | 1860 | 11.82 | 7.33 | 33.6779 | -118.0103 | 63.371
GWD 1870 | Girth Weld |  | 4214.08 | 5.51 | 0.25 | 35000 | SMLS | 8.625 | 715 | [10 empty] | AGM 1 | 2462.31 | AGM 2 | 734.21 | 16.21 | 11.82 | 22.14 | 16.21 | 11.82 | 1870 | 7.33 | 21.45 | 33.6779 | -118.0102 | 63.597 | Estimated WT 0.250
DMA 111 | Metal Loss | Ext | 4219.59 | 0.86 | 0.25 | 35000 | SMLS | 8.625 | 715 | 21.7656 | 0.054 | 0.886 | 1.314 | 10:05 | 2552 | 0.38913 | 22 | 0.89 | 2540 | AGM 1 | 2467.82 | AGM 2 | 728.7 | 5.51 | 6.31 | 22.14 | 16.21 | 11.82 | 1870 | 7.33 | 21.45 | 33.6779 | -118.0102 | 63.67
DMA 112 | Metal Loss | Ext | 4220.45 | 2.07 | 0.25 | 35000 | SMLS | 8.625 | 715 | 17.9048 | 0.045 | 1.331 | 1.716 | 11:13 | 2524 | 0.39345 | 18 | 1.33 | 2506 | AGM 1 | 2468.69 | AGM 2 | 727.84 | 6.37 | 5.44 | 22.14 | 16.21 | 11.82 | 1870 | 7.33 | 21.45 | 33.6779 | -118.0102 | 63.685
PAH 1 | Patch |  | 4222.52 | 0.5 | 0.25 | 35000 | SMLS | 8.625 | 715 |  |  |  |  | 10:16 | [5 empty] | AGM 1 | 2470.76 | AGM 2 | 725.77 | 8.44 | 3.37 | 22.14 | 16.21 | 11.82 | 1870 | 7.33 | 21.45 | 33.6779 | -118.0102 | 63.726
DMA 113 | Metal Loss | Ext | 4223.02 | 2.87 | 0.25 | 35000 | SMLS | 8.625 | 715 | 54.0682 | 0.135 | 3.547 | 3.397 | 11:43 | 1797 | 0.55262 | 54 | 3.55 | 1605 | AGM 1 | 2471.26 | AGM 2 | 725.27 | 8.94 | 2.87 | 22.14 | 16.21 | 11.82 | 1870 | 7.33 | 21.45 | 33.6779 | -118.0102 | 63.737
GWD 1880 | Girth Weld |  | 4225.89 | 7.33 | 0.25 | 35000 | SMLS | 8.625 | 715 | [10 empty] | AGM 1 | 2474.13 | AGM 2 | 722.4 | 11.82 | 7.33 | 16.21 | 11.82 | 7.33 | 1880 | 21.45 | 18.29 | 33.6779 | -118.0102 | 63.819
GWD 1890 | Girth Weld |  | 4233.22 | 21.45 | 0.25 | 35000 | SMLS | 8.625 | 715 | [10 empty] | AGM 1 | 2481.46 | AGM 2 | 715.06 | 7.33 | 21.45 | 11.82 | 7.33 | 21.45 | 1890 | 18.29 | 20.41 | 33.6779 | -118.0102 | 64.038
GWD 1900 | Girth Weld |  | 4254.67 | 18.29 | 0.28 | 35000 | ERW | 8.625 | 715 | [10 empty] | AGM 1 | 2502.91 | AGM 2 | 693.61 | 21.45 | 18.29 | 7.33 | 21.45 | 18.29 | 1900 | 20.41 | 17.53 | 33.678 | -118.0101 | 64.771
GWD 1910 | Girth Weld |  | 4272.96 | 20.41 | 0.28 | 35000 | ERW | 8.625 | 715 | [10 empty] | AGM 1 | 2521.19 | AGM 2 | 675.33 | 18.29 | 20.41 | 21.45 | 18.29 | 20.41 | 1910 | 17.53 | 22.17 | 33.678 | -118.0101 | 65.18
GWD 1920 | Girth Weld |  | 4293.37 | 17.53 | 0.25 | 35000 | SMLS | 8.625 | 715 | [10 empty] | AGM 1 | 2541.6 | AGM 2 | 654.92 | 20.41 | 17.53 | 18.29 | 20.41 | 17.53 | 1920 | 22.17 | 42.24 | 33.678 | -118.01 | 65.494 | Estimated WT 0.250
GWD 1930 | Girth Weld |  | 4310.9 | 22.17 | 0.25 | 35000 | SMLS | 8.625 | 715 | [10 empty] | AGM 1 | 2559.14 | AGM 2 | 637.39 | 17.53 | 22.17 | 20.41 | 17.53 | 22.17 | 1930 | 42.24 | 19.92 | 33.6781 | -118.0099 | 65.749
GWD 1940 | Girth Weld |  | 4333.07 | 42.24 | 0.25 | 35000 | SMLS | 8.625 | 715 | [10 empty] | AGM 1 | 2581.3 | AGM 2 | 615.22 | 22.17 | 42.24 | 17.53 | 22.17 | 42.24 | 1940 | 19.92 | 21.54 | 33.6781 | -118.0099 | 66.223
GWD 1950 | Girth Weld |  | 4375.3 | 8.86 | 0.28 | 35000 | ERW | 8.625 | 715 | [10 empty] | AGM 1 | 2623.54 | AGM 2 | 572.98 | 42.24 | 19.92 | 22.17 | 42.24 | 19.92 | 1950 | 21.54 | 20.79 | 33.6782 | -118.0098 | 67.095
SLV 7 | Sleeve Start |  | 4384.17 | 1.1 | 0.28 | 35000 | ERW | 8.625 | 715 |  |  | 13.249 | [7 empty] | AGM 1 | 2632.4 | AGM 2 | 564.12 | 8.86 | 11.05 | 22.17 | 42.24 | 19.92 | 1950 | 21.54 | 20.79 | 33.6782 | -118.0097 | 67.303 | Repair Sleeve - Start
SLV 8 | Sleeve End |  | 4385.27 | 9.95 | 0.28 | 35000 | ERW | 8.625 | 715 | [10 empty] | AGM 1 | 2633.51 | AGM 2 | 563.02 | 9.97 | 9.95 | 22.17 | 42.24 | 19.92 | 1950 | 21.54 | 20.79 | 33.6782 | -118.0097 | 67.34 | Repair Sleeve - End
GWD 1960 | Girth Weld |  | 4395.22 | 7.43 | 0.28 | 35000 | ERW | 8.625 | 715 | [10 empty] | AGM 1 | 2643.45 | AGM 2 | 553.07 | 19.92 | 21.54 | 42.24 | 19.92 | 21.54 | 1960 | 20.79 | 20.62 | 33.6782 | -118.0097 | 67.692
PMA 10 | Pipe Mill | Ext | 4402.65 | 10.79 | 0.28 | 35000 | ERW | 8.625 | 715 | 12.6801 | 0.036 | 1.008 | 0.897 | 12:28 | [5 empty] | AGM 1 | 2650.88 | AGM 2 | 545.64 | 7.43 | 14.11 | 42.24 | 19.92 | 21.54 | 1960 | 20.79 | 20.62 | 33.6782 | -118.0097 | 67.982
DMA 114 | Metal Loss | Ext | 4413.44 | 3.32 | 0.28 | 35000 | ERW | 8.625 | 715 | 17.6108 | 0.049 | 0.527 | 0.641 | 5:40 | 2904 | 0.34196 | 18 | 0.53 | 2901 | AGM 1 | 2661.67 | AGM 2 | 534.85 | 18.22 | 3.32 | 42.24 | 19.92 | 21.54 | 1960 | 20.79 | 20.62 | 33.6782 | -118.0097 | 68.279
GWD 1970 | Girth Weld |  | 4416.76 | 20.79 | 0.28 | 35000 | ERW | 8.625 | 715 | [10 empty] | AGM 1 | 2664.99 | AGM 2 | 531.53 | 21.54 | 20.79 | 19.92 | 21.54 | 20.79 | 1970 | 20.62 | 20.37 | 33.6782 | -118.0097 | 68.282
GWD 1980 | Girth Weld |  | 4437.54 | 3.05 | 0.28 | 35000 | ERW | 8.625 | 715 | [10 empty] | AGM 1 | 2685.78 | AGM 2 | 510.74 | 20.79 | 20.62 | 21.54 | 20.79 | 20.62 | 1980 | 20.37 | 19.92 | 33.6783 | -118.0096 | 68.794
DMA 115 | Metal Loss | Ext | 4440.6 | 0.23 | 0.28 | 35000 | ERW | 8.625 | 715 | 11.4996 | 0.032 | 1.073 | 0.846 | 7:52 | 2883 | 0.34445 | 11 | 1.07 | 2876 | AGM 1 | 2688.83 | AGM 2 | 507.69 | 3.05 | 17.56 | 21.54 | 20.79 | 20.62 | 1980 | 20.37 | 19.92 | 33.6783 | -118.0096 | 68.919
DMA 116 | Metal Loss | Ext | 4440.83 | 0.19 | 0.28 | 35000 | ERW | 8.625 | 715 | 12.689 | 0.036 | 1.05 | 0.777 | 7:49 | 2881 | 0.34469 | 13 | 1.05 | 2872 | AGM 1 | 2689.06 | AGM 2 | 507.46 | 3.28 | 17.33 | 21.54 | 20.79 | 20.62 | 1980 | 20.37 | 19.92 | 33.6783 | -118.0096 | 68.928
DMA 117 | Metal Loss | Ext | 4441.02 | 0.26 | 0.28 | 35000 | ERW | 8.625 | 715 | 13.1411 | 0.037 | 0.789 | 1.11 | 7:16 | 2895 | 0.34302 | 13 | 0.79 | 2890 | AGM 1 | 2689.25 | AGM 2 | 507.27 | 3.47 | 17.15 | 21.54 | 20.79 | 20.62 | 1980 | 20.37 | 19.92 | 33.6783 | -118.0096 | 68.935
DMA 118 | Metal Loss | Ext | 4441.28 | 0.63 | 0.28 | 35000 | ERW | 8.625 | 715 | 18.6967 | 0.052 | 1.814 | 1.035 | 5:40 | 2783 | 0.35683 | 19 | 1.81 | 2754 | AGM 1 | 2689.51 | AGM 2 | 507.01 | 3.74 | 16.88 | 21.54 | 20.79 | 20.62 | 1980 | 20.37 | 19.92 | 33.6783 | -118.0096 | 68.944
DMA 119 | Metal Loss | Ext | 4441.91 | 16.26 | 0.28 | 35000 | ERW | 8.625 | 715 | 11.5242 | 0.032 | 0.962 | 1.025 | 7:18 | 2890 | 0.34362 | 12 | 0.96 | 2883 | AGM 1 | 2690.14 | AGM 2 | 506.38 | 4.36 | 16.26 | 21.54 | 20.79 | 20.62 | 1980 | 20.37 | 19.92 | 33.6783 | -118.0096 | 68.967
GWD 1990 | Girth Weld |  | 4458.16 | 20.37 | 0.28 | 35000 | ERW | 8.625 | 715 | [10 empty] | AGM 1 | 2706.4 | AGM 2 | 490.13 | 20.62 | 20.37 | 20.79 | 20.62 | 20.37 | 1990 | 19.92 | 43.57 | 33.6783 | -118.0095 | 69.468
GWD 2000 | Girth Weld |  | 4478.53 | 19.91 | 0.28 | 35000 | ERW | 8.625 | 715 | [10 empty] | AGM 1 | 2726.77 | AGM 2 | 469.76 | 20.37 | 19.92 | 20.62 | 20.37 | 19.92 | 2000 | 43.57 | 42.49 | 33.6783 | -118.0095 | 69.787
GWD 2010 | Girth Weld |  | 4498.45 | 37.71 | 0.25 | 35000 | SMLS | 8.625 | 715 | [10 empty] | AGM 1 | 2746.68 | AGM 2 | 449.84 | 19.92 | 43.57 | 20.37 | 19.92 | 43.57 | 2010 | 42.49 | 20.96 | 33.6783 | -118.0094 | 70.054 | Estimated WT 0.250
DMA 120 | Metal Loss | Ext | 4536.16 | 0.52 | 0.25 | 35000 | SMLS | 8.625 | 715 | 16.4681 | 0.041 | 1.608 | 1.375 | 4:34 | 2509 | 0.3958 | 16 | 1.61 | 2489 | AGM 1 | 2784.39 | AGM 2 | 412.13 | 37.71 | 5.86 | 20.37 | 19.92 | 43.57 | 2010 | 42.49 | 20.96 | 33.6784 | -118.0093 | 70.561
DMA 121 | Metal Loss | Ext | 4536.68 | 0.63 | 0.25 | 35000 | SMLS | 8.625 | 715 | 32.1555 | 0.08 | 2.067 | 3.061 | 7:08 | 2320 | 0.42804 | 32 | 2.07 | 2255 | AGM 1 | 2784.92 | AGM 2 | 411.61 | 38.23 | 5.34 | 20.37 | 19.92 | 43.57 | 2010 | 42.49 | 20.96 | 33.6784 | -118.0093 | 70.571
DMA 122 | Metal Loss | Ext | 4537.31 | 4.71 | 0.25 | 35000 | SMLS | 8.625 | 715 | 25.142 | 0.063 | 0.607 | 1.698 | 9:44 | 2574 | 0.3858 | 25 | 0.61 | 2566 | AGM 1 | 2785.55 | AGM 2 | 410.97 | 38.87 | 4.71 | 20.37 | 19.92 | 43.57 | 2010 | 42.49 | 20.96 | 33.6784 | -118.0093 | 70.584
GWD 2020 | Girth Weld |  | 4542.02 | 42.49 | 0.25 | 35000 | SMLS | 8.625 | 715 | [10 empty] | AGM 1 | 2790.25 | AGM 2 | 406.27 | 43.57 | 42.49 | 19.92 | 43.57 | 42.49 | 2020 | 20.96 | 20.78 | 33.6784 | -118.0093 | 70.669
GWD 2030 | Girth Weld |  | 4584.51 | 20.96 | 0.28 | 35000 | ERW | 8.625 | 715 | [10 empty] | AGM 1 | 2832.74 | AGM 2 | 363.78 | 42.49 | 20.96 | 43.57 | 42.49 | 20.96 | 2030 | 20.78 | 20.07 | 33.6785 | -118.0092 | 71.259
GWD 2040 | Girth Weld |  | 4605.46 | 5.53 | 0.28 | 35000 | ERW | 8.625 | 715 | [10 empty] | AGM 1 | 2853.7 | AGM 2 | 342.82 | 20.96 | 20.78 | 42.49 | 20.96 | 20.78 | 2040 | 20.07 | 19.77 | 33.6785 | -118.0091 | 71.557
DMA 123 | Metal Loss | Ext | 4611 | 15.25 | 0.28 | 35000 | ERW | 8.625 | 715 | 15.2681 | 0.043 | 1.496 | 1.066 | 1:47 | 2835 | 0.35028 | 15 | 1.5 | 2818 | AGM 1 | 2859.23 | AGM 2 | 337.29 | 5.53 | 15.25 | 42.49 | 20.96 | 20.78 | 2040 | 20.07 | 19.77 | 33.6785 | -118.0091 | 71.688
GWD 2050 | Girth Weld |  | 4626.25 | 20.07 | 0.28 | 35000 | ERW | 8.625 | 715 | [10 empty] | AGM 1 | 2874.48 | AGM 2 | 322.04 | 20.78 | 20.07 | 20.96 | 20.78 | 20.07 | 2050 | 19.77 | 17.63 | 33.6785 | -118.0091 | 71.998
GWD 2060 | Girth Weld |  | 4646.32 | 19.77 | 0.28 | 35000 | ERW | 8.625 | 715 | [10 empty] | AGM 1 | 2894.56 | AGM 2 | 301.97 | 20.07 | 19.77 | 20.78 | 20.07 | 19.77 | 2060 | 17.63 | 19.33 | 33.6786 | -118.009 | 72.581
GWD 2070 | Girth Weld |  | 4666.09 | 14.25 | 0.28 | 35000 | ERW | 8.625 | 715 | [10 empty] | AGM 1 | 2914.33 | AGM 2 | 282.2 | 19.77 | 17.63 | 20.07 | 19.77 | 17.63 | 2070 | 19.33 | 36.84 | 33.6786 | -118.009 | 73.363
DMA 124 | Metal Loss | Ext | 4680.34 | 2.08 | 0.28 | 35000 | ERW | 8.625 | 715 | 16.1221 | 0.045 | 1.057 | 0.846 | 12:14 | 2867 | 0.34637 | 16 | 1.06 | 2856 | AGM 1 | 2928.58 | AGM 2 | 267.95 | 14.25 | 3.38 | 20.07 | 19.77 | 17.63 | 2070 | 19.33 | 36.84 | 33.6786 | -118.0089 | 73.981
DMA 125 | Metal Loss | Ext | 4682.42 | 1.3 | 0.28 | 35000 | ERW | 8.625 | 715 | 15.8169 | 0.044 | 1.193 | 1.07 | 10:33 | 2857 | 0.34759 | 16 | 1.19 | 2844 | AGM 1 | 2930.66 | AGM 2 | 265.86 | 16.33 | 1.3 | 20.07 | 19.77 | 17.63 | 2070 | 19.33 | 36.84 | 33.6786 | -118.0089 | 74.076
GWD 2080 | Girth Weld |  | 4683.72 | 19.33 | 0.28 | 35000 | ERW | 8.625 | 715 | [10 empty] | AGM 1 | 2931.95 | AGM 2 | 264.57 | 17.63 | 19.33 | 19.77 | 17.63 | 19.33 | 2080 | 36.84 | 19.94 | 33.6786 | -118.0089 | 74.137
GWD 2090 | Girth Weld |  | 4703.05 | 36.84 | 0.28 | 35000 | SMLS | 8.625 | 715 | [10 empty] | AGM 1 | 2951.29 | AGM 2 | 245.23 | 19.33 | 36.84 | 17.63 | 19.33 | 36.84 | 2090 | 19.94 | 16.32 | 33.6787 | -118.0089 | 74.975
GWD 2100 | Girth Weld |  | 4739.89 | 19.94 | 0.28 | 35000 | ERW | 8.625 | 715 | [10 empty] | AGM 1 | 2988.13 | AGM 2 | 208.4 | 36.84 | 19.94 | 19.33 | 36.84 | 19.94 | 2100 | 16.32 | 18.97 | 33.6787 | -118.0088 | 76.54
GWD 2110 | Girth Weld |  | 4759.84 | 16.32 | 0.28 | 35000 | ERW | 8.625 | 715 | [10 empty] | AGM 1 | 3008.07 | AGM 2 | 188.45 | 19.94 | 16.32 | 36.84 | 19.94 | 16.32 | 2110 | 18.97 | 18.53 | 33.6787 | -118.0087 | 77.257
GWD 2120 | Girth Weld |  | 4776.16 | 18.96 | 0.28 | 35000 | ERW | 8.625 | 715 | [10 empty] | AGM 1 | 3024.39 | AGM 2 | 172.13 | 16.32 | 18.97 | 19.94 | 16.32 | 18.97 | 2120 | 18.53 | 19.42 | 33.6788 | -118.0087 | 77.847
GWD 2130 | Girth Weld |  | 4795.12 | 18.54 | 0.28 | 35000 | ERW | 8.625 | 715 | [10 empty] | AGM 1 | 3043.36 | AGM 2 | 153.17 | 18.97 | 18.53 | 16.32 | 18.97 | 18.53 | 2130 | 19.42 | 1.57 | 33.6788 | -118.0086 | 78.57
GWD 2140 | Girth Weld |  | 4813.66 | 14.2 | 0.28 | 35000 | ERW | 8.625 | 715 | [10 empty] | AGM 1 | 3061.89 | AGM 2 | 134.63 | 18.53 | 19.42 | 18.97 | 18.53 | 19.42 | 2140 | 1.57 | 1.02 | 33.6788 | -118.0086 | 79.318
DMA 126 | Metal Loss | Ext | 4827.86 | 4.25 | 0.28 | 35000 | ERW | 8.625 | 715 | 45.4412 | 0.127 | 1.114 | 0.664 | 10:19 | 2700 | 0.3678 | 45 | 1.11 | 2636 | AGM 1 | 3076.09 | AGM 2 | 120.43 | 14.2 | 5.22 | 18.97 | 18.53 | 19.42 | 2140 | 1.57 | 1.02 | 33.6789 | -118.0085 | 79.804
TAP 3 | TAP |  | 4832.11 | 0.96 | 0.28 | 35000 | ERW | 8.625 | 715 |  |  |  |  | 12:15 | [5 empty] | AGM 1 | 3080.35 | AGM 2 | 116.17 | 18.46 | 0.96 | 18.97 | 18.53 | 19.42 | 2140 | 1.57 | 1.02 | 33.6789 | -118.0085 | 79.948
GWD 2150 | Girth Weld |  | 4833.08 | 1.57 | 0.28 | 35000 | ERW | 8.625 | 715 | [10 empty] | AGM 1 | 3081.31 | AGM 2 | 115.21 | 19.42 | 1.57 | 18.53 | 19.42 | 1.57 | 2150 | 1.02 | 3.3 | 33.6789 | -118.0085 | 79.978
GWD 2160 | Girth Weld |  | 4834.65 | 1.02 | 0.28 | 35000 | ERW | 8.625 | 715 | [10 empty] | AGM 1 | 3082.88 | AGM 2 | 113.64 | 1.57 | 1.02 | 19.42 | 1.57 | 1.02 | 2160 | 3.3 | 6.22 | 33.6789 | -118.0085 | 80.032
GWD 2170 | Girth Weld |  | 4835.67 | 1.83 | 0.28 | 35000 | ERW | 8.625 | 715 | [10 empty] | AGM 1 | 3083.91 | AGM 2 | 112.62 | 1.02 | 3.3 | 1.57 | 1.02 | 3.3 | 2170 | 6.22 | 5.38 | 33.6789 | -118.0085 | 80.055
BND 36 | Bend |  | 4837.5 | 1.47 | 0.28 | 35000 | ERW | 8.625 | 715 |  |  | 37.922 | [7 empty] | AGM 1 | 3085.74 | AGM 2 | 110.78 | 1.83 | 1.47 | 1.57 | 1.02 | 3.3 | 2170 | 6.22 | 5.38 | 33.6789 | -118.0085 | 79.979 | 3.0D 88.6 deg left turn over bend
GWD 2180 | Girth Weld |  | 4838.97 | 6.22 | 0.28 | 35000 | ERW | 8.625 | 715 | [10 empty] | AGM 1 | 3087.21 | AGM 2 | 109.31 | 3.3 | 6.22 | 1.02 | 3.3 | 6.22 | 2180 | 5.38 | 3.24 | 33.6789 | -118.0085 | 79.776
GWD 2190 | Girth Weld |  | 4845.19 | 5.38 | 0.28 | 35000 | ERW | 8.625 | 715 | [10 empty] | AGM 1 | 3093.43 | AGM 2 | 103.1 | 6.22 | 5.38 | 3.3 | 6.22 | 5.38 | 2190 | 3.24 | 23.89 | 33.6789 | -118.0085 | 78.764
GWD 2200 | Girth Weld |  | 4850.57 | 1.72 | 0.28 | 35000 | ERW | 8.625 | 715 | [10 empty] | AGM 1 | 3098.8 | AGM 2 | 97.72 | 5.38 | 3.24 | 6.22 | 5.38 | 3.24 | 2200 | 23.89 | 1.14 | 33.6789 | -118.0085 | 77.83
BND 37 | Bend |  | 4852.29 | 1.52 | 0.28 | 35000 | ERW | 8.625 | 715 |  |  | 37.419 | [7 empty] | AGM 1 | 3100.52 | AGM 2 | 96 | 1.72 | 1.52 | 6.22 | 5.38 | 3.24 | 2200 | 23.89 | 1.14 | 33.6789 | -118.0085 | 77.558 | 3.0D 89.8 deg right turn sag bend
GWD 2210 | Girth Weld |  | 4853.81 | 23.89 | 0.28 | 35000 | ERW | 8.625 | 715 | [10 empty] | AGM 1 | 3102.04 | AGM 2 | 94.48 | 3.24 | 23.89 | 5.38 | 3.24 | 23.89 | 2210 | 1.14 | 41.22 | 33.6789 | -118.0085 | 77.481
GWD 2220 | Girth Weld |  | 4877.7 | 1.15 | 0.28 | 35000 | ERW | 8.625 | 715 | [10 empty] | AGM 1 | 3125.93 | AGM 2 | 70.59 | 23.89 | 1.14 | 3.24 | 23.89 | 1.14 | 2220 | 41.22 | 29.49 | 33.6789 | -118.0085 | 78.174
GWD 2230 | Girth Weld |  | 4878.84 | 1.58 | 0.28 | 35000 | SMLS | 8.625 | 715 | [10 empty] | AGM 1 | 3127.08 | AGM 2 | 69.45 | 1.14 | 41.22 | 23.89 | 1.14 | 41.22 | 2230 | 29.49 | 28.49 | 33.6789 | -118.0085 | 78.216
TAP 4 | TAP |  | 4880.42 | 0.87 | 0.28 | 35000 | SMLS | 8.625 | 715 |  |  |  |  | 11:51 | [5 empty] | AGM 1 | 3128.66 | AGM 2 | 67.86 | 1.58 | 39.63 | 23.89 | 1.14 | 41.22 | 2230 | 29.49 | 28.49 | 33.6789 | -118.0085 | 78.272
DMA 127 | Metal Loss | Ext | 4881.3 | 2.23 | 0.28 | 35000 | SMLS | 8.625 | 715 | 38.7755 | 0.109 | 0.992 | 1.209 | 1:45 | 2775 | 0.35786 | 39 | 0.99 | 2736 | AGM 1 | 3129.53 | AGM 2 | 66.99 | 2.46 | 38.76 | 23.89 | 1.14 | 41.22 | 2230 | 29.49 | 28.49 | 33.6789 | -118.0085 | 78.308
CLS 17 | Cluster | Ext | 4883.53 | 15.92 | 0.28 | 35000 | SMLS | 8.625 | 715 | 22.6003 | 0.063 | 1.971 | 1.205 | 11:51 | 2731 | 0.36362 | 16 | 1.97 | 2766 | AGM 1 | 3131.76 | AGM 2 | 64.76 | 4.69 | 36.53 | 23.89 | 1.14 | 41.22 | 2230 | 29.49 | 28.49 | 33.679 | -118.0085 | 78.394 | CLS C
DMA 130 | Metal Loss | Ext | 4899.45 | 4.92 | 0.28 | 35000 | SMLS | 8.625 | 715 | 14.0783 | 0.039 | 0.798 | 0.687 | 11:49 | 2893 | 0.34326 | 14 | 0.8 | 2887 | AGM 1 | 3147.68 | AGM 2 | 48.84 | 20.6 | 20.61 | 23.89 | 1.14 | 41.22 | 2230 | 29.49 | 28.49 | 33.679 | -118.0084 | 78.961
DMA 131 | Metal Loss | Ext | 4904.36 | 0.68 | 0.28 | 35000 | SMLS | 8.625 | 715 | 16.3054 | 0.046 | 1.726 | 1.947 | 12:38 | 2810 | 0.3534 | 16 | 1.73 | 2787 | AGM 1 | 3152.6 | AGM 2 | 43.92 | 25.52 | 15.7 | 23.89 | 1.14 | 41.22 | 2230 | 29.49 | 28.49 | 33.679 | -118.0084 | 79.132
DMA 132 | Metal Loss | Ext | 4905.04 | 0.29 | 0.28 | 35000 | SMLS | 8.625 | 715 | 53.6039 | 0.15 | 0.733 | 1.341 | 11:06 | 2775 | 0.35786 | 54 | 0.73 | 2723 | AGM 1 | 3153.28 | AGM 2 | 43.24 | 26.2 | 15.02 | 23.89 | 1.14 | 41.22 | 2230 | 29.49 | 28.49 | 33.679 | -118.0084 | 79.154
DMA 133 | Metal Loss | Ext | 4905.33 | 0.17 | 0.28 | 35000 | SMLS | 8.625 | 715 | 39.6891 | 0.111 | 0.525 | 0.545 | 11:58 | 2872 | 0.34577 | 40 | 0.53 | 2858 | AGM 1 | 3153.57 | AGM 2 | 42.95 | 26.49 | 14.73 | 23.89 | 1.14 | 41.22 | 2230 | 29.49 | 28.49 | 33.679 | -118.0084 | 79.165
DMA 134 | Metal Loss | Ext | 4905.5 | 14.56 | 0.28 | 35000 | SMLS | 8.625 | 715 | 11.0989 | 0.031 | 1.74 | 2.113 | 10:17 | 2847 | 0.34881 | 11 | 1.74 | 2833 | AGM 1 | 3153.74 | AGM 2 | 42.79 | 26.66 | 14.56 | 23.89 | 1.14 | 41.22 | 2230 | 29.49 | 28.49 | 33.679 | -118.0084 | 79.169
GWD 2240 | Girth Weld |  | 4920.06 | 21 | 0.28 | 35000 | SMLS | 8.625 | 715 | [10 empty] | AGM 1 | 3168.29 | AGM 2 | 28.23 | 41.22 | 29.49 | 1.14 | 41.22 | 29.49 | 2240 | 28.49 | 38.42 | 33.679 | -118.0084 | 79.73
CLS 18 | Cluster | Ext | 4941.06 | 0.08 | 0.28 | 35000 | SMLS | 8.625 | 715 | 52.7936 | 0.148 | 3.068 | 9.073 | 10:57 | 2129 | 0.46644 | 41 | 3.07 | 2211 | AGM 1 | 3189.3 | AGM 2 | 7.22 | 21 | 8.49 | 1.14 | 41.22 | 29.49 | 2240 | 28.49 | 38.42 | 33.679 | -118.0083 | 80.724 | CLS C
DMA 138 | Metal Loss | Ext | 4941.14 | 7.14 | 0.28 | 35000 | SMLS | 8.625 | 715 | 12.7346 | 0.036 | 1.1 | 1.379 | 5:35 | 2877 | 0.34517 | 13 | 1.1 | 2868 | AGM 1 | 3189.38 | AGM 2 | 7.14 | 21.08 | 8.41 | 1.14 | 41.22 | 29.49 | 2240 | 28.49 | 38.42 | 33.679 | -118.0083 | 80.729
MRK 2 | Marker |  | 4948.29 | 1.27 | 0.28 | 35000 | SMLS | 8.625 | 715 |  |  |  |  | 11:40 | [5 empty] | AGM 1 | 3196.52 | Valve 607 | 2914.34 | 28.23 | 1.27 | 1.14 | 41.22 | 29.49 | 2240 | 28.49 | 38.42 | 33.679 | -118.0083 | 81.058 | AGM 2 34' U/S of Silver Beach Circle - 9' U/S of Metal Fence
GWD 2250 | Girth Weld |  | 4949.55 | 28.48 | 0.28 | 35000 | SMLS | 8.625 | 715 | [10 empty] | AGM 2 | 1.27 | Valve 607 | 2913.07 | 29.49 | 28.49 | 41.22 | 29.49 | 28.49 | 2250 | 38.42 | 37.96 | 33.6791 | -118.0083 | 80.986
GWD 2260 | Girth Weld |  | 4978.04 | 38.42 | 0.28 | 35000 | SMLS | 8.625 | 715 | [10 empty] | AGM 2 | 29.75 | Valve 607 | 2884.59 | 28.49 | 38.42 | 29.49 | 28.49 | 38.42 | 2260 | 37.96 | 0.52 | 33.6791 | -118.0082 | 79.209
GWD 2270 | Girth Weld |  | 5016.46 | 37.96 | 0.28 | 35000 | SMLS | 8.625 | 715 | [10 empty] | AGM 2 | 68.18 | Valve 607 | 2846.16 | 38.42 | 37.96 | 28.49 | 38.42 | 37.96 | 2270 | 0.52 | 5.42 | 33.6792 | -118.0081 | 75.915
GWD 2280 | Girth Weld |  | 5054.42 | 0.28 | 0.28 | 35000 | SMLS | 8.625 | 715 | [10 empty] | AGM 2 | 106.13 | Valve 607 | 2808.21 | 37.96 | 0.52 | 38.42 | 37.96 | 0.52 | 2280 | 5.42 | 28.37 | 33.6793 | -118.008 | 72.212
BND 38 | Bend |  | 5054.7 | 0.24 | 0.28 | 35000 | SMLS | 8.625 | 715 |  |  | 6.26 | [7 empty] | AGM 2 | 106.41 | Valve 607 | 2807.93 | 0.28 | 0.25 | 38.42 | 37.96 | 0.52 | 2280 | 5.42 | 28.37 | 33.6793 | -118.008 | 72.222 | 1.5D 29.9 deg left turn sag bend
GWD 2290 | Girth Weld |  | 5054.94 | 5.42 | 0.28 | 35000 | SMLS | 8.625 | 715 | [10 empty] | AGM 2 | 106.65 | Valve 607 | 2807.68 | 0.52 | 5.42 | 37.96 | 0.52 | 5.42 | 2290 | 28.37 | 29.26 | 33.6793 | -118.008 | 72.238
GWD 2300 | Girth Weld |  | 5060.36 | 28.37 | 0.28 | 35000 | SMLS | 8.625 | 715 | [10 empty] | AGM 2 | 112.08 | Valve 607 | 2802.26 | 5.42 | 28.37 | 0.52 | 5.42 | 28.37 | 2300 | 29.26 | 28.49 | 33.6793 | -118.008 | 72.598
GWD 2310 | Girth Weld |  | 5088.73 | 29.26 | 0.28 | 35000 | SMLS | 8.625 | 715 | [10 empty] | AGM 2 | 140.44 | Valve 607 | 2773.89 | 28.37 | 29.26 | 5.42 | 28.37 | 29.26 | 2310 | 28.49 | 33.56 | 33.6794 | -118.0079 | 74.202
GWD 2320 | Girth Weld |  | 5117.99 | 28.49 | 0.28 | 35000 | SMLS | 8.625 | 715 | [10 empty] | AGM 2 | 169.71 | Valve 607 | 2744.63 | 29.26 | 28.49 | 28.37 | 29.26 | 28.49 | 2320 | 33.56 | 41.47 | 33.6794 | -118.0079 | 74.896
GWD 2330 | Girth Weld |  | 5146.49 | 33.56 | 0.28 | 35000 | SMLS | 8.625 | 715 | [10 empty] | AGM 2 | 198.2 | Valve 607 | 2716.14 | 28.49 | 33.56 | 29.26 | 28.49 | 33.56 | 2330 | 41.47 | 40.22 | 33.6795 | -118.0079 | 75.79
GWD 2340 | Girth Weld |  | 5180.04 | 41.47 | 0.28 | 35000 | SMLS | 8.625 | 715 | [10 empty] | AGM 2 | 231.75 | Valve 607 | 2682.58 | 33.56 | 41.47 | 28.49 | 33.56 | 41.47 | 2340 | 40.22 | 36.11 | 33.6796 | -118.0078 | 76.473
GWD 2350 | Girth Weld |  | 5221.52 | 40.22 | 0.28 | 35000 | SMLS | 8.625 | 715 | [10 empty] | AGM 2 | 273.23 | Valve 607 | 2641.11 | 41.47 | 40.22 | 33.56 | 41.47 | 40.22 | 2350 | 36.11 | 47.67 | 33.6797 | -118.0078 | 77.329
GWD 2360 | Girth Weld |  | 5261.74 | 36.11 | 0.28 | 35000 | SMLS | 8.625 | 715 | [10 empty] | AGM 2 | 313.45 | Valve 607 | 2600.89 | 40.22 | 36.11 | 41.47 | 40.22 | 36.11 | 2360 | 47.67 | 34.78 | 33.6798 | -118.0078 | 79.212
GWD 2370 | Girth Weld |  | 5297.85 | 47.67 | 0.28 | 35000 | ERW | 8.625 | 715 | [10 empty] | AGM 2 | 349.56 | Valve 607 | 2564.78 | 36.11 | 47.67 | 40.22 | 36.11 | 47.67 | 2370 | 34.78 | 34.13 | 33.6799 | -118.0078 | 79.929
GWD 2380 | Girth Weld |  | 5345.52 | 3.22 | 0.28 | 35000 | ERW | 8.625 | 715 | [10 empty] | AGM 2 | 397.23 | Valve 607 | 2517.11 | 47.67 | 34.78 | 36.11 | 47.67 | 34.78 | 2380 | 34.13 | 1.56 | 33.68 | -118.0078 | 81.211
DMA 139 | Metal Loss | Ext | 5348.74 | 1.21 | 0.28 | 35000 | ERW | 8.625 | 715 | 24.0023 | 0.067 | 0.533 | 0.742 | 5:44 | 2896 | 0.34291 | 24 | 0.53 | 2890 | AGM 2 | 400.45 | Valve 607 | 2513.89 | 3.22 | 31.56 | 36.11 | 47.67 | 34.78 | 2380 | 34.13 | 1.56 | 33.68 | -118.0078 | 81.439
CLS 19 | Cluster | Ext | 5349.95 | 0.19 | 0.28 | 35000 | ERW | 8.625 | 715 | 20.0317 | 0.056 | 1.812 | 2.351 | 2:16 | 2771 | 0.35837 | 13 | 1.81 | 2809 | AGM 2 | 401.66 | Valve 607 | 2512.68 | 4.43 | 30.35 | 36.11 | 47.67 | 34.78 | 2380 | 34.13 | 1.56 | 33.68 | -118.0078 | 81.522 | CLS C
DMA 142 | Metal Loss | Ext | 5350.14 | 1.05 | 0.28 | 35000 | ERW | 8.625 | 715 | 11.5343 | 0.032 | 0.481 | 0.643 | 1:49 | 2913 | 0.3409 | 12 | 0.48 | 2911 | AGM 2 | 401.86 | Valve 607 | 2512.48 | 4.63 | 30.16 | 36.11 | 47.67 | 34.78 | 2380 | 34.13 | 1.56 | 33.68 | -118.0078 | 81.54
DMA 143 | Metal Loss | Ext | 5351.2 | 3.04 | 0.28 | 35000 | ERW | 8.625 | 715 | 18.5269 | 0.052 | 0.79 | 0.564 | 2:05 | 2883 | 0.34445 | 19 | 0.79 | 2875 | AGM 2 | 402.91 | Valve 607 | 2511.43 | 5.68 | 29.1 | 36.11 | 47.67 | 34.78 | 2380 | 34.13 | 1.56 | 33.68 | -118.0078 | 81.611
DMA 144 | Metal Loss | Ext | 5354.24 | 0.02 | 0.28 | 35000 | ERW | 8.625 | 715 | 16.3746 | 0.046 | 1.723 | 2.834 | 11:36 | 2809 | 0.35353 | 16 | 1.72 | 2787 | AGM 2 | 405.96 | Valve 607 | 2508.38 | 8.72 | 26.06 | 36.11 | 47.67 | 34.78 | 2380 | 34.13 | 1.56 | 33.68 | -118.0078 | 81.8
DMA 145 | Metal Loss | Ext | 5354.26 | 0.03 | 0.28 | 35000 | ERW | 8.625 | 715 | 14.8681 | 0.042 | 0.444 | 0.564 | 3:33 | 2911 | 0.34114 | 15 | 0.44 | 2909 | AGM 2 | 405.97 | Valve 607 | 2508.37 | 8.74 | 26.04 | 36.11 | 47.67 | 34.78 | 2380 | 34.13 | 1.56 | 33.68 | -118.0078 | 81.8
DMA 146 | Metal Loss | Ext | 5354.29 | 0.17 | 0.28 | 35000 | ERW | 8.625 | 715 | 12.0716 | 0.034 | 1.173 | 0.827 | 1:32 | 2875 | 0.34541 | 12 | 1.17 | 2866 | AGM 2 | 406 | Valve 607 | 2508.34 | 8.77 | 26.01 | 36.11 | 47.67 | 34.78 | 2380 | 34.13 | 1.56 | 33.68 | -118.0078 | 81.801
DMA 147 | Metal Loss | Ext | 5354.46 | 0.18 | 0.28 | 35000 | ERW | 8.625 | 715 | 15.4215 | 0.043 | 0.599 | 0.716 | 1:35 | 2903 | 0.34208 | 15 | 0.6 | 2899 | AGM 2 | 406.17 | Valve 607 | 2508.17 | 8.94 | 25.85 | 36.11 | 47.67 | 34.78 | 2380 | 34.13 | 1.56 | 33.68 | -118.0078 | 81.813
DMA 148 | Metal Loss | Ext | 5354.64 | 3.36 | 0.28 | 35000 | ERW | 8.625 | 715 | 18.3739 | 0.051 | 0.804 | 0.761 | 12:53 | 2882 | 0.34457 | 18 | 0.8 | 2873 | AGM 2 | 406.35 | Valve 607 | 2507.99 | 9.12 | 25.67 | 36.11 | 47.67 | 34.78 | 2380 | 34.13 | 1.56 | 33.68 | -118.0078 | 81.824
DMA 149 | Metal Loss | Ext | 5358 | 0.07 | 0.28 | 35000 | ERW | 8.625 | 715 | 11.9207 | 0.033 | 1.459 | 1.817 | 3:08 | 2858 | 0.34747 | 12 | 1.46 | 2846 | AGM 2 | 409.71 | Valve 607 | 2504.63 | 12.48 | 22.3 | 36.11 | 47.67 | 34.78 | 2380 | 34.13 | 1.56 | 33.68 | -118.0078 | 82.018
DMA 150 | Metal Loss | Ext | 5358.07 | 22.23 | 0.28 | 35000 | ERW | 8.625 | 715 | 21.9562 | 0.061 | 2.118 | 1.579 | 11:42 | 2723 | 0.36469 | 22 | 2.12 | 2681 | AGM 2 | 409.78 | Valve 607 | 2504.56 | 12.55 | 22.23 | 36.11 | 47.67 | 34.78 | 2380 | 34.13 | 1.56 | 33.68 | -118.0078 | 82.023
GWD 2390 | Girth Weld |  | 5380.3 | 31.3 | 0.28 | 35000 | ERW | 8.625 | 715 | [10 empty] | AGM 2 | 432.01 | Valve 607 | 2482.32 | 34.78 | 34.13 | 47.67 | 34.78 | 34.13 | 2390 | 1.56 | 1.54 | 33.6801 | -118.0079 | 82.959
TAP 5 | TAP |  | 5411.6 | 2.84 | 0.28 | 35000 | ERW | 8.625 | 715 |  |  |  |  | 11:54 | [5 empty] | AGM 2 | 463.31 | Valve 607 | 2451.03 | 31.3 | 2.83 | 47.67 | 34.78 | 34.13 | 2390 | 1.56 | 1.54 | 33.6801 | -118.0079 | 83.862
GWD 2400 | Girth Weld |  | 5414.43 | 1.56 | 0.28 | 35000 | ERW | 8.625 | 715 | [10 empty] | AGM 2 | 466.14 | Valve 607 | 2448.2 | 34.13 | 1.56 | 34.78 | 34.13 | 1.56 | 2400 | 1.54 | 1.29 | 33.6801 | -118.0079 | 83.94
GWD 2410 | Girth Weld |  | 5415.99 | 0.76 | 0.28 | 35000 | ERW | 8.625 | 715 | [10 empty] | AGM 2 | 467.7 | Valve 607 | 2446.64 | 1.56 | 1.54 | 34.13 | 1.56 | 1.54 | 2410 | 1.29 | 1.6 | 33.6801 | -118.0079 | 84.01
BND 39 | Bend |  | 5416.75 | 0.78 | 0.28 | 35000 | ERW | 8.625 | 715 |  |  | 25.931 | [7 empty] | AGM 2 | 468.47 | Valve 607 | 2445.87 | 0.76 | 0.78 | 34.13 | 1.56 | 1.54 | 2410 | 1.29 | 1.6 | 33.6801 | -118.0079 | 83.87 | 3.0D 49.7 deg right turn over bend
GWD 2420 | Girth Weld |  | 5417.53 | 1.29 | 0.28 | 35000 | ERW | 8.625 | 715 | [10 empty] | AGM 2 | 469.25 | Valve 607 | 2445.09 | 1.54 | 1.29 | 1.56 | 1.54 | 1.29 | 2420 | 1.6 | 1.85 | 33.6801 | -118.0079 | 83.491
GWD 2430 | Girth Weld |  | 5418.82 | 0.8 | 0.28 | 35000 | ERW | 8.625 | 715 | [10 empty] | AGM 2 | 470.54 | Valve 607 | 2443.8 | 1.29 | 1.6 | 1.54 | 1.29 | 1.6 | 2430 | 1.85 | 3.28 | 33.6801 | -118.0079 | 82.603
BND 40 | Bend |  | 5419.63 | 0.8 | 0.28 | 35000 | ERW | 8.625 | 715 |  |  | 21.956 | [7 empty] | AGM 2 | 471.34 | Valve 607 | 2443 | 0.8 | 0.79 | 1.54 | 1.29 | 1.6 | 2430 | 1.85 | 3.28 | 33.6801 | -118.0079 | 82.174 | 3.0D 46.6 deg left turn sag bend
GWD 2440 | Girth Weld |  | 5420.42 | 1.85 | 0.28 | 35000 | ERW | 8.625 | 715 | [10 empty] | AGM 2 | 472.14 | Valve 607 | 2442.2 | 1.6 | 1.85 | 1.29 | 1.6 | 1.85 | 2440 | 3.28 | 3.24 | 33.6801 | -118.0079 | 82.013
GWD 2450 | Girth Weld |  | 5422.27 | 1.34 | 0.28 | 35000 | ERW | 8.625 | 715 | [10 empty] | AGM 2 | 473.99 | Valve 607 | 2440.35 | 1.85 | 3.28 | 1.6 | 1.85 | 3.28 | 2450 | 3.24 | 3.85 | 33.6801 | -118.0079 | 82.047
DMA 151 | Metal Loss | Ext | 5423.61 | 0.35 | 0.28 | 35000 | ERW | 8.625 | 715 | 11.7881 | 0.033 | 0.315 | 0.507 | 11:49 | 2918 | 0.34032 | 12 | 0.31 | 2917 | AGM 2 | 475.32 | Valve 607 | 2439.01 | 1.34 | 1.94 | 1.6 | 1.85 | 3.28 | 2450 | 3.24 | 3.85 | 33.6802 | -118.0079 | 82.502
DMA 152 | Metal Loss | Ext | 5423.97 | 0.64 | 0.28 | 35000 | ERW | 8.625 | 715 | 15.9463 | 0.045 | 0.403 | 0.554 | 12:08 | 2912 | 0.34102 | 16 | 0.4 | 2910 | AGM 2 | 475.68 | Valve 607 | 2438.66 | 1.69 | 1.59 | 1.6 | 1.85 | 3.28 | 2450 | 3.24 | 3.85 | 33.6802 | -118.0079 | 82.748
CLS 20 | Cluster | Ext | 5424.6 | 0.95 | 0.28 | 35000 | ERW | 8.625 | 715 | 18.1951 | 0.051 | 1.011 | 1.868 | 12:20 | 2864 | 0.34674 | 11 | 1.01 | 2883 | AGM 2 | 476.31 | Valve 607 | 2438.02 | 2.33 | 0.95 | 1.6 | 1.85 | 3.28 | 2450 | 3.24 | 3.85 | 33.6802 | -118.0079 | 83.281 | CLS C
GWD 2460 | Girth Weld |  | 5425.55 | 0.12 | 0.28 | 35000 | ERW | 8.625 | 715 | [10 empty] | AGM 2 | 477.26 | Valve 607 | 2437.07 | 3.28 | 3.24 | 1.85 | 3.28 | 3.24 | 2460 | 3.85 | 32.62 | 33.6802 | -118.0079 | 84.205
BND 41 | Bend |  | 5425.67 | 3.12 | 0.28 | 35000 | ERW | 8.625 | 715 |  |  | 81.859 | [7 empty] | AGM 2 | 477.38 | Valve 607 | 2436.96 | 0.12 | 3.12 | 1.85 | 3.28 | 3.24 | 2460 | 3.85 | 32.62 | 33.6802 | -118.0079 | 84.32 | 3.0D 100.5 deg right turn bend
GWD 2470 | Girth Weld |  | 5428.79 | 3.85 | 0.28 | 35000 | ERW | 8.625 | 715 | [10 empty] | AGM 2 | 480.5 | Valve 607 | 2433.84 | 3.24 | 3.85 | 3.28 | 3.24 | 3.85 | 2470 | 32.62 | 2.15 | 33.6802 | -118.0079 | 86.526
GWD 2480 | Girth Weld |  | 5432.64 | 1.32 | 0.28 | 35000 | ERW | 8.625 | 715 | [10 empty] | AGM 2 | 484.35 | Valve 607 | 2429.99 | 3.85 | 32.62 | 3.24 | 3.85 | 32.62 | 2480 | 2.15 | 3.37 | 33.6802 | -118.0079 | 86.506
TAP 6 | TAP |  | 5433.96 | 10.17 | 0.28 | 35000 | ERW | 8.625 | 715 |  |  |  |  | 12:31 | [5 empty] | AGM 2 | 485.67 | Valve 607 | 2428.67 | 1.32 | 31.3 | 3.24 | 3.85 | 32.62 | 2480 | 2.15 | 3.37 | 33.6802 | -118.0079 | 86.478
DMA 155 | Metal Loss | Ext | 5444.12 | 3.08 | 0.28 | 35000 | ERW | 8.625 | 715 | 30.6304 | 0.086 | 0.751 | 1.097 | 2:59 | 2855 | 0.34783 | 31 | 0.75 | 2839 | AGM 2 | 495.83 | Valve 607 | 2418.5 | 11.49 | 21.14 | 3.24 | 3.85 | 32.62 | 2480 | 2.15 | 3.37 | 33.6802 | -118.0078 | 86.313
DMA 156 | Metal Loss | Ext | 5447.2 | 11.99 | 0.28 | 35000 | ERW | 8.625 | 715 | 15.6359 | 0.044 | 0.926 | 4.596 | 6:25 | 2880 | 0.34481 | 16 | 0.93 | 2871 | AGM 2 | 498.91 | Valve 607 | 2415.43 | 14.56 | 18.06 | 3.24 | 3.85 | 32.62 | 2480 | 2.15 | 3.37 | 33.6802 | -118.0078 | 86.26
CLS 21 | Cluster | Ext | 5459.18 | 0.39 | 0.28 | 35000 | ERW | 8.625 | 715 | 17.6013 | 0.049 | 2.09 | 2.184 | 10:45 | 2769 | 0.35863 | 17 | 2.09 | 2741 | AGM 2 | 510.9 | Valve 607 | 2403.44 | 26.55 | 6.08 | 3.24 | 3.85 | 32.62 | 2480 | 2.15 | 3.37 | 33.6802 | -118.0078 | 85.946 | CLS C
DMA 159 | Metal Loss | Ext | 5459.57 | 5.69 | 0.28 | 35000 | ERW | 8.625 | 715 | 12.479 | 0.035 | 0.795 | 0.617 | 3:06 | 2897 | 0.34279 | 12 | 0.79 | 2892 | AGM 2 | 511.28 | Valve 607 | 2403.05 | 26.94 | 5.69 | 3.24 | 3.85 | 32.62 | 2480 | 2.15 | 3.37 | 33.6802 | -118.0078 | 85.931
GWD 2490 | Girth Weld |  | 5465.26 | 2.15 | 0.28 | 35000 | ERW | 8.625 | 715 | [10 empty] | AGM 2 | 516.97 | Valve 607 | 2397.37 | 32.62 | 2.15 | 3.85 | 32.62 | 2.15 | 2490 | 3.37 | 47.3 | 33.6802 | -118.0078 | 85.739
GWD 2500 | Girth Weld |  | 5467.41 | 2.09 | 0.28 | 35000 | ERW | 8.625 | 715 | [10 empty] | AGM 2 | 519.12 | Valve 607 | 2395.22 | 2.15 | 3.37 | 32.62 | 2.15 | 3.37 | 2500 | 47.3 | 33.85 | 33.6802 | -118.0078 | 85.671
CLS 22 | Cluster | Ext | 5469.49 | 0.15 | 0.28 | 35000 | ERW | 8.625 | 715 | 13.3813 | 0.037 | 2.577 | 0.834 | 8:30 | 2782 | 0.35696 | 9 | 2.58 | 2808 | AGM 2 | 521.21 | Valve 607 | 2393.13 | 2.09 | 1.28 | 32.62 | 2.15 | 3.37 | 2500 | 47.3 | 33.85 | 33.6802 | -118.0078 | 85.619 | CLS C
DMA 162 | Metal Loss | Ext | 5469.65 | 1.13 | 0.28 | 35000 | ERW | 8.625 | 715 | 16.9183 | 0.047 | 0.956 | 0.588 | 7:01 | 2873 | 0.34565 | 17 | 0.96 | 2863 | AGM 2 | 521.36 | Valve 607 | 2392.98 | 2.24 | 1.13 | 32.62 | 2.15 | 3.37 | 2500 | 47.3 | 33.85 | 33.6802 | -118.0078 | 85.617
GWD 2510 | Girth Weld |  | 5470.77 | 0.54 | 0.28 | 35000 | ERW | 8.625 | 715 | [10 empty] | AGM 2 | 522.49 | Valve 607 | 2391.85 | 3.37 | 47.3 | 2.15 | 3.37 | 47.3 | 2510 | 33.85 | 18.5 | 33.6802 | -118.0078 | 85.589
DMA 163 | Metal Loss | Ext | 5471.31 | 0.49 | 0.28 | 35000 | ERW | 8.625 | 715 | 16.2618 | 0.046 | 0.682 | 0.649 | 2:26 | 2896 | 0.34291 | 16 | 0.68 | 2891 | AGM 2 | 523.02 | Valve 607 | 2391.32 | 0.54 | 46.76 | 2.15 | 3.37 | 47.3 | 2510 | 33.85 | 18.5 | 33.6802 | -118.0078 | 85.581
DMA 164 | Metal Loss | Ext | 5471.8 | 2.96 | 0.28 | 35000 | ERW | 8.625 | 715 | 28.2184 | 0.079 | 1.033 | 2.108 | 5:26 | 2820 | 0.35215 | 28 | 1.03 | 2795 | AGM 2 | 523.52 | Valve 607 | 2390.82 | 1.03 | 46.27 | 2.15 | 3.37 | 47.3 | 2510 | 33.85 | 18.5 | 33.6802 | -118.0077 | 85.573
DMA 165 | Metal Loss | Ext | 5474.76 | 1.23 | 0.28 | 35000 | ERW | 8.625 | 715 | 24.2468 | 0.068 | 0.666 | 0.568 | 3:12 | 2882 | 0.34457 | 24 | 0.67 | 2873 | AGM 2 | 526.47 | Valve 607 | 2387.87 | 3.99 | 43.31 | 2.15 | 3.37 | 47.3 | 2510 | 33.85 | 18.5 | 33.6802 | -118.0077 | 85.53
DMA 166 | Metal Loss | Ext | 5475.99 | 4.87 | 0.28 | 35000 | ERW | 8.625 | 715 | 20.2159 | 0.057 | 1.103 | 3.566 | 12:04 | 2846 | 0.34893 | 20 | 1.1 | 2830 | AGM 2 | 527.7 | Valve 607 | 2386.64 | 5.21 | 42.08 | 2.15 | 3.37 | 47.3 | 2510 | 33.85 | 18.5 | 33.6802 | -118.0077 | 85.52
DMA 167 | Metal Loss | Ext | 5480.85 | 19.83 | 0.28 | 35000 | ERW | 8.625 | 715 | 66.0485 | 0.185 | 0.888 | 0.733 | 12:27 | 2623 | 0.3786 | 66 | 0.89 | 2491 | AGM 2 | 532.56 | Valve 607 | 2381.78 | 10.08 | 37.22 | 2.15 | 3.37 | 47.3 | 2510 | 33.85 | 18.5 | 33.6802 | -118.0077 | 85.501
DMA 168 | Metal Loss | Ext | 5500.68 | 4.07 | 0.28 | 35000 | ERW | 8.625 | 715 | 21.4668 | 0.06 | 1.479 | 1.124 | 9:08 | 2796 | 0.35517 | 21 | 1.48 | 2770 | AGM 2 | 552.4 | Valve 607 | 2361.94 | 29.91 | 17.39 | 2.15 | 3.37 | 47.3 | 2510 | 33.85 | 18.5 | 33.6802 | -118.0077 | 85.849
CLS 23 | Cluster | Ext | 5504.76 | 13.31 | 0.28 | 35000 | ERW | 8.625 | 715 | 55.789 | 0.156 | 2.814 | 5.697 | 2:44 | 2113 | 0.46997 | 50 | 2.81 | 2049 | AGM 2 | 556.47 | Valve 607 | 2357.87 | 33.98 | 13.31 | 2.15 | 3.37 | 47.3 | 2510 | 33.85 | 18.5 | 33.6801 | -118.0076 | 85.94 | CLS C
GWD 2520 | Girth Weld |  | 5518.07 | 0.35 | 0.28 | 35000 | ERW | 8.625 | 715 | [10 empty] | AGM 2 | 569.78 | Valve 607 | 2344.56 | 47.3 | 33.85 | 3.37 | 47.3 | 33.85 | 2520 | 18.5 | 40.78 | 33.6801 | -118.0076 | 86.244
DMA 172 | Metal Loss | Ext | 5518.42 | 6.51 | 0.28 | 35000 | ERW | 8.625 | 715 | 18.1419 | 0.051 | 0.683 | 0.671 | 2:55 | 2892 | 0.34338 | 18 | 0.68 | 2886 | AGM 2 | 570.14 | Valve 607 | 2344.2 | 0.35 | 33.49 | 3.37 | 47.3 | 33.85 | 2520 | 18.5 | 40.78 | 33.6801 | -118.0076 | 86.256
DMA 173 | Metal Loss | Ext | 5524.93 | 6.2 | 0.28 | 35000 | ERW | 8.625 | 715 | 12.259 | 0.034 | 1.074 | 0.918 | 12:44 | 2881 | 0.34469 | 12 | 1.07 | 2873 | AGM 2 | 576.64 | Valve 607 | 2337.7 | 6.86 | 26.99 | 3.37 | 47.3 | 33.85 | 2520 | 18.5 | 40.78 | 33.6801 | -118.0076 | 86.486
DMA 174 | Metal Loss | Ext | 5531.13 | 15.4 | 0.28 | 35000 | ERW | 8.625 | 715 | 12.6169 | 0.035 | 1.356 | 2.542 | 3:38 | 2861 | 0.3471 | 13 | 1.36 | 2849 | AGM 2 | 582.85 | Valve 607 | 2331.49 | 13.06 | 20.78 | 3.37 | 47.3 | 33.85 | 2520 | 18.5 | 40.78 | 33.6801 | -118.0076 | 86.756
CLS 24 | Cluster | Ext | 5546.53 | 0.27 | 0.28 | 35000 | ERW | 8.625 | 715 | 19.9107 | 0.056 | 2.468 | 1.087 | 12:09 | 2714 | 0.3659 | 10 | 2.47 | 2801 | AGM 2 | 598.24 | Valve 607 | 2316.09 | 28.46 | 5.38 | 3.37 | 47.3 | 33.85 | 2520 | 18.5 | 40.78 | 33.6801 | -118.0075 | 87.347 | CLS C
DMA 177 | Metal Loss | Ext | 5546.8 | 0.75 | 0.28 | 35000 | ERW | 8.625 | 715 | 10.3441 | 0.029 | 0.798 | 0.751 | 12:11 | 2901 | 0.34231 | 10 | 0.8 | 2897 | AGM 2 | 598.51 | Valve 607 | 2315.83 | 28.73 | 5.12 | 3.37 | 47.3 | 33.85 | 2520 | 18.5 | 40.78 | 33.6801 | -118.0075 | 87.354
DMA 178 | Metal Loss | Ext | 5547.55 | 0.37 | 0.28 | 35000 | ERW | 8.625 | 715 | 17.5439 | 0.049 | 0.622 | 0.625 | 11:26 | 2898 | 0.34267 | 18 | 0.62 | 2893 | AGM 2 | 599.26 | Valve 607 | 2315.08 | 29.48 | 4.37 | 3.37 | 47.3 | 33.85 | 2520 | 18.5 | 40.78 | 33.6801 | -118.0075 | 87.376
DMA 179 | Metal Loss | Ext | 5547.92 | 0.17 | 0.28 | 35000 | ERW | 8.625 | 715 | 11.7611 | 0.033 | 0.315 | 0.512 | 11:28 | 2918 | 0.34032 | 12 | 0.31 | 2917 | AGM 2 | 599.63 | Valve 607 | 2314.71 | 29.85 | 4 | 3.37 | 47.3 | 33.85 | 2520 | 18.5 | 40.78 | 33.6801 | -118.0075 | 87.384
CLS 25 | Cluster | Ext | 5548.09 | 0.07 | 0.28 | 35000 | ERW | 8.625 | 715 | 12.237 | 0.034 | 1.476 | 1.465 | 11:27 | 2855 | 0.34783 | 9 | 1.48 | 2867 | AGM 2 | 599.8 | Valve 607 | 2314.53 | 30.02 | 3.82 | 3.37 | 47.3 | 33.85 | 2520 | 18.5 | 40.78 | 33.6801 | -118.0075 | 87.388 | CLS C
CLS 26 | Cluster | Ext | 5548.16 | 0.27 | 0.28 | 35000 | ERW | 8.625 | 715 | 13.6285 | 0.038 | 2.098 | 2.384 | 12:59 | 2806 | 0.3539 | 12 | 2.1 | 2798 | AGM 2 | 599.87 | Valve 607 | 2314.47 | 30.09 | 3.76 | 3.37 | 47.3 | 33.85 | 2520 | 18.5 | 40.78 | 33.6801 | -118.0075 | 87.389 | CLS C
CLS 27 | Cluster | Ext | 5548.42 | 0.21 | 0.28 | 35000 | ERW | 8.625 | 715 | 16.3381 | 0.046 | 1.341 | 3.221 | 12:11 | 2842 | 0.34942 | 16 | 1.34 | 2826 | AGM 2 | 600.14 | Valve 607 | 2314.2 | 30.35 | 3.49 | 3.37 | 47.3 | 33.85 | 2520 | 18.5 | 40.78 | 33.6801 | -118.0075 | 87.395 | CLS C
DMA 186 | Metal Loss | Ext | 5548.63 | 0.11 | 0.28 | 35000 | ERW | 8.625 | 715 | 14.4149 | 0.04 | 0.819 | 0.689 | 11:28 | 2891 | 0.3435 | 14 | 0.82 | 2884 | AGM 2 | 600.35 | Valve 607 | 2313.99 | 30.56 | 3.28 | 3.37 | 47.3 | 33.85 | 2520 | 18.5 | 40.78 | 33.6801 | -118.0075 | 87.399
CLS 28 | Cluster | Ext | 5548.75 | 0.15 | 0.28 | 35000 | ERW | 8.625 | 715 | 14.6398 | 0.041 | 2.226 | 2.788 | 12:51 | 2788 | 0.35619 | 10 | 2.23 | 2818 | AGM 2 | 600.46 | Valve 607 | 2313.88 | 30.68 | 3.17 | 3.37 | 47.3 | 33.85 | 2520 | 18.5 | 40.78 | 33.6801 | -118.0075 | 87.402 | CLS C
DMA 189 | Metal Loss | Ext | 5548.9 | 0.14 | 0.28 | 35000 | ERW | 8.625 | 715 | 10.7668 | 0.03 | 0.918 | 0.68 | 10:40 | 2894 | 0.34314 | 11 | 0.92 | 2889 | AGM 2 | 600.61 | Valve 607 | 2313.73 | 30.82 | 3.02 | 3.37 | 47.3 | 33.85 | 2520 | 18.5 | 40.78 | 33.6801 | -118.0075 | 87.406
DMA 190 | Metal Loss | Ext | 5549.04 | 0.1 | 0.28 | 35000 | ERW | 8.625 | 715 | 20.5308 | 0.057 | 0.94 | 0.686 | 1:25 | 2862 | 0.34698 | 21 | 0.94 | 2850 | AGM 2 | 600.75 | Valve 607 | 2313.59 | 30.97 | 2.88 | 3.37 | 47.3 | 33.85 | 2520 | 18.5 | 40.78 | 33.6801 | -118.0075 | 87.406
DMA 191 | Metal Loss | Ext | 5549.14 | 0.2 | 0.28 | 35000 | ERW | 8.625 | 715 | 13.8493 | 0.039 | 1.083 | 0.774 | 11:16 | 2874 | 0.34553 | 14 | 1.08 | 2865 | AGM 2 | 600.85 | Valve 607 | 2313.49 | 31.07 | 2.78 | 3.37 | 47.3 | 33.85 | 2520 | 18.5 | 40.78 | 33.6801 | -118.0075 | 87.409
CLS 29 | Cluster | Ext | 5549.34 | 0.25 | 0.28 | 35000 | ERW | 8.625 | 715 | 16.4592 | 0.046 | 0.911 | 2.067 | 11:07 | 2878 | 0.34505 | 16 | 0.91 | 2872 | AGM 2 | 601.05 | Valve 607 | 2313.29 | 31.27 | 2.58 | 3.37 | 47.3 | 33.85 | 2520 | 18.5 | 40.78 | 33.6801 | -118.0075 | 87.415 | CLS C
CLS 30 | Cluster | Ext | 5549.59 | 0.3 | 0.28 | 35000 | ERW | 8.625 | 715 | 26.0552 | 0.073 | 2.359 | 3.554 | 12:13 | 2651 | 0.3746 | 22 | 2.36 | 2649 | AGM 2 | 601.3 | Valve 607 | 2313.04 | 31.52 | 2.33 | 3.37 | 47.3 | 33.85 | 2520 | 18.5 | 40.78 | 33.6801 | -118.0075 | 87.419 | CLS C
DMA 197 | Metal Loss | Ext | 5549.89 | 0.59 | 0.28 | 35000 | ERW | 8.625 | 715 | 13.9269 | 0.039 | 0.655 | 0.635 | 1:36 | 2902 | 0.3422 | 14 | 0.65 | 2898 | AGM 2 | 601.61 | Valve 607 | 2312.73 | 31.82 | 2.02 | 3.37 | 47.3 | 33.85 | 2520 | 18.5 | 40.78 | 33.6801 | -118.0075 | 87.428
DMA 198 | Metal Loss | Ext | 5550.48 | 0.14 | 0.28 | 35000 | ERW | 8.625 | 715 | 28.3801 | 0.079 | 0.974 | 0.555 | 1:42 | 2828 | 0.35115 | 28 | 0.97 | 2806 | AGM 2 | 602.2 | Valve 607 | 2312.14 | 32.41 | 1.43 | 3.37 | 47.3 | 33.85 | 2520 | 18.5 | 40.78 | 33.6801 | -118.0075 | 87.441
CLS 31 | Cluster | Ext | 5550.62 | 0.23 | 0.28 | 35000 | ERW | 8.625 | 715 | 32.9975 | 0.092 | 2.231 | 3.196 | 11:56 | 2582 | 0.38461 | 25 | 2.23 | 2629 | AGM 2 | 602.33 | Valve 607 | 2312.01 | 32.55 | 1.3 | 3.37 | 47.3 | 33.85 | 2520 | 18.5 | 40.78 | 33.6801 | -118.0075 | 87.445 | CLS C
DMA 202 | Metal Loss | Ext | 5550.85 | 0.02 | 0.28 | 35000 | ERW | 8.625 | 715 | 27.4479 | 0.077 | 0.582 | 0.539 | 12:34 | 2885 | 0.34421 | 27 | 0.58 | 2877 | AGM 2 | 602.56 | Valve 607 | 2311.78 | 32.78 | 1.07 | 3.37 | 47.3 | 33.85 | 2520 | 18.5 | 40.78 | 33.6801 | -118.0075 | 87.451
DMA 203 | Metal Loss | Ext | 5550.87 | 0.61 | 0.28 | 35000 | ERW | 8.625 | 715 | 13.4615 | 0.038 | 0.852 | 0.694 | 11:18 | 2891 | 0.3435 | 13 | 0.85 | 2885 | AGM 2 | 602.58 | Valve 607 | 2311.76 | 32.8 | 1.04 | 3.37 | 47.3 | 33.85 | 2520 | 18.5 | 40.78 | 33.6801 | -118.0075 | 87.451
CLS 32 | Cluster | Ext | 5551.48 | 0.44 | 0.28 | 35000 | ERW | 8.625 | 715 | 30.461 | 0.085 | 2.053 | 2.682 | 12:11 | 2638 | 0.37644 | 19 | 2.05 | 2721 | AGM 2 | 603.19 | Valve 607 | 2311.15 | 33.41 | 0.44 | 3.37 | 47.3 | 33.85 | 2520 | 18.5 | 40.78 | 33.6801 | -118.0075 | 87.464 | CLS C
GWD 2530 | Girth Weld |  | 5551.92 | 18.5 | 0.219 | 35000 | ERW | 8.625 | 715 | [10 empty] | AGM 2 | 603.63 | Valve 607 | 2310.71 | 33.85 | 18.5 | 47.3 | 33.85 | 18.5 | 2530 | 40.78 | 40.82 | 33.6801 | -118.0075 | 87.474
GWD 2540 | Girth Weld |  | 5570.42 | 40.78 | 0.219 | 35000 | ERW | 8.625 | 715 | [10 empty] | AGM 2 | 622.13 | Valve 607 | 2292.21 | 18.5 | 40.78 | 33.85 | 18.5 | 40.78 | 2540 | 40.82 | 9.35 | 33.6801 | -118.0074 | 87.77
GWD 2550 | Girth Weld |  | 5611.2 | 40.82 | 0.219 | 35000 | ERW | 8.625 | 715 | [10 empty] | AGM 2 | 662.91 | Valve 607 | 2251.42 | 40.78 | 40.82 | 18.5 | 40.78 | 40.82 | 2550 | 9.35 | 1.04 | 33.6801 | -118.0073 | 88.404
GWD 2560 | Girth Weld |  | 5652.03 | 9.35 | 0.219 | 35000 | ERW | 8.625 | 715 | [10 empty] | AGM 2 | 703.74 | Valve 607 | 2210.6 | 40.82 | 9.35 | 40.78 | 40.82 | 9.35 | 2560 | 1.04 | 3.31 | 33.6801 | -118.0072 | 88.579
GWD 2570 | Girth Weld |  | 5661.37 | 1.04 | 0.219 | 35000 | ERW | 8.625 | 715 | [10 empty] | AGM 2 | 713.09 | Valve 607 | 2201.25 | 9.35 | 1.04 | 40.82 | 9.35 | 1.04 | 2570 | 3.31 | 9.59 | 33.6801 | -118.0072 | 88.539
GWD 2580 | Girth Weld |  | 5662.41 | 1.93 | 0.219 | 35000 | ERW | 8.625 | 715 | [10 empty] | AGM 2 | 714.13 | Valve 607 | 2200.21 | 1.04 | 3.31 | 9.35 | 1.04 | 3.31 | 2580 | 9.59 | 40.59 | 33.6801 | -118.0072 | 88.459
BND 42 | Bend |  | 5664.34 | 1.38 | 0.219 | 35000 | ERW | 8.625 | 715 |  |  | 38.372 | [7 empty] | AGM 2 | 716.06 | Valve 607 | 2198.28 | 1.93 | 1.38 | 9.35 | 1.04 | 3.31 | 2580 | 9.59 | 40.59 | 33.6801 | -118.0072 | 88.369 | 3.0D 88.5 deg left turn sag bend
GWD 2590 | Girth Weld |  | 5665.73 | 9.59 | 0.219 | 35000 | ERW | 8.625 | 715 | [10 empty] | AGM 2 | 717.44 | Valve 607 | 2196.9 | 3.31 | 9.59 | 1.04 | 3.31 | 9.59 | 2590 | 40.59 | 15.33 | 33.6802 | -118.0071 | 88.328
GWD 2600 | Girth Weld |  | 5675.32 | 40.59 | 0.219 | 35000 | ERW | 8.625 | 715 | [10 empty] | AGM 2 | 727.03 | Valve 607 | 2187.31 | 9.59 | 40.59 | 3.31 | 9.59 | 40.59 | 2600 | 15.33 | 40.98 | 33.6802 | -118.0071 | 88.114
GWD 2610 | Girth Weld |  | 5715.91 | 15.33 | 0.219 | 35000 | ERW | 8.625 | 715 | [10 empty] | AGM 2 | 767.62 | Valve 607 | 2146.72 | 40.59 | 15.33 | 9.59 | 40.59 | 15.33 | 2610 | 40.98 | 1.6 | 33.6803 | -118.0071 | 86.977
GWD 2620 | Girth Weld |  | 5731.24 | 29.12 | 0.219 | 35000 | ERW | 8.625 | 715 | [10 empty] | AGM 2 | 782.96 | Valve 607 | 2131.38 | 15.33 | 40.98 | 40.59 | 15.33 | 40.98 | 2620 | 1.6 | 17.13 | 33.6803 | -118.0071 | 86.308
DMA 206 | Metal Loss | Ext | 5760.36 | 11.86 | 0.219 | 35000 | ERW | 8.625 | 715 | 23.5178 | 0.052 | 0.882 | 1.201 | 8:56 | 2225 | 0.44632 | 24 | 0.88 | 2212 | AGM 2 | 812.07 | Valve 607 | 2102.27 | 29.12 | 11.86 | 40.59 | 15.33 | 40.98 | 2620 | 1.6 | 17.13 | 33.6804 | -118.0071 | 85.44
GWD 2630 | Girth Weld |  | 5772.22 | 0.82 | 0.219 | 35000 | ERW | 8.625 | 715 | [10 empty] | AGM 2 | 823.93 | Valve 607 | 2090.41 | 40.98 | 1.6 | 15.33 | 40.98 | 1.6 | 2630 | 17.13 | 1.53 | 33.6805 | -118.0071 | 85.354
BND 43 | Bend |  | 5773.04 | 0.79 | 0.219 | 35000 | ERW | 8.625 | 715 |  |  | 25.097 | [7 empty] | AGM 2 | 824.75 | Valve 607 | 2089.59 | 0.82 | 0.78 | 15.33 | 40.98 | 1.6 | 2630 | 17.13 | 1.53 | 33.6805 | -118.0071 | 85.362 | 3.0D 46.8 deg right turn bend
GWD 2640 | Girth Weld |  | 5773.82 | 17.12 | 0.219 | 35000 | ERW | 8.625 | 715 | [10 empty] | AGM 2 | 825.54 | Valve 607 | 2088.8 | 1.6 | 17.13 | 40.98 | 1.6 | 17.13 | 2640 | 1.53 | 24.63 | 33.6805 | -118.0071 | 85.366
GWD 2650 | Girth Weld |  | 5790.95 | 0.73 | 0.219 | 35000 | ERW | 8.625 | 715 | [10 empty] | AGM 2 | 842.66 | Valve 607 | 2071.68 | 17.13 | 1.53 | 1.6 | 17.13 | 1.53 | 2650 | 24.63 | 40.78 | 33.6805 | -118.007 | 85.339
BND 44 | Bend |  | 5791.68 | 0.8 | 0.219 | 35000 | ERW | 8.625 | 715 |  |  | 24.832 | [7 empty] | AGM 2 | 843.39 | Valve 607 | 2070.95 | 0.73 | 0.8 | 1.6 | 17.13 | 1.53 | 2650 | 24.63 | 40.78 | 33.6805 | -118.007 | 85.34 | 3.0D 46.1 deg right turn bend
GWD 2660 | Girth Weld |  | 5792.48 | 24.64 | 0.219 | 35000 | ERW | 8.625 | 715 | [10 empty] | AGM 2 | 844.19 | Valve 607 | 2070.15 | 1.53 | 24.63 | 17.13 | 1.53 | 24.63 | 2660 | 40.78 | 40.84 | 33.6805 | -118.007 | 85.346
GWD 2670 | Girth Weld |  | 5817.11 | 40.78 | 0.219 | 35000 | ERW | 8.625 | 715 | [10 empty] | AGM 2 | 868.82 | Valve 607 | 2045.51 | 24.63 | 40.78 | 1.53 | 24.63 | 40.78 | 2670 | 40.84 | 40.57 | 33.6805 | -118.0069 | 85.612
GWD 2680 | Girth Weld |  | 5857.89 | 40.84 | 0.219 | 35000 | ERW | 8.625 | 715 | [10 empty] | AGM 2 | 909.6 | Valve 607 | 2004.74 | 40.78 | 40.84 | 24.63 | 40.78 | 40.84 | 2680 | 40.57 | 40.83 | 33.6805 | -118.0068 | 85.988
GWD 2690 | Girth Weld |  | 5898.73 | 40.57 | 0.219 | 35000 | ERW | 8.625 | 715 | [10 empty] | AGM 2 | 950.44 | Valve 607 | 1963.9 | 40.84 | 40.57 | 40.78 | 40.84 | 40.57 | 2690 | 40.83 | 40.83 | 33.6805 | -118.0067 | 85.978
GWD 2700 | Girth Weld |  | 5939.3 | 40.83 | 0.219 | 35000 | ERW | 8.625 | 715 | [10 empty] | AGM 2 | 991.01 | Valve 607 | 1923.33 | 40.57 | 40.83 | 40.84 | 40.57 | 40.83 | 2700 | 40.83 | 0.46 | 33.6805 | -118.0065 | 85.946
GWD 2710 | Girth Weld |  | 5980.13 | 40.83 | 0.219 | 35000 | ERW | 8.625 | 715 | [10 empty] | AGM 2 | 1031.84 | Valve 607 | 1882.5 | 40.83 | 40.83 | 40.57 | 40.83 | 40.83 | 2710 | 0.46 | 16.05 | 33.6805 | -118.0064 | 86.17
GWD 2720 | Girth Weld |  | 6020.96 | 0.19 | 0.219 | 35000 | ERW | 8.625 | 715 | [10 empty] | AGM 2 | 1072.67 | Valve 607 | 1841.66 | 40.83 | 0.46 | 40.83 | 40.83 | 0.46 | 2720 | 16.05 | 3.31 | 33.6805 | -118.0063 | 85.856
BND 45 | Bend |  | 6021.15 | 0.27 | 0.219 | 35000 | ERW | 8.625 | 715 |  |  | 23.304 | [7 empty] | AGM 2 | 1072.87 | Valve 607 | 1841.47 | 0.19 | 0.27 | 40.83 | 40.83 | 0.46 | 2720 | 16.05 | 3.31 | 33.6805 | -118.0063 | 85.867 | 12.3D 12.4 deg sag bend
GWD 2730 | Girth Weld |  | 6021.42 | 16.05 | 0.219 | 35000 | ERW | 8.625 | 715 | [10 empty] | AGM 2 | 1073.14 | Valve 607 | 1841.2 | 0.46 | 16.05 | 40.83 | 0.46 | 16.05 | 2730 | 3.31 | 1.77 | 33.6805 | -118.0063 | 85.891
GWD 2740 | Girth Weld |  | 6037.47 | 2.02 | 0.219 | 35000 | ERW | 8.625 | 715 | [10 empty] | AGM 2 | 1089.19 | Valve 607 | 1825.15 | 16.05 | 3.31 | 0.46 | 16.05 | 3.31 | 2740 | 1.77 | 15.68 | 33.6805 | -118.0062 | 88.925
BND 46 | Bend |  | 6039.49 | 1.29 | 0.219 | 35000 | ERW | 8.625 | 715 |  |  | 38.709 | [7 empty] | AGM 2 | 1091.21 | Valve 607 | 1823.13 | 2.02 | 1.29 | 0.46 | 16.05 | 3.31 | 2740 | 1.77 | 15.68 | 33.6805 | -118.0062 | 89.361 | 3.0D 87.2 deg left turn over bend
GWD 2750 | Girth Weld |  | 6040.79 | 1.77 | 0.219 | 35000 | ERW | 8.625 | 715 | [10 empty] | AGM 2 | 1092.5 | Valve 607 | 1821.84 | 3.31 | 1.77 | 16.05 | 3.31 | 1.77 | 2750 | 15.68 | 38.85 | 33.6805 | -118.0062 | 89.571
GWD 2760 | Girth Weld |  | 6042.55 | 10.05 | 0.28 | 35000 | ERW | 8.625 | 715 | [10 empty] | AGM 2 | 1094.27 | Valve 607 | 1820.07 | 1.77 | 15.68 | 3.31 | 1.77 | 15.68 | 2760 | 38.85 | 36.44 | 33.6805 | -118.0062 | 89.716
DMA 207 | Metal Loss | Ext | 6052.6 | 5.63 | 0.28 | 35000 | ERW | 8.625 | 715 | 44.5316 | 0.125 | 1.319 | 0.714 | 5:53 | 2648 | 0.37502 | 45 | 1.32 | 2572 | AGM 2 | 1104.32 | Valve 607 | 1810.02 | 10.05 | 5.63 | 3.31 | 1.77 | 15.68 | 2760 | 38.85 | 36.44 | 33.6805 | -118.0062 | 90.356
GWD 2770 | Girth Weld |  | 6058.23 | 4.03 | 0.28 | 35000 | ERW | 8.625 | 715 | [10 empty] | AGM 2 | 1109.95 | Valve 607 | 1804.39 | 15.68 | 38.85 | 1.77 | 15.68 | 38.85 | 2770 | 36.44 | 47.39 | 33.6806 | -118.0062 | 90.657
DMA 208 | Metal Loss | Ext | 6062.26 | 0.46 | 0.28 | 35000 | ERW | 8.625 | 715 | 25.5348 | 0.071 | 0.793 | 0.694 | 8:03 | 2864 | 0.34674 | 26 | 0.79 | 2851 | AGM 2 | 1113.97 | Valve 607 | 1800.37 | 4.03 | 34.82 | 1.77 | 15.68 | 38.85 | 2770 | 36.44 | 47.39 | 33.6806 | -118.0062 | 90.85
DMA 209 | Metal Loss | Ext | 6062.72 | 0.45 | 0.28 | 35000 | ERW | 8.625 | 715 | 24.3097 | 0.068 | 1.099 | 1.123 | 8:40 | 2828 | 0.35115 | 24 | 1.1 | 2807 | AGM 2 | 1114.43 | Valve 607 | 1799.91 | 4.49 | 34.36 | 1.77 | 15.68 | 38.85 | 2770 | 36.44 | 47.39 | 33.6806 | -118.0062 | 90.87
PAH 2 | Patch |  | 6063.18 | 0.38 | 0.28 | 35000 | ERW | 8.625 | 715 |  |  |  |  | 6:25 | [5 empty] | AGM 2 | 1114.89 | Valve 607 | 1799.45 | 4.94 | 33.9 | 1.77 | 15.68 | 38.85 | 2770 | 36.44 | 47.39 | 33.6806 | -118.0062 | 90.892
DMA 210 | Metal Loss | Ext | 6063.55 | 0.26 | 0.28 | 35000 | ERW | 8.625 | 715 | 18.2841 | 0.051 | 0.734 | 0.815 | 8:07 | 2888 | 0.34386 | 18 | 0.73 | 2881 | AGM 2 | 1115.27 | Valve 607 | 1799.07 | 5.32 | 33.52 | 1.77 | 15.68 | 38.85 | 2770 | 36.44 | 47.39 | 33.6806 | -118.0062 | 90.907
CLS 33 | Cluster | Ext | 6063.81 | 0.25 | 0.28 | 35000 | ERW | 8.625 | 715 | 47.0764 | 0.132 | 2.306 | 2.937 | 7:36 | 2369 | 0.41919 | 30 | 2.31 | 2544 | AGM 2 | 1115.52 | Valve 607 | 1798.82 | 5.58 | 33.27 | 1.77 | 15.68 | 38.85 | 2770 | 36.44 | 47.39 | 33.6806 | -118.0062 | 90.917 | CLS C
DMA 214 | Metal Loss | Ext | 6064.06 | 0.23 | 0.28 | 35000 | ERW | 8.625 | 715 | 16.4053 | 0.046 | 0.772 | 0.777 | 7:51 | 2889 | 0.34374 | 16 | 0.77 | 2882 | AGM 2 | 1115.77 | Valve 607 | 1798.57 | 5.83 | 33.02 | 1.77 | 15.68 | 38.85 | 2770 | 36.44 | 47.39 | 33.6806 | -118.0062 | 90.924
DMA 215 | Metal Loss | Ext | 6064.29 | 0.47 | 0.28 | 35000 | ERW | 8.625 | 715 | 19.3672 | 0.054 | 0.472 | 0.592 | 7:06 | 2906 | 0.34173 | 19 | 0.47 | 2902 | AGM 2 | 1116 | Valve 607 | 1798.34 | 6.06 | 32.79 | 1.77 | 15.68 | 38.85 | 2770 | 36.44 | 47.39 | 33.6806 | -118.0062 | 90.934
DMA 216 | Metal Loss | Ext | 6064.76 | 0.7 | 0.28 | 35000 | ERW | 8.625 | 715 | 35.5507 | 0.1 | 0.643 | 0.786 | 8:14 | 2860 | 0.34722 | 36 | 0.64 | 2844 | AGM 2 | 1116.47 | Valve 607 | 1797.86 | 6.53 | 32.32 | 1.77 | 15.68 | 38.85 | 2770 | 36.44 | 47.39 | 33.6806 | -118.0062 | 90.957
DMA 217 | Metal Loss | Ext | 6065.47 | 0.18 | 0.28 | 35000 | ERW | 8.625 | 715 | 13.2173 | 0.037 | 0.864 | 0.953 | 8:17 | 2891 | 0.3435 | 13 | 0.86 | 2884 | AGM 2 | 1117.18 | Valve 607 | 1797.16 | 7.23 | 31.61 | 1.77 | 15.68 | 38.85 | 2770 | 36.44 | 47.39 | 33.6806 | -118.0062 | 90.983
DMA 218 | Metal Loss | Ext | 6065.64 | 31.44 | 0.28 | 35000 | ERW | 8.625 | 715 | 25.1294 | 0.07 | 0.692 | 0.602 | 9:49 | 2877 | 0.34517 | 25 | 0.69 | 2867 | AGM 2 | 1117.35 | Valve 607 | 1796.98 | 7.41 | 31.44 | 1.77 | 15.68 | 38.85 | 2770 | 36.44 | 47.39 | 33.6806 | -118.0062 | 90.989
GWD 2780 | Girth Weld |  | 6097.08 | 19.96 | 0.28 | 35000 | ERW | 8.625 | 715 | [10 empty] | AGM 2 | 1148.79 | Valve 607 | 1765.55 | 38.85 | 36.44 | 15.68 | 38.85 | 36.44 | 2780 | 47.39 | 47.17 | 33.6807 | -118.0062 | 91.979
DMA 219 | Metal Loss | Ext | 6117.04 | 3.62 | 0.28 | 35000 | ERW | 8.625 | 715 | 10.5677 | 0.03 | 1.304 | 0.848 | 1:52 | 2874 | 0.34553 | 11 | 1.3 | 2865 | AGM 2 | 1168.75 | Valve 607 | 1745.58 | 19.96 | 16.48 | 15.68 | 38.85 | 36.44 | 2780 | 47.39 | 47.17 | 33.6807 | -118.0062 | 92.428
DMA 220 | Metal Loss | Ext | 6120.66 | 0.34 | 0.28 | 35000 | ERW | 8.625 | 715 | 22.3262 | 0.063 | 0.857 | 0.687 | 7:45 | 2866 | 0.3465 | 22 | 0.86 | 2853 | AGM 2 | 1172.37 | Valve 607 | 1741.96 | 23.58 | 12.86 | 15.68 | 38.85 | 36.44 | 2780 | 47.39 | 47.17 | 33.6807 | -118.0062 | 92.518
CLS 34 | Cluster | Ext | 6121 | 1.38 | 0.28 | 35000 | ERW | 8.625 | 715 | 18.4348 | 0.052 | 3.071 | 0.872 | 6:36 | 2693 | 0.36875 | 12 | 3.07 | 2750 | AGM 2 | 1172.71 | Valve 607 | 1741.63 | 23.92 | 12.53 | 15.68 | 38.85 | 36.44 | 2780 | 47.39 | 47.17 | 33.6807 | -118.0062 | 92.526 | CLS C
DMA 223 | Metal Loss | Ext | 6122.38 | 11.15 | 0.28 | 35000 | ERW | 8.625 | 715 | 14.7772 | 0.041 | 1.699 | 0.77 | 5:46 | 2823 | 0.35177 | 15 | 1.7 | 2804 | AGM 2 | 1174.09 | Valve 607 | 1740.25 | 25.3 | 11.15 | 15.68 | 38.85 | 36.44 | 2780 | 47.39 | 47.17 | 33.6807 | -118.0062 | 92.563
GWD 2790 | Girth Weld |  | 6133.52 | 47.39 | 0.28 | 35000 | ERW | 8.625 | 715 | [10 empty] | AGM 2 | 1185.24 | Valve 607 | 1729.1 | 36.44 | 47.39 | 38.85 | 36.44 | 47.39 | 2790 | 47.17 | 47.48 | 33.6808 | -118.0062 | 92.882
GWD 2800 | Girth Weld |  | 6180.91 | 22.13 | 0.28 | 35000 | ERW | 8.625 | 715 | [10 empty] | AGM 2 | 1232.63 | Valve 607 | 1681.71 | 47.39 | 47.17 | 36.44 | 47.39 | 47.17 | 2800 | 47.48 | 47.39 | 33.6809 | -118.0062 | 93.762
DMA 224 | Metal Loss | Ext | 6203.04 | 0.25 | 0.28 | 35000 | ERW | 8.625 | 715 | 14.4566 | 0.04 | 2.182 | 1.776 | 6:11 | 2793 | 0.35555 | 14 | 2.18 | 2768 | AGM 2 | 1254.75 | Valve 607 | 1659.59 | 22.13 | 25.04 | 36.44 | 47.39 | 47.17 | 2800 | 47.48 | 47.39 | 33.681 | -118.0062 | 94.604
DMA 225 | Metal Loss | Ext | 6203.29 | 0.96 | 0.28 | 35000 | ERW | 8.625 | 715 | 14.1298 | 0.04 | 0.661 | 0.749 | 6:48 | 2901 | 0.34231 | 14 | 0.66 | 2897 | AGM 2 | 1255 | Valve 607 | 1659.34 | 22.38 | 24.79 | 36.44 | 47.39 | 47.17 | 2800 | 47.48 | 47.39 | 33.681 | -118.0062 | 94.616
DMA 226 | Metal Loss | Ext | 6204.25 | 2.78 | 0.28 | 35000 | ERW | 8.625 | 715 | 13.0382 | 0.037 | 0.992 | 1.057 | 7:43 | 2883 | 0.34445 | 13 | 0.99 | 2875 | AGM 2 | 1255.96 | Valve 607 | 1658.38 | 23.34 | 23.83 | 36.44 | 47.39 | 47.17 | 2800 | 47.48 | 47.39 | 33.681 | -118.0062 | 94.66
DMA 227 | Metal Loss | Ext | 6207.03 | 0.37 | 0.28 | 35000 | ERW | 8.625 | 715 | 11.7781 | 0.033 | 0.412 | 0.555 | 7:45 | 2915 | 0.34067 | 12 | 0.41 | 2913 | AGM 2 | 1258.74 | Valve 607 | 1655.6 | 26.11 | 21.05 | 36.44 | 47.39 | 47.17 | 2800 | 47.48 | 47.39 | 33.681 | -118.0062 | 94.789
CLS 35 | Cluster | Ext | 6207.4 | 1.24 | 0.28 | 35000 | ERW | 8.625 | 715 | 21.0224 | 0.059 | 2.153 | 0.833 | 6:38 | 2729 | 0.36389 | 15 | 2.15 | 2758 | AGM 2 | 1259.11 | Valve 607 | 1655.23 | 26.49 | 20.68 | 36.44 | 47.39 | 47.17 | 2800 | 47.48 | 47.39 | 33.681 | -118.0062 | 94.806 | CLS C
DMA 230 | Metal Loss | Ext | 6208.64 | 1 | 0.28 | 35000 | ERW | 8.625 | 715 | 11.4576 | 0.032 | 1.18 | 1.699 | 7:19 | 2877 | 0.34517 | 11 | 1.18 | 2869 | AGM 2 | 1260.36 | Valve 607 | 1653.98 | 27.73 | 19.44 | 36.44 | 47.39 | 47.17 | 2800 | 47.48 | 47.39 | 33.681 | -118.0062 | 94.863
DMA 231 | Metal Loss | Ext | 6209.64 | 0.69 | 0.28 | 35000 | ERW | 8.625 | 715 | 15.3064 | 0.043 | 1.87 | 2.194 | 6:07 | 2806 | 0.3539 | 15 | 1.87 | 2784 | AGM 2 | 1261.35 | Valve 607 | 1652.98 | 28.73 | 18.44 | 36.44 | 47.39 | 47.17 | 2800 | 47.48 | 47.39 | 33.681 | -118.0062 | 94.907
DMA 232 | Metal Loss | Ext | 6210.33 | 0.09 | 0.28 | 35000 | ERW | 8.625 | 715 | 11.7667 | 0.033 | 0.394 | 0.567 | 7:40 | 2915 | 0.34067 | 12 | 0.39 | 2914 | AGM 2 | 1262.04 | Valve 607 | 1652.29 | 29.42 | 17.75 | 36.44 | 47.39 | 47.17 | 2800 | 47.48 | 47.39 | 33.681 | -118.0062 | 94.941
DMA 233 | Metal Loss | Ext | 6210.42 | 0.64 | 0.28 | 35000 | ERW | 8.625 | 715 | 15.8729 | 0.044 | 0.792 | 0.711 | 5:40 | 2889 | 0.34374 | 16 | 0.79 | 2882 | AGM 2 | 1262.13 | Valve 607 | 1652.21 | 29.5 | 17.67 | 36.44 | 47.39 | 47.17 | 2800 | 47.48 | 47.39 | 33.681 | -118.0062 | 94.945
DMA 234 | Metal Loss | Ext | 6211.05 | 1.7 | 0.28 | 35000 | ERW | 8.625 | 715 | 11.1323 | 0.031 | 0.856 | 0.68 | 6:27 | 2897 | 0.34279 | 11 | 0.86 | 2892 | AGM 2 | 1262.77 | Valve 607 | 1651.57 | 30.14 | 17.03 | 36.44 | 47.39 | 47.17 | 2800 | 47.48 | 47.39 | 33.681 | -118.0062 | 94.974
CLS 36 | Cluster | Ext | 6212.76 | 15.32 | 0.28 | 35000 | ERW | 8.625 | 715 | 20.6117 | 0.058 | 3.511 | 2.067 | 7:26 | 2638 | 0.37644 | 14 | 3.51 | 2692 | AGM 2 | 1264.47 | Valve 607 | 1649.87 | 31.84 | 15.32 | 36.44 | 47.39 | 47.17 | 2800 | 47.48 | 47.39 | 33.681 | -118.0062 | 95.056 | CLS C
GWD 2810 | Girth Weld |  | 6228.08 | 3.49 | 0.28 | 35000 | ERW | 8.625 | 715 | [10 empty] | AGM 2 | 1279.79 | Valve 607 | 1634.54 | 47.17 | 47.48 | 47.39 | 47.17 | 47.48 | 2810 | 47.39 | 45.14 | 33.681 | -118.0062 | 95.757
DMA 238 | Metal Loss | Ext | 6231.58 | 0.22 | 0.28 | 35000 | ERW | 8.625 | 715 | 16.5165 | 0.046 | 0.893 | 0.589 | 5:51 | 2880 | 0.34481 | 17 | 0.89 | 2871 | AGM 2 | 1283.29 | Valve 607 | 1631.05 | 3.49 | 43.98 | 47.39 | 47.17 | 47.48 | 2810 | 47.39 | 45.14 | 33.681 | -118.0062 | 95.89
DMA 239 | Metal Loss | Ext | 6231.8 | 0.22 | 0.28 | 35000 | ERW | 8.625 | 715 | 15.8109 | 0.044 | 0.607 | 0.555 | 6:46 | 2902 | 0.3422 | 16 | 0.61 | 2897 | AGM 2 | 1283.51 | Valve 607 | 1630.83 | 3.71 | 43.76 | 47.39 | 47.17 | 47.48 | 2810 | 47.39 | 45.14 | 33.681 | -118.0062 | 95.898
DMA 240 | Metal Loss | Ext | 6232.01 | 0.36 | 0.28 | 35000 | ERW | 8.625 | 715 | 14.4481 | 0.04 | 0.818 | 0.595 | 6:58 | 2891 | 0.3435 | 14 | 0.82 | 2884 | AGM 2 | 1283.72 | Valve 607 | 1630.61 | 3.93 | 43.55 | 47.39 | 47.17 | 47.48 | 2810 | 47.39 | 45.14 | 33.681 | -118.0062 | 95.903
DMA 241 | Metal Loss | Ext | 6232.38 | 0.03 | 0.28 | 35000 | ERW | 8.625 | 715 | 13.9658 | 0.039 | 0.572 | 0.589 | 6:54 | 2906 | 0.34173 | 14 | 0.57 | 2903 | AGM 2 | 1284.09 | Valve 607 | 1630.25 | 4.3 | 43.18 | 47.39 | 47.17 | 47.48 | 2810 | 47.39 | 45.14 | 33.681 | -118.0062 | 95.918
DMA 242 | Metal Loss | Ext | 6232.41 | 0.18 | 0.28 | 35000 | ERW | 8.625 | 715 | 13.3073 | 0.037 | 0.731 | 0.601 | 5:16 | 2899 | 0.34255 | 13 | 0.73 | 2894 | AGM 2 | 1284.12 | Valve 607 | 1630.21 | 4.33 | 43.15 | 47.39 | 47.17 | 47.48 | 2810 | 47.39 | 45.14 | 33.681 | -118.0062 | 95.919
CLS 37 | Cluster | Ext | 6232.59 | 42.96 | 0.28 | 35000 | ERW | 8.625 | 715 | 17.3768 | 0.049 | 1.05 | 2.579 | 7:30 | 2863 | 0.34686 | 17 | 1.05 | 2855 | AGM 2 | 1284.31 | Valve 607 | 1630.03 | 4.51 | 42.97 | 47.39 | 47.17 | 47.48 | 2810 | 47.39 | 45.14 | 33.681 | -118.0062 | 95.926 | CLS C
GWD 2820 | Girth Weld |  | 6275.56 | 47.39 | 0.28 | 35000 | ERW | 8.625 | 715 | [10 empty] | AGM 2 | 1327.27 | Valve 607 | 1587.07 | 47.48 | 47.39 | 47.17 | 47.48 | 47.39 | 2820 | 45.14 | 47.14 | 33.6811 | -118.0062 | 96.52
GWD 2830 | Girth Weld |  | 6322.94 | 45.14 | 0.28 | 35000 | ERW | 8.625 | 715 | [10 empty] | AGM 2 | 1374.66 | Valve 607 | 1539.68 | 47.39 | 45.14 | 47.48 | 47.39 | 45.14 | 2830 | 47.14 | 48.35 | 33.6813 | -118.0062 | 96.77
GWD 2840 | Girth Weld |  | 6368.08 | 47.14 | 0.28 | 35000 | ERW | 8.625 | 715 | [10 empty] | AGM 2 | 1419.8 | Valve 607 | 1494.54 | 45.14 | 47.14 | 47.39 | 45.14 | 47.14 | 2840 | 48.35 | 46.65 | 33.6814 | -118.0062 | 98.896
GWD 2850 | Girth Weld |  | 6415.22 | 48.35 | 0.28 | 35000 | ERW | 8.625 | 715 | [10 empty] | AGM 2 | 1466.94 | Valve 607 | 1447.4 | 47.14 | 48.35 | 45.14 | 47.14 | 48.35 | 2850 | 46.65 | 46.73 | 33.6815 | -118.0062 | 99.932
GWD 2860 | Girth Weld |  | 6463.57 | 46.65 | 0.28 | 35000 | ERW | 8.625 | 715 | [10 empty] | AGM 2 | 1515.29 | Valve 607 | 1399.05 | 48.35 | 46.65 | 47.14 | 48.35 | 46.65 | 2860 | 46.73 | 47.51 | 33.6817 | -118.0062 | 100.816
GWD 2870 | Girth Weld |  | 6510.22 | 46.73 | 0.28 | 35000 | ERW | 8.625 | 715 | [10 empty] | AGM 2 | 1561.94 | Valve 607 | 1352.4 | 46.65 | 46.73 | 48.35 | 46.65 | 46.73 | 2870 | 47.51 | 46.71 | 33.6818 | -118.0062 | 101.277
GWD 2880 | Girth Weld |  | 6556.95 | 45.01 | 0.28 | 35000 | ERW | 8.625 | 715 | [10 empty] | AGM 2 | 1608.67 | Valve 607 | 1305.67 | 46.73 | 47.51 | 46.65 | 46.73 | 47.51 | 2880 | 46.71 | 45.18 | 33.6819 | -118.0062 | 101.698
PMA 11 | Pipe Mill | Ext | 6601.97 | 0.3 | 0.28 | 35000 | ERW | 8.625 | 715 | 14.8862 | 0.042 | 0.678 | 0.67 | 5:01 | [5 empty] | AGM 2 | 1653.68 | Valve 607 | 1260.66 | 45.01 | 2.5 | 46.65 | 46.73 | 47.51 | 2880 | 46.71 | 45.18 | 33.682 | -118.0062 | 102.149
PMA 12 | Pipe Mill | Ext | 6602.27 | 2.2 | 0.28 | 35000 | ERW | 8.625 | 715 | 11.2323 | 0.031 | 0.867 | 0.923 | 4:39 | [5 empty] | AGM 2 | 1653.98 | Valve 607 | 1260.36 | 45.31 | 2.2 | 46.65 | 46.73 | 47.51 | 2880 | 46.71 | 45.18 | 33.682 | -118.0062 | 102.152
GWD 2890 | Girth Weld |  | 6604.47 | 27.72 | 0.28 | 35000 | ERW | 8.625 | 715 | [10 empty] | AGM 2 | 1656.18 | Valve 607 | 1258.16 | 47.51 | 46.71 | 46.73 | 47.51 | 46.71 | 2890 | 45.18 | 47 | 33.682 | -118.0062 | 102.172
DMA 245 | Metal Loss | Ext | 6632.19 | 18.99 | 0.28 | 35000 | ERW | 8.625 | 715 | 16.2544 | 0.046 | 0.731 | 0.754 | 7:39 | 2893 | 0.34326 | 16 | 0.73 | 2887 | AGM 2 | 1683.9 | Valve 607 | 1230.44 | 27.72 | 18.99 | 46.73 | 47.51 | 46.71 | 2890 | 45.18 | 47 | 33.6821 | -118.0062 | 102.357
GWD 2900 | Girth Weld |  | 6651.17 | 45.18 | 0.28 | 35000 | ERW | 8.625 | 715 | [10 empty] | AGM 2 | 1702.89 | Valve 607 | 1211.45 | 46.71 | 45.18 | 47.51 | 46.71 | 45.18 | 2900 | 47 | 17.41 | 33.6822 | -118.0062 | 102.637
GWD 2910 | Girth Weld |  | 6696.35 | 47 | 0.28 | 35000 | ERW | 8.625 | 715 | [10 empty] | AGM 2 | 1748.06 | Valve 607 | 1166.28 | 45.18 | 47 | 46.71 | 45.18 | 47 | 2910 | 17.41 | 35.89 | 33.6823 | -118.0062 | 103.189
GWD 2920 | Girth Weld |  | 6743.35 | 17.41 | 0.28 | 35000 | ERW | 8.625 | 715 | [10 empty] | AGM 2 | 1795.06 | Valve 607 | 1119.28 | 47 | 17.41 | 45.18 | 47 | 17.41 | 2920 | 35.89 | 46.52 | 33.6824 | -118.0062 | 103.66
GWD 2930 | Girth Weld |  | 6760.76 | 35.89 | 0.28 | 35000 | ERW | 8.625 | 715 | [10 empty] | AGM 2 | 1812.47 | Valve 607 | 1101.87 | 17.41 | 35.89 | 47 | 17.41 | 35.89 | 2930 | 46.52 | 47.29 | 33.6825 | -118.0062 | 103.584
GWD 2940 | Girth Weld |  | 6796.65 | 46.52 | 0.28 | 35000 | ERW | 8.625 | 715 | [10 empty] | AGM 2 | 1848.36 | Valve 607 | 1065.98 | 35.89 | 46.52 | 17.41 | 35.89 | 46.52 | 2940 | 47.29 | 46.27 | 33.6826 | -118.0062 | 102.566
GWD 2950 | Girth Weld |  | 6843.17 | 47.29 | 0.28 | 35000 | ERW | 8.625 | 715 | [10 empty] | AGM 2 | 1894.88 | Valve 607 | 1019.46 | 46.52 | 47.29 | 35.89 | 46.52 | 47.29 | 2950 | 46.27 | 45.18 | 33.6827 | -118.0062 | 102.736
GWD 2960 | Girth Weld |  | 6890.46 | 46.27 | 0.28 | 35000 | ERW | 8.625 | 715 | [10 empty] | AGM 2 | 1942.17 | Valve 607 | 972.17 | 47.29 | 46.27 | 46.52 | 47.29 | 46.27 | 2960 | 45.18 | 47.11 | 33.6828 | -118.0062 | 102.974
GWD 2970 | Girth Weld |  | 6936.72 | 45.18 | 0.28 | 35000 | ERW | 8.625 | 715 | [10 empty] | AGM 2 | 1988.43 | Valve 607 | 925.91 | 46.27 | 45.18 | 47.29 | 46.27 | 45.18 | 2970 | 47.11 | 35.95 | 33.6829 | -118.0062 | 103.001
GWD 2980 | Girth Weld |  | 6981.9 | 20.03 | 0.28 | 35000 | ERW | 8.625 | 715 | [10 empty] | AGM 2 | 2033.62 | Valve 607 | 880.72 | 45.18 | 47.11 | 46.27 | 45.18 | 47.11 | 2980 | 35.95 | 0.36 | 33.6831 | -118.0062 | 102.195
CLS 38 | Cluster | Ext | 7001.94 | 0.81 | 0.28 | 35000 | ERW | 8.625 | 715 | 14.178 | 0.04 | 0.728 | 1.747 | 4:37 | 2897 | 0.34279 | 13 | 0.73 | 2894 | AGM 2 | 2053.65 | Valve 607 | 860.69 | 20.03 | 27.07 | 46.27 | 45.18 | 47.11 | 2980 | 35.95 | 0.36 | 33.6831 | -118.0062 | 101.864 | CLS C
CLS 39 | Cluster | Ext | 7002.75 | 12.94 | 0.28 | 35000 | ERW | 8.625 | 715 | 29.1289 | 0.082 | 1.7 | 4.559 | 6:17 | 2705 | 0.36712 | 28 | 1.7 | 2665 | AGM 2 | 2054.46 | Valve 607 | 859.88 | 20.84 | 26.26 | 46.27 | 45.18 | 47.11 | 2980 | 35.95 | 0.36 | 33.6831 | -118.0062 | 101.847 | CLS C
DMA 250 | Metal Loss | Ext | 7015.69 | 13.32 | 0.28 | 35000 | ERW | 8.625 | 715 | 59.7237 | 0.167 | 0.584 | 0.754 | 2:10 | 2802 | 0.35441 | 60 | 0.58 | 2752 | AGM 2 | 2067.4 | Valve 607 | 846.94 | 33.79 | 13.32 | 46.27 | 45.18 | 47.11 | 2980 | 35.95 | 0.36 | 33.6832 | -118.0062 | 101.388
GWD 2990 | Girth Weld |  | 7029.01 | 0.7 | 0.28 | 35000 | ERW | 8.625 | 715 | [10 empty] | AGM 2 | 2080.72 | Valve 607 | 833.62 | 47.11 | 35.95 | 45.18 | 47.11 | 35.95 | 2990 | 0.36 | 1.29 | 33.6832 | -118.0062 | 100.889
DMA 251 | Metal Loss | Ext | 7029.7 | 0.64 | 0.28 | 35000 | ERW | 8.625 | 715 | 12.5212 | 0.035 | 1.54 | 0.822 | 3:45 | 2850 | 0.34844 | 13 | 1.54 | 2835 | AGM 2 | 2081.42 | Valve 607 | 832.92 | 0.7 | 35.25 | 45.18 | 47.11 | 35.95 | 2990 | 0.36 | 1.29 | 33.6832 | -118.0062 | 100.86
DMA 252 | Metal Loss | Ext | 7030.35 | 0.89 | 0.28 | 35000 | ERW | 8.625 | 715 | 10.5814 | 0.03 | 1.016 | 1.019 | 3:43 | 2890 | 0.34362 | 11 | 1.02 | 2884 | AGM 2 | 2082.06 | Valve 607 | 832.28 | 1.34 | 34.61 | 45.18 | 47.11 | 35.95 | 2990 | 0.36 | 1.29 | 33.6832 | -118.0062 | 100.84
DMA 253 | Metal Loss | Ext | 7031.24 | 11.37 | 0.28 | 35000 | ERW | 8.625 | 715 | 25.7637 | 0.072 | 1.354 | 0.813 | 2:52 | 2784 | 0.3567 | 26 | 1.35 | 2753 | AGM 2 | 2082.95 | Valve 607 | 831.39 | 2.23 | 33.72 | 45.18 | 47.11 | 35.95 | 2990 | 0.36 | 1.29 | 33.6832 | -118.0062 | 100.803
DMA 254 | Metal Loss | Ext | 7042.61 | 3.39 | 0.28 | 35000 | ERW | 8.625 | 715 | 17.9585 | 0.05 | 0.711 | 0.691 | 3:14 | 2891 | 0.3435 | 18 | 0.71 | 2884 | AGM 2 | 2094.33 | Valve 607 | 820.01 | 13.6 | 22.34 | 45.18 | 47.11 | 35.95 | 2990 | 0.36 | 1.29 | 33.6832 | -118.0062 | 100.479
DMA 255 | Metal Loss | Ext | 7046.01 | 0.73 | 0.28 | 35000 | ERW | 8.625 | 715 | 26.4522 | 0.074 | 0.906 | 1.561 | 2:08 | 2846 | 0.34893 | 26 | 0.91 | 2828 | AGM 2 | 2097.72 | Valve 607 | 816.62 | 17 | 18.95 | 45.18 | 47.11 | 35.95 | 2990 | 0.36 | 1.29 | 33.6832 | -118.0062 | 100.42
DMA 256 | Metal Loss | Ext | 7046.74 | 1.12 | 0.28 | 35000 | ERW | 8.625 | 715 | 43.8499 | 0.123 | 2.108 | 1.08 | 11:40 | 2459 | 0.40385 | 44 | 2.11 | 2342 | AGM 2 | 2098.45 | Valve 607 | 815.89 | 17.73 | 18.22 | 45.18 | 47.11 | 35.95 | 2990 | 0.36 | 1.29 | 33.6832 | -118.0062 | 100.409
DMA 257 | Metal Loss | Ext | 7047.86 | 0.35 | 0.28 | 35000 | ERW | 8.625 | 715 | 33.5359 | 0.094 | 0.788 | 1.537 | 10:04 | 2840 | 0.34967 | 34 | 0.79 | 2819 | AGM 2 | 2099.58 | Valve 607 | 814.76 | 18.85 | 17.09 | 45.18 | 47.11 | 35.95 | 2990 | 0.36 | 1.29 | 33.6833 | -118.0062 | 100.395
DMA 258 | Metal Loss | Ext | 7048.22 | 0.22 | 0.28 | 35000 | ERW | 8.625 | 715 | 17.8863 | 0.05 | 0.934 | 0.508 | 11:39 | 2872 | 0.34577 | 18 | 0.93 | 2861 | AGM 2 | 2099.93 | Valve 607 | 814.41 | 19.21 | 16.74 | 45.18 | 47.11 | 35.95 | 2990 | 0.36 | 1.29 | 33.6833 | -118.0062 | 100.389
DMA 259 | Metal Loss | Ext | 7048.43 | 0.44 | 0.28 | 35000 | ERW | 8.625 | 715 | 12.5884 | 0.035 | 0.891 | 0.662 | 11:41 | 2891 | 0.3435 | 13 | 0.89 | 2885 | AGM 2 | 2100.14 | Valve 607 | 814.2 | 19.42 | 16.53 | 45.18 | 47.11 | 35.95 | 2990 | 0.36 | 1.29 | 33.6833 | -118.0062 | 100.388
CLS 40 | Cluster | Ext | 7048.87 | 0.35 | 0.28 | 35000 | ERW | 8.625 | 715 | 28.3281 | 0.079 | 3.11 | 2.736 | 11:15 | 2548 | 0.38974 | 18 | 3.11 | 2651 | AGM 2 | 2100.58 | Valve 607 | 813.76 | 19.86 | 16.09 | 45.18 | 47.11 | 35.95 | 2990 | 0.36 | 1.29 | 33.6833 | -118.0062 | 100.382 | CLS C
DMA 263 | Metal Loss | Ext | 7049.22 | 0.2 | 0.28 | 35000 | ERW | 8.625 | 715 | 14.9016 | 0.042 | 1.498 | 0.813 | 10:37 | 2838 | 0.34991 | 15 | 1.5 | 2821 | AGM 2 | 2100.93 | Valve 607 | 813.41 | 20.21 | 15.74 | 45.18 | 47.11 | 35.95 | 2990 | 0.36 | 1.29 | 33.6833 | -118.0062 | 100.376
DMA 264 | Metal Loss | Ext | 7049.42 | 1.42 | 0.28 | 35000 | ERW | 8.625 | 715 | 25.8624 | 0.072 | 0.948 | 0.531 | 11:39 | 2842 | 0.34942 | 26 | 0.95 | 2824 | AGM 2 | 2101.13 | Valve 607 | 813.21 | 20.41 | 15.54 | 45.18 | 47.11 | 35.95 | 2990 | 0.36 | 1.29 | 33.6833 | -118.0062 | 100.375
CLS 41 | Cluster | Ext | 7050.84 | 1.12 | 0.28 | 35000 | ERW | 8.625 | 715 | 29.7187 | 0.083 | 4.411 | 3.146 | 11:07 | 2439 | 0.40716 | 14 | 4.41 | 2667 | AGM 2 | 2102.55 | Valve 607 | 811.79 | 21.83 | 14.12 | 45.18 | 47.11 | 35.95 | 2990 | 0.36 | 1.29 | 33.6833 | -118.0062 | 100.359 | CLS C
DMA 270 | Metal Loss | Ext | 7051.96 | 0.18 | 0.28 | 35000 | ERW | 8.625 | 715 | 13.9076 | 0.039 | 1.452 | 1.287 | 6:41 | 2847 | 0.34881 | 14 | 1.45 | 2832 | AGM 2 | 2103.67 | Valve 607 | 810.66 | 22.95 | 13 | 45.18 | 47.11 | 35.95 | 2990 | 0.36 | 1.29 | 33.6833 | -118.0062 | 100.346
CLS 42 | Cluster | Ext | 7052.14 | 0.36 | 0.28 | 35000 | ERW | 8.625 | 715 | 22.3733 | 0.063 | 1.224 | 2.011 | 8:04 | 2822 | 0.3519 | 18 | 1.22 | 2828 | AGM 2 | 2103.86 | Valve 607 | 810.48 | 23.13 | 12.81 | 45.18 | 47.11 | 35.95 | 2990 | 0.36 | 1.29 | 33.6833 | -118.0062 | 100.346 | CLS C
CLS 43 | Cluster | Ext | 7052.5 | 0.8 | 0.28 | 35000 | ERW | 8.625 | 715 | 28.6925 | 0.08 | 3.964 | 2.774 | 8:12 | 2481 | 0.40026 | 19 | 3.96 | 2589 | AGM 2 | 2104.22 | Valve 607 | 810.12 | 23.49 | 12.45 | 45.18 | 47.11 | 35.95 | 2990 | 0.36 | 1.29 | 33.6833 | -118.0062 | 100.342 | CLS C
CLS 44 | Cluster | Ext | 7053.3 | 1.2 | 0.28 | 35000 | ERW | 8.625 | 715 | 15.9781 | 0.045 | 1.859 | 2.353 | 7:13 | 2802 | 0.35441 | 9 | 1.86 | 2844 | AGM 2 | 2105.01 | Valve 607 | 809.32 | 24.29 | 11.66 | 45.18 | 47.11 | 35.95 | 2990 | 0.36 | 1.29 | 33.6833 | -118.0062 | 100.336 | CLS C
DMA 278 | Metal Loss | Ext | 7054.5 | 5.47 | 0.28 | 35000 | ERW | 8.625 | 715 | 10.5811 | 0.03 | 1.646 | 1.373 | 10:17 | 2856 | 0.34771 | 11 | 1.65 | 2843 | AGM 2 | 2106.21 | Valve 607 | 808.13 | 25.49 | 10.46 | 45.18 | 47.11 | 35.95 | 2990 | 0.36 | 1.29 | 33.6833 | -118.0062 | 100.323
DMA 279 | Metal Loss | Ext | 7059.97 | 4.99 | 0.28 | 35000 | ERW | 8.625 | 715 | 14.0179 | 0.039 | 1.317 | 1.151 | 11:34 | 2856 | 0.34771 | 14 | 1.32 | 2843 | AGM 2 | 2111.68 | Valve 607 | 802.66 | 30.96 | 4.99 | 45.18 | 47.11 | 35.95 | 2990 | 0.36 | 1.29 | 33.6833 | -118.0062 | 100.255
GWD 3000 | Girth Weld |  | 7064.96 | 0.17 | 0.28 | 35000 | ERW | 8.625 | 715 | [10 empty] | AGM 2 | 2116.67 | Valve 607 | 797.67 | 35.95 | 0.36 | 47.11 | 35.95 | 0.36 | 3000 | 1.29 | 16.64 | 33.6833 | -118.0062 | 100.176
RED 1 | Reducer |  | 7065.12 | 0.19 | 0.28 | 35000 | ERW | 8.625 | 715 |  |  |  |  | 7:20 | [5 empty] | AGM 2 | 2116.84 | Valve 607 | 797.5 | 0.17 | 0.19 | 47.11 | 35.95 | 0.36 | 3000 | 1.29 | 16.64 | 33.6833 | -118.0062 | 100.177 | Reducer NPS 8 x 6
GWD 3010 | Girth Weld |  | 7065.32 | 0.74 | 0.28 | 35000 | ERW | 6.625 | 715 | [10 empty] | AGM 2 | 2117.03 | Valve 607 | 797.31 | 0.36 | 1.29 | 35.95 | 0.36 | 1.29 | 3010 | 16.64 | 1.21 | 33.6833 | -118.0062 | 100.179
BND 47 | Bend |  | 7066.06 | 0.54 | 0.28 | 35000 | ERW | 6.625 | 715 |  |  | 15.472 | [7 empty] | AGM 2 | 2117.77 | Valve 607 | 796.57 | 0.74 | 0.55 | 35.95 | 0.36 | 1.29 | 3010 | 16.64 | 1.21 | 33.6833 | -118.0062 | 100.195 | 3.0D 50.5 deg right turn bend
GWD 3020 | Girth Weld |  | 7066.6 | 16.22 | 0.219 | 35000 | ERW | 6.625 | 715 | [10 empty] | AGM 2 | 2118.32 | Valve 607 | 796.02 | 1.29 | 16.64 | 0.36 | 1.29 | 16.64 | 3020 | 1.21 | 1.01 | 33.6833 | -118.0062 | 100.199
DMA 280 | Metal Loss | Ext | 7082.82 | 0.42 | 0.219 | 35000 | ERW | 6.625 | 715 | 14.7361 | 0.032 | 0.512 | 0.561 | 5:16 | 2953 | 0.33629 | 15 | 0.51 | 2949 | AGM 2 | 2134.53 | Valve 607 | 779.8 | 16.22 | 0.42 | 0.36 | 1.29 | 16.64 | 3020 | 1.21 | 1.01 | 33.6833 | -118.0062 | 100.19
GWD 3030 | Girth Weld |  | 7083.24 | 0.77 | 0.219 | 35000 | ERW | 6.625 | 715 | [10 empty] | AGM 2 | 2134.95 | Valve 607 | 779.39 | 16.64 | 1.21 | 1.29 | 16.64 | 1.21 | 3030 | 1.01 | 40.06 | 33.6833 | -118.0062 | 100.19
BND 48 | Bend |  | 7084.01 | 0.44 | 0.219 | 35000 | ERW | 6.625 | 715 |  |  | 14.528 | [7 empty] | AGM 2 | 2135.73 | Valve 607 | 778.61 | 0.77 | 0.44 | 1.29 | 16.64 | 1.21 | 3030 | 1.01 | 40.06 | 33.6833 | -118.0062 | 100.19 | 3.0D 48.3 deg left turn over bend
GWD 3040 | Girth Weld |  | 7084.45 | 1.01 | 0.219 | 35000 | ERW | 6.625 | 715 | [10 empty] | AGM 2 | 2136.17 | Valve 607 | 778.17 | 1.21 | 1.01 | 16.64 | 1.21 | 1.01 | 3040 | 40.06 | 40.97 | 33.6833 | -118.0062 | 100.183
GWD 3050 | Girth Weld |  | 7085.46 | 40.06 | 0.219 | 35000 | ERW | 6.625 | 715 | [10 empty] | AGM 2 | 2137.17 | Valve 607 | 777.16 | 1.01 | 40.06 | 1.21 | 1.01 | 40.06 | 3050 | 40.97 | 40.95 | 33.6833 | -118.0062 | 100.17
GWD 3060 | Girth Weld |  | 7125.52 | 40.97 | 0.219 | 35000 | ERW | 6.625 | 715 | [10 empty] | AGM 2 | 2177.23 | Valve 607 | 737.1 | 40.06 | 40.97 | 1.01 | 40.06 | 40.97 | 3060 | 40.95 | 40.81 | 33.6835 | -118.0062 | 98.518
GWD 3070 | Girth Weld |  | 7166.5 | 40.95 | 0.219 | 35000 | ERW | 6.625 | 715 | [10 empty] | AGM 2 | 2218.21 | Valve 607 | 696.13 | 40.97 | 40.95 | 40.06 | 40.97 | 40.95 | 3070 | 40.81 | 41.02 | 33.6836 | -118.0062 | 95.598
GWD 3080 | Girth Weld |  | 7207.44 | 40.81 | 0.219 | 35000 | ERW | 6.625 | 715 | [10 empty] | AGM 2 | 2259.15 | Valve 607 | 655.18 | 40.95 | 40.81 | 40.97 | 40.95 | 40.81 | 3080 | 41.02 | 40.99 | 33.6837 | -118.0062 | 94.17
GWD 3090 | Girth Weld |  | 7248.26 | 41.02 | 0.219 | 35000 | ERW | 6.625 | 715 | [10 empty] | AGM 2 | 2299.97 | Valve 607 | 614.37 | 40.81 | 41.02 | 40.95 | 40.81 | 41.02 | 3090 | 40.99 | 40.92 | 33.6838 | -118.0062 | 92.041
GWD 3100 | Girth Weld |  | 7289.28 | 40.99 | 0.219 | 35000 | ERW | 6.625 | 715 | [10 empty] | AGM 2 | 2340.99 | Valve 607 | 573.35 | 41.02 | 40.99 | 40.81 | 41.02 | 40.99 | 3100 | 40.92 | 41.03 | 33.6839 | -118.0062 | 89.779
GWD 3110 | Girth Weld |  | 7330.26 | 40.92 | 0.219 | 35000 | ERW | 6.625 | 715 | [10 empty] | AGM 2 | 2381.98 | Valve 607 | 532.36 | 40.99 | 40.92 | 41.02 | 40.99 | 40.92 | 3110 | 41.03 | 40.95 | 33.684 | -118.0062 | 87.595
GWD 3120 | Girth Weld |  | 7371.18 | 41.03 | 0.219 | 35000 | ERW | 6.625 | 715 | [10 empty] | AGM 2 | 2422.9 | Valve 607 | 491.44 | 40.92 | 41.03 | 40.99 | 40.92 | 41.03 | 3120 | 40.95 | 40.96 | 33.6841 | -118.0062 | 85.812
GWD 3130 | Girth Weld |  | 7412.21 | 40.95 | 0.219 | 35000 | ERW | 6.625 | 715 | [10 empty] | AGM 2 | 2463.93 | Valve 607 | 450.41 | 41.03 | 40.95 | 40.92 | 41.03 | 40.95 | 3130 | 40.96 | 40.87 | 33.6842 | -118.0062 | 83.019
GWD 3140 | Girth Weld |  | 7453.16 | 40.96 | 0.219 | 35000 | ERW | 6.625 | 715 | [10 empty] | AGM 2 | 2504.87 | Valve 607 | 409.47 | 40.95 | 40.96 | 41.03 | 40.95 | 40.96 | 3140 | 40.87 | 40.98 | 33.6843 | -118.0062 | 81.392
GWD 3150 | Girth Weld |  | 7494.12 | 40.87 | 0.219 | 35000 | ERW | 6.625 | 715 | [10 empty] | AGM 2 | 2545.83 | Valve 607 | 368.51 | 40.96 | 40.87 | 40.95 | 40.96 | 40.87 | 3150 | 40.98 | 40.87 | 33.6845 | -118.0062 | 79.847
GWD 3160 | Girth Weld |  | 7534.99 | 40.97 | 0.219 | 35000 | ERW | 6.625 | 715 | [10 empty] | AGM 2 | 2586.7 | Valve 607 | 327.64 | 40.87 | 40.98 | 40.96 | 40.87 | 40.98 | 3160 | 40.87 | 40.94 | 33.6846 | -118.0062 | 78.758
GWD 3170 | Girth Weld |  | 7575.96 | 40.87 | 0.219 | 35000 | ERW | 6.625 | 715 | [10 empty] | AGM 2 | 2627.67 | Valve 607 | 286.66 | 40.98 | 40.87 | 40.87 | 40.98 | 40.87 | 3170 | 40.94 | 40.95 | 33.6847 | -118.0062 | 78.12
GWD 3180 | Girth Weld |  | 7616.83 | 40.94 | 0.219 | 35000 | ERW | 6.625 | 715 | [10 empty] | AGM 2 | 2668.55 | Valve 607 | 245.79 | 40.87 | 40.94 | 40.98 | 40.87 | 40.94 | 3180 | 40.95 | 40.81 | 33.6848 | -118.0062 | 77.384
GWD 3190 | Girth Weld |  | 7657.78 | 40.95 | 0.219 | 35000 | ERW | 6.625 | 715 | [10 empty] | AGM 2 | 2709.49 | Valve 607 | 204.85 | 40.94 | 40.95 | 40.87 | 40.94 | 40.95 | 3190 | 40.81 | 40.84 | 33.6849 | -118.0063 | 76.529
GWD 3200 | Girth Weld |  | 7698.72 | 40.8 | 0.219 | 35000 | ERW | 6.625 | 715 | [10 empty] | AGM 2 | 2750.44 | Valve 607 | 163.9 | 40.95 | 40.81 | 40.94 | 40.95 | 40.81 | 3200 | 40.84 | 40.79 | 33.685 | -118.0063 | 76.401
GWD 3210 | Girth Weld |  | 7739.53 | 40.84 | 0.219 | 35000 | ERW | 6.625 | 715 | [10 empty] | AGM 2 | 2791.24 | Valve 607 | 123.1 | 40.81 | 40.84 | 40.95 | 40.81 | 40.84 | 3210 | 40.79 | 5.34 | 33.6851 | -118.0063 | 76.366
GWD 3220 | Girth Weld |  | 7780.37 | 40.79 | 0.219 | 35000 | ERW | 6.625 | 715 | [10 empty] | AGM 2 | 2832.08 | Valve 607 | 82.26 | 40.84 | 40.79 | 40.81 | 40.84 | 40.79 | 3220 | 5.34 | 2.41 | 33.6852 | -118.0063 | 76.471
GWD 3230 | Girth Weld |  | 7821.15 | 5.34 | 0.219 | 35000 | ERW | 6.625 | 715 | [10 empty] | AGM 2 | 2872.87 | Valve 607 | 41.47 | 40.79 | 5.34 | 40.84 | 40.79 | 5.34 | 3230 | 2.41 | 24.51 | 33.6853 | -118.0063 | 76.31
GWD 3240 | Girth Weld |  | 7826.49 | 1.2 | 0.219 | 35000 | ERW | 6.625 | 715 | [10 empty] | AGM 2 | 2878.2 | Valve 607 | 36.14 | 5.34 | 2.41 | 40.79 | 5.34 | 2.41 | 3240 | 24.51 | 1.95 | 33.6854 | -118.0063 | 76.243
BND 49 | Bend |  | 7827.69 | 1.21 | 0.219 | 35000 | ERW | 6.625 | 715 |  |  | 28.946 | [7 empty] | AGM 2 | 2879.41 | Valve 607 | 34.93 | 1.2 | 1.21 | 40.79 | 5.34 | 2.41 | 3240 | 24.51 | 1.95 | 33.6854 | -118.0063 | 76.262 | 3.0D 91.6 deg left turn sag bend
GWD 3250 | Girth Weld |  | 7828.9 | 24.51 | 0.219 | 35000 | ERW | 6.625 | 715 | [10 empty] | AGM 2 | 2880.62 | Valve 607 | 33.72 | 2.41 | 24.51 | 5.34 | 2.41 | 24.51 | 3250 | 1.95 | 1 | 33.6854 | -118.0063 | 76.315
GWD 3260 | Girth Weld |  | 7853.41 | 0.74 | 0.219 | 35000 | ERW | 6.625 | 715 | [10 empty] | AGM 2 | 2905.13 | Valve 607 | 9.21 | 24.51 | 1.95 | 2.41 | 24.51 | 1.95 | 3260 | 1 | 0.92 | 33.6854 | -118.0063 | 77.337
CLS 45 | Cluster | Ext | 7854.16 | 0.16 | 0.219 | 35000 | ERW | 6.625 | 715 | 15.2319 | 0.033 | 3.725 | 3.686 | 5:44 | 2726 | 0.36429 | 10 | 3.72 | 2783 | AGM 2 | 2905.87 | Valve 607 | 8.47 | 0.75 | 1.2 | 2.41 | 24.51 | 1.95 | 3260 | 1 | 0.92 | 33.6854 | -118.0063 | 77.36 | CLS C
CLS 46 | Cluster | Ext | 7854.32 | 0.1 | 0.219 | 35000 | ERW | 6.625 | 715 | 11.4975 | 0.025 | 1.13 | 2.876 | 10:18 | 2913 | 0.3409 | 11 | 1.13 | 2902 | AGM 2 | 2906.04 | Valve 607 | 8.3 | 0.91 | 1.04 | 2.41 | 24.51 | 1.95 | 3260 | 1 | 0.92 | 33.6854 | -118.0063 | 77.364 | CLS C
DMA 300 | Metal Loss | Ext | 7854.43 | 0.03 | 0.219 | 35000 | ERW | 6.625 | 715 | 10.9544 | 0.024 | 0.605 | 0.593 | 6:53 | 2954 | 0.33617 | 11 | 0.61 | 2949 | AGM 2 | 2906.14 | Valve 607 | 8.2 | 1.01 | 0.94 | 2.41 | 24.51 | 1.95 | 3260 | 1 | 0.92 | 33.6854 | -118.0063 | 77.364
CLS 47 | Cluster | Ext | 7854.45 | 0.02 | 0.219 | 35000 | ERW | 6.625 | 715 | 13.4003 | 0.029 | 9.148 | 8.511 | 3:22 | 2696 | 0.36834 | 9 | 6.62 | 2757 | AGM 2 | 2906.17 | Valve 607 | 8.17 | 1.04 | 0.91 | 2.41 | 24.51 | 1.95 | 3260 | 1 | 0.92 | 33.6854 | -118.0063 | 77.364 | CLS C
DMA 302 | Metal Loss | Ext | 7854.47 | 0.18 | 0.219 | 35000 | ERW | 6.625 | 715 | 11.763 | 0.026 | 0.315 | 0.541 | 10:14 | 2968 | 0.33459 | 12 | 0.31 | 2967 | AGM 2 | 2906.18 | Valve 607 | 8.15 | 1.06 | 0.89 | 2.41 | 24.51 | 1.95 | 3260 | 1 | 0.92 | 33.6854 | -118.0063 | 77.364
CLS 48 | Cluster | Ext | 7854.65 | 0.09 | 0.219 | 35000 | ERW | 6.625 | 715 | 11.4715 | 0.025 | 2.409 | 3.085 | 8:54 | 2834 | 0.35041 | 8 | 2.41 | 2866 | AGM 2 | 2906.36 | Valve 607 | 7.98 | 1.23 | 0.72 | 2.41 | 24.51 | 1.95 | 3260 | 1 | 0.92 | 33.6854 | -118.0063 | 77.364 | CLS C
CLS 49 | Cluster | Ext | 7854.74 | 0.08 | 0.219 | 35000 | ERW | 6.625 | 715 | 13.0397 | 0.029 | 0.99 | 2.154 | 1:16 | 2916 | 0.34055 | 12 | 0.99 | 2911 | AGM 2 | 2906.45 | Valve 607 | 7.89 | 1.32 | 0.63 | 2.41 | 24.51 | 1.95 | 3260 | 1 | 0.92 | 33.6854 | -118.0063 | 77.364 | CLS C
DMA 318 | Metal Loss | Ext | 7854.82 | 0.1 | 0.219 | 35000 | ERW | 6.625 | 715 | 10.4215 | 0.023 | 0.629 | 0.701 | 10:57 | 2953 | 0.33629 | 10 | 0.63 | 2949 | AGM 2 | 2906.53 | Valve 607 | 7.81 | 1.4 | 0.55 | 2.41 | 24.51 | 1.95 | 3260 | 1 | 0.92 | 33.6854 | -118.0063 | 77.364
DMA 319 | Metal Loss | Ext | 7854.92 | 0.44 | 0.219 | 35000 | ERW | 6.625 | 715 | 13.0376 | 0.029 | 0.447 | 0.768 | 6:21 | 2960 | 0.33549 | 13 | 0.45 | 2957 | AGM 2 | 2906.63 | Valve 607 | 7.71 | 1.51 | 0.44 | 2.41 | 24.51 | 1.95 | 3260 | 1 | 0.92 | 33.6854 | -118.0063 | 77.364
GWD 3270 | Girth Weld |  | 7855.36 | 0.3 | 0.219 | 35000 | ERW | 6.625 | 715 | [10 empty] | AGM 2 | 2907.08 | Valve 607 | 7.26 | 1.95 | 1 | 24.51 | 1.95 | 1 | 3270 | 0.92 | 4.3 | 33.6854 | -118.0064 | 77.377
BND 50 | Bend |  | 7855.67 | 0.7 | 0.219 | 35000 | ERW | 6.625 | 715 |  |  | 14.788 | [7 empty] | AGM 2 | 2907.38 | Valve 607 | 6.96 | 0.3 | 0.7 | 24.51 | 1.95 | 1 | 3270 | 0.92 | 4.3 | 33.6854 | -118.0064 | 77.408 | 6.7D 25.5 deg sag bend
GWD 3280 | Girth Weld |  | 7856.37 | 0.92 | 0.219 | 35000 | ERW | 6.625 | 715 | [10 empty] | AGM 2 | 2908.08 | Valve 607 | 6.26 | 1 | 0.92 | 1.95 | 1 | 0.92 | 3280 | 4.3 | 2.12 | 33.6854 | -118.0064 | 77.606
GWD 3290 | Girth Weld |  | 7857.29 | 0.21 | 0.219 | 35000 | ERW | 6.625 | 715 | [10 empty] | AGM 2 | 2909 | Valve 607 | 5.34 | 0.92 | 4.3 | 1 | 0.92 | 4.3 | 3290 | 2.12 | 5.14 | 33.6854 | -118.0064 | 77.95
BND 51 | Bend |  | 7857.5 | 1.25 | 0.219 | 35000 | ERW | 6.625 | 715 |  |  | 14.334 | [7 empty] | AGM 2 | 2909.21 | Valve 607 | 5.13 | 0.21 | 4.09 | 1 | 0.92 | 4.3 | 3290 | 2.12 | 5.14 | 33.6854 | -118.0064 | 77.99 | 6.8D 24.5 deg over bend
SUP 1 | Support |  | 7858.75 | 2.12 | 0.219 | 35000 | ERW | 6.625 | 715 |  |  |  |  | 12:20 | [5 empty] | AGM 2 | 2910.46 | Valve 607 | 3.88 | 1.46 | 2.85 | 1 | 0.92 | 4.3 | 3290 | 2.12 | 5.14 | 33.6854 | -118.0064 | 78.045 | Full Circ.
TAP 7 | TAP |  | 7860.86 | 0.73 | 0.219 | 35000 | ERW | 6.625 | 715 |  |  |  |  | 11:54 | [5 empty] | AGM 2 | 2912.58 | Valve 607 | 1.76 | 3.57 | 0.73 | 1 | 0.92 | 4.3 | 3290 | 2.12 | 5.14 | 33.6854 | -118.0064 | 78.118
GWD 3300 | Girth Weld |  | 7861.59 | 1.04 | 0.219 | 35000 | ERW | 6.625 | 715 | [10 empty] | AGM 2 | 2913.3 | Valve 607 | 1.04 | 4.3 | 2.12 | 0.92 | 4.3 | 2.12 | 3300 | 5.14 | 2.44 | 33.6854 | -118.0064 | 78.139
VLV 1 | Valve |  | 7862.63 | 1.09 | 0.219 | 35000 | ERW | 6.625 | 715 | [10 empty] | AGM 2 | 2914.34 | MLV 1 | 21.63 | 1.04 | 1.09 | 0.92 | 4.3 | 2.12 | 3300 | 5.14 | 2.44 | 33.6854 | -118.0064 | 78.167 | Valve 607 Located Inside Underground Vault by Carls JR¦Start Section CSFM 1305¦End Section CSFM 825
GWD 3310 | Girth Weld |  | 7863.71 | 4.14 | 0.219 | 35000 | ERW | 6.625 | 715 | [10 empty] | Valve 607 | 1.09 | MLV 1 | 20.54 | 2.12 | 5.14 | 4.3 | 2.12 | 5.14 | 3310 | 2.44 | 1.01 | 33.6854 | -118.0064 | 78.2
TAP 8 | TAP |  | 7867.85 | 1 | 0.219 | 35000 | ERW | 6.625 | 715 |  |  |  |  | 11:44 | [5 empty] | Valve 607 | 5.23 | MLV 1 | 16.4 | 4.14 | 1 | 4.3 | 2.12 | 5.14 | 3310 | 2.44 | 1.01 | 33.6854 | -118.0064 | 78.275
GWD 3320 | Girth Weld |  | 7868.85 | 1.25 | 0.219 | 35000 | ERW | 6.625 | 715 | [10 empty] | Valve 607 | 6.23 | MLV 1 | 15.4 | 5.14 | 2.44 | 2.12 | 5.14 | 2.44 | 3320 | 1.01 | 1.02 | 33.6854 | -118.0064 | 78.292
BND 52 | Bend |  | 7870.11 | 1.18 | 0.219 | 35000 | ERW | 6.625 | 715 |  |  | 29.711 | [7 empty] | Valve 607 | 7.48 | MLV 1 | 14.15 | 1.25 | 1.18 | 2.12 | 5.14 | 2.44 | 3320 | 1.01 | 1.02 | 33.6854 | -118.0064 | 78.301 | 3.0D 91.8 deg right turn bend
GWD 3330 | Girth Weld |  | 7871.29 | 1.01 | 0.219 | 35000 | ERW | 6.625 | 715 | [10 empty] | Valve 607 | 8.67 | MLV 1 | 12.96 | 2.44 | 1.01 | 5.14 | 2.44 | 1.01 | 3330 | 1.02 | 5.04 | 33.6854 | -118.0064 | 78.324
GWD 3340 | Girth Weld |  | 7872.3 | 0.53 | 0.219 | 35000 | ERW | 6.625 | 715 | [10 empty] | Valve 607 | 9.67 | MLV 1 | 11.95 | 1.01 | 1.02 | 2.44 | 1.01 | 1.02 | 3340 | 5.04 | 2.42 | 33.6854 | -118.0064 | 78.344
TEE 2 | Tee |  | 7872.82 | 0.49 | 0.219 | 35000 | ERW | 6.625 | 715 |  |  | 8.835 | 8.835 | 3:03 | [5 empty] | Valve 607 | 10.2 | MLV 1 | 11.43 | 0.52 | 0.49 | 2.44 | 1.01 | 1.02 | 3340 | 5.04 | 2.42 | 33.6854 | -118.0064 | 78.356
GWD 3350 | Girth Weld |  | 7873.32 | 5.04 | 0.219 | 35000 | ERW | 6.625 | 715 | [10 empty] | Valve 607 | 10.69 | MLV 1 | 10.94 | 1.02 | 5.04 | 1.01 | 1.02 | 5.04 | 3350 | 2.42 | 2.42 | 33.6854 | -118.0064 | 78.364
GWD 3360 | Girth Weld |  | 7878.35 | 1.26 | 0.219 | 35000 | ERW | 6.625 | 715 | [10 empty] | Valve 607 | 15.73 | MLV 1 | 5.9 | 5.04 | 2.42 | 1.02 | 5.04 | 2.42 | 3360 | 2.42 | 2.12 | 33.6854 | -118.0064 | 78.437
BND 53 | Bend |  | 7879.62 | 1.15 | 0.219 | 35000 | ERW | 6.625 | 715 |  |  | 28.56 | [7 empty] | Valve 607 | 16.99 | MLV 1 | 4.64 | 1.27 | 1.15 | 1.02 | 5.04 | 2.42 | 3360 | 2.42 | 2.12 | 33.6854 | -118.0064 | 78.453 | 3.0D 90.6 deg right turn bend
GWD 3370 | Girth Weld |  | 7880.77 | 1.03 | 0.219 | 35000 | ERW | 6.625 | 715 | [10 empty] | Valve 607 | 18.14 | MLV 1 | 3.49 | 2.42 | 2.42 | 5.04 | 2.42 | 2.42 | 3370 | 2.12 | 0.62 | 33.6854 | -118.0064 | 78.486
TAP 9 | TAP |  | 7881.8 | 1.39 | 0.219 | 35000 | ERW | 6.625 | 715 |  |  |  |  | 5:45 | [5 empty] | Valve 607 | 19.17 | MLV 1 | 2.46 | 1.03 | 1.39 | 5.04 | 2.42 | 2.42 | 3370 | 2.12 | 0.62 | 33.6854 | -118.0064 | 78.515
GWD 3380 | Girth Weld |  | 7883.19 | 1.06 | 0.219 | 35000 | ERW | 6.625 | 715 | [10 empty] | Valve 607 | 20.56 | MLV 1 | 1.06 | 2.42 | 2.12 | 2.42 | 2.42 | 2.12 | 3380 | 0.62 | 2.15 | 33.6854 | -118.0064 | 78.548
VLV 2 | Valve |  | 7884.25 | 1.05 | 0.219 | 35000 | ERW | 6.625 | 715 | [10 empty] | Valve 607 | 21.63 | MLV 2 | 2.73 | 1.06 | 1.05 | 2.42 | 2.42 | 2.12 | 3380 | 0.62 | 2.15 | 33.6854 | -118.0064 | 78.568 | MLV 1
GWD 3390 | Girth Weld |  | 7885.31 | 0.61 | 0.219 | 35000 | ERW | 6.625 | 715 | [10 empty] | MLV 1 | 1.05 | MLV 2 | 1.68 | 2.12 | 0.62 | 2.42 | 2.12 | 0.62 | 3390 | 2.15 | 4.1 | 33.6854 | -118.0064 | 78.584
GWD 3400 | Girth Weld |  | 7885.92 | 1.07 | 0.219 | 35000 | ERW | 6.625 | 715 | [10 empty] | MLV 1 | 1.67 | MLV 2 | 1.06 | 0.62 | 2.15 | 2.12 | 0.62 | 2.15 | 3400 | 4.1 | 0.91 | 33.6854 | -118.0064 | 78.59
VLV 3 | Valve |  | 7886.99 | 1.08 | 0.219 | 35000 | ERW | 6.625 | 715 | [10 empty] | MLV 1 | 2.73 | AGM 3 | 2776.95 | 1.06 | 1.08 | 2.12 | 0.62 | 2.15 | 3400 | 4.1 | 0.91 | 33.6854 | -118.0064 | 78.598 | MLV 2
GWD 3410 | Girth Weld |  | 7888.07 | 0.74 | 0.219 | 42000 | ERW | 6.625 | 728 | [10 empty] | MLV 2 | 1.08 | AGM 3 | 2775.87 | 2.15 | 4.1 | 0.62 | 2.15 | 4.1 | 3410 | 0.91 | 0.92 | 33.6854 | -118.0064 | 78.608
TAP 10 | TAP |  | 7888.81 | 2.08 | 0.219 | 42000 | ERW | 6.625 | 728 |  |  |  |  | 11:56 | [5 empty] | MLV 2 | 1.82 | AGM 3 | 2775.13 | 0.74 | 3.36 | 0.62 | 2.15 | 4.1 | 3410 | 0.91 | 0.92 | 33.6854 | -118.0064 | 78.612
SUP 2 | Support |  | 7890.89 | 1.28 | 0.219 | 42000 | ERW | 6.625 | 728 |  |  |  |  | 12:16 | [5 empty] | MLV 2 | 3.9 | AGM 3 | 2773.05 | 2.82 | 1.28 | 0.62 | 2.15 | 4.1 | 3410 | 0.91 | 0.92 | 33.6854 | -118.0064 | 78.625 | Full Circ.
GWD 3420 | Girth Weld |  | 7892.17 | 0.17 | 0.219 | 42000 | ERW | 6.625 | 728 | [10 empty] | MLV 2 | 5.18 | AGM 3 | 2771.77 | 4.1 | 0.91 | 2.15 | 4.1 | 0.91 | 3420 | 0.92 | 13 | 33.6854 | -118.0064 | 78.649
BND 54 | Bend |  | 7892.34 | 0.74 | 0.219 | 42000 | ERW | 6.625 | 728 |  |  | 15.196 | [7 empty] | MLV 2 | 5.35 | AGM 3 | 2771.6 | 0.17 | 0.74 | 2.15 | 4.1 | 0.91 | 3420 | 0.92 | 13 | 33.6854 | -118.0064 | 78.628 | 6.2D 27.4 deg left turn over bend
GWD 3430 | Girth Weld |  | 7893.08 | 0.92 | 0.219 | 42000 | ERW | 6.625 | 728 | [10 empty] | MLV 2 | 6.09 | AGM 3 | 2770.86 | 0.91 | 0.92 | 4.1 | 0.91 | 0.92 | 3430 | 13 | 1.21 | 33.6854 | -118.0064 | 78.42
GWD 3440 | Girth Weld |  | 7894 | 0.17 | 0.219 | 42000 | ERW | 6.625 | 728 | [10 empty] | MLV 2 | 7.01 | AGM 3 | 2769.94 | 0.92 | 13 | 0.91 | 0.92 | 13 | 3440 | 1.21 | 20.45 | 33.6854 | -118.0064 | 78.089
BND 55 | Bend |  | 7894.16 | 12.84 | 0.219 | 42000 | ERW | 6.625 | 728 |  |  | 15.615 | [7 empty] | MLV 2 | 7.18 | AGM 3 | 2769.77 | 0.17 | 12.84 | 0.91 | 0.92 | 13 | 3440 | 1.21 | 20.45 | 33.6854 | -118.0064 | 78.062 | 6.9D 24.9 deg right turn sag bend
GWD 3450 | Girth Weld |  | 7907 | 0.68 | 0.219 | 42000 | ERW | 6.625 | 728 | [10 empty] | MLV 2 | 20.01 | AGM 3 | 2756.94 | 13 | 1.21 | 0.92 | 13 | 1.21 | 3450 | 20.45 | 1.22 | 33.6854 | -118.0063 | 77.917
BND 56 | Bend |  | 7907.67 | 0.54 | 0.219 | 42000 | ERW | 6.625 | 728 |  |  | 14.528 | [7 empty] | MLV 2 | 20.69 | AGM 3 | 2756.26 | 0.68 | 0.54 | 0.92 | 13 | 1.21 | 3450 | 20.45 | 1.22 | 33.6854 | -118.0063 | 77.911 | 3.0D 49.8 deg left turn bend
GWD 3460 | Girth Weld |  | 7908.21 | 20.45 | 0.219 | 42000 | ERW | 6.625 | 728 | [10 empty] | MLV 2 | 21.23 | AGM 3 | 2755.73 | 1.21 | 20.45 | 13 | 1.21 | 20.45 | 3460 | 1.22 | 4.17 | 33.6854 | -118.0063 | 77.908
GWD 3470 | Girth Weld |  | 7928.67 | 0.72 | 0.219 | 42000 | ERW | 6.625 | 728 | [10 empty] | MLV 2 | 41.68 | AGM 3 | 2735.27 | 20.45 | 1.22 | 1.21 | 20.45 | 1.22 | 3470 | 4.17 | 40.98 | 33.6854 | -118.0063 | 77.811
BND 57 | Bend |  | 7929.38 | 0.51 | 0.219 | 42000 | ERW | 6.625 | 728 |  |  | 14.646 | [7 empty] | MLV 2 | 42.39 | AGM 3 | 2734.56 | 0.71 | 0.5 | 1.21 | 20.45 | 1.22 | 3470 | 4.17 | 40.98 | 33.6854 | -118.0063 | 77.812 | 3.0D 49.9 deg left turn bend
GWD 3480 | Girth Weld |  | 7929.88 | 4.17 | 0.219 | 42000 | ERW | 6.625 | 728 | [10 empty] | MLV 2 | 42.9 | AGM 3 | 2734.05 | 1.22 | 4.17 | 20.45 | 1.22 | 4.17 | 3480 | 40.98 | 40.46 | 33.6854 | -118.0063 | 77.812
GWD 3490 | Girth Weld |  | 7934.06 | 40.98 | 0.219 | 42000 | ERW | 6.625 | 728 | [10 empty] | MLV 2 | 47.07 | AGM 3 | 2729.88 | 4.17 | 40.98 | 1.22 | 4.17 | 40.98 | 3490 | 40.46 | 40.88 | 33.6854 | -118.0063 | 77.815
GWD 3500 | Girth Weld |  | 7975.04 | 40.46 | 0.219 | 42000 | ERW | 6.625 | 728 | [10 empty] | MLV 2 | 88.05 | AGM 3 | 2688.9 | 40.98 | 40.46 | 4.17 | 40.98 | 40.46 | 3500 | 40.88 | 40.86 | 33.6856 | -118.0063 | 77.823
GWD 3510 | Girth Weld |  | 8015.5 | 40.88 | 0.219 | 42000 | ERW | 6.625 | 728 | [10 empty] | MLV 2 | 128.51 | AGM 3 | 2648.44 | 40.46 | 40.88 | 40.98 | 40.46 | 40.88 | 3510 | 40.86 | 40.93 | 33.6857 | -118.0063 | 78.346
GWD 3520 | Girth Weld |  | 8056.38 | 40.86 | 0.219 | 42000 | ERW | 6.625 | 728 | [10 empty] | MLV 2 | 169.39 | AGM 3 | 2607.56 | 40.88 | 40.86 | 40.46 | 40.88 | 40.86 | 3520 | 40.93 | 40.92 | 33.6858 | -118.0063 | 78.441
GWD 3530 | Girth Weld |  | 8097.23 | 40.93 | 0.219 | 42000 | ERW | 6.625 | 728 | [10 empty] | MLV 2 | 210.25 | AGM 3 | 2566.71 | 40.86 | 40.93 | 40.88 | 40.86 | 40.93 | 3530 | 40.92 | 40.85 | 33.6859 | -118.0063 | 78.665
GWD 3540 | Girth Weld |  | 8138.16 | 40.92 | 0.219 | 42000 | ERW | 6.625 | 728 | [10 empty] | MLV 2 | 251.18 | AGM 3 | 2525.77 | 40.93 | 40.92 | 40.86 | 40.93 | 40.92 | 3540 | 40.85 | 40.8 | 33.686 | -118.0063 | 77.824
GWD 3550 | Girth Weld |  | 8179.08 | 40.86 | 0.219 | 42000 | ERW | 6.625 | 728 | [10 empty] | MLV 2 | 292.09 | AGM 3 | 2484.86 | 40.92 | 40.85 | 40.93 | 40.92 | 40.85 | 3550 | 40.8 | 38.67 | 33.6861 | -118.0063 | 77.427
GWD 3560 | Girth Weld |  | 8219.93 | 40.79 | 0.219 | 42000 | ERW | 6.625 | 728 | [10 empty] | MLV 2 | 332.95 | AGM 3 | 2444 | 40.85 | 40.8 | 40.92 | 40.85 | 40.8 | 3560 | 38.67 | 1.21 | 33.6862 | -118.0063 | 77.765
GWD 3570 | Girth Weld |  | 8260.73 | 38.67 | 0.219 | 42000 | ERW | 6.625 | 728 | [10 empty] | MLV 2 | 373.74 | AGM 3 | 2403.21 | 40.8 | 38.67 | 40.85 | 40.8 | 38.67 | 3570 | 1.21 | 4.29 | 33.6863 | -118.0063 | 77.668
GWD 3580 | Girth Weld |  | 8299.4 | 0.67 | 0.219 | 42000 | ERW | 6.625 | 728 | [10 empty] | MLV 2 | 412.42 | AGM 3 | 2364.54 | 38.67 | 1.21 | 40.8 | 38.67 | 1.21 | 3580 | 4.29 | 1.22 | 33.6864 | -118.0063 | 76.633
BND 58 | Bend |  | 8300.07 | 0.54 | 0.219 | 42000 | ERW | 6.625 | 728 |  |  | 14.528 | [7 empty] | MLV 2 | 413.09 | AGM 3 | 2363.86 | 0.67 | 0.54 | 40.8 | 38.67 | 1.21 | 3580 | 4.29 | 1.22 | 33.6864 | -118.0063 | 76.499 | 3.0D 49.3 deg left turn over bend
GWD 3590 | Girth Weld |  | 8300.61 | 4.29 | 0.219 | 42000 | ERW | 6.625 | 728 | [10 empty] | MLV 2 | 413.62 | AGM 3 | 2363.33 | 1.21 | 4.29 | 38.67 | 1.21 | 4.29 | 3590 | 1.22 | 40.91 | 33.6864 | -118.0063 | 76.221
GWD 3600 | Girth Weld |  | 8304.9 | 0.69 | 0.219 | 42000 | ERW | 6.625 | 728 | [10 empty] | MLV 2 | 417.91 | AGM 3 | 2359.04 | 4.29 | 1.22 | 1.21 | 4.29 | 1.22 | 3600 | 40.91 | 40.79 | 33.6865 | -118.0063 | 73.11
BND 59 | Bend |  | 8305.59 | 0.54 | 0.219 | 42000 | ERW | 6.625 | 728 |  |  | 14.685 | [7 empty] | MLV 2 | 418.6 | AGM 3 | 2358.35 | 0.69 | 0.54 | 1.21 | 4.29 | 1.22 | 3600 | 40.91 | 40.79 | 33.6865 | -118.0063 | 72.719 | 3.0D 50.6 deg right turn sag bend
GWD 3610 | Girth Weld |  | 8306.12 | 40.91 | 0.219 | 42000 | ERW | 6.625 | 728 | [10 empty] | MLV 2 | 419.14 | AGM 3 | 2357.81 | 1.22 | 40.91 | 4.29 | 1.22 | 40.91 | 3610 | 40.79 | 40.64 | 33.6865 | -118.0063 | 72.587
GWD 3620 | Girth Weld |  | 8347.03 | 40.78 | 0.219 | 42000 | ERW | 6.625 | 728 | [10 empty] | MLV 2 | 460.05 | AGM 3 | 2316.91 | 40.91 | 40.79 | 1.22 | 40.91 | 40.79 | 3620 | 40.64 | 40.91 | 33.6866 | -118.0063 | 72.86
GWD 3630 | Girth Weld |  | 8387.82 | 40.64 | 0.219 | 42000 | ERW | 6.625 | 728 | [10 empty] | MLV 2 | 500.83 | AGM 3 | 2276.12 | 40.79 | 40.64 | 40.91 | 40.79 | 40.64 | 3630 | 40.91 | 40.98 | 33.6867 | -118.0063 | 72.895
GWD 3640 | Girth Weld |  | 8428.46 | 40.91 | 0.219 | 42000 | ERW | 6.625 | 728 | [10 empty] | MLV 2 | 541.47 | AGM 3 | 2235.48 | 40.64 | 40.91 | 40.79 | 40.64 | 40.91 | 3640 | 40.98 | 40.91 | 33.6868 | -118.0063 | 73.74
GWD 3650 | Girth Weld |  | 8469.37 | 40.98 | 0.219 | 42000 | ERW | 6.625 | 728 | [10 empty] | MLV 2 | 582.39 | AGM 3 | 2194.57 | 40.91 | 40.98 | 40.64 | 40.91 | 40.98 | 3650 | 40.91 | 40.97 | 33.6869 | -118.0063 | 73.51
GWD 3660 | Girth Weld |  | 8510.35 | 40.91 | 0.219 | 42000 | ERW | 6.625 | 728 | [10 empty] | MLV 2 | 623.37 | AGM 3 | 2153.58 | 40.98 | 40.91 | 40.91 | 40.98 | 40.91 | 3660 | 40.97 | 40.93 | 33.687 | -118.0063 | 73.415
GWD 3670 | Girth Weld |  | 8551.26 | 40.97 | 0.219 | 42000 | ERW | 6.625 | 728 | [10 empty] | MLV 2 | 664.28 | AGM 3 | 2112.67 | 40.91 | 40.97 | 40.98 | 40.91 | 40.97 | 3670 | 40.93 | 40.8 | 33.6871 | -118.0063 | 72.179
GWD 3680 | Girth Weld |  | 8592.24 | 40.93 | 0.219 | 42000 | ERW | 6.625 | 728 | [10 empty] | MLV 2 | 705.25 | AGM 3 | 2071.7 | 40.97 | 40.93 | 40.91 | 40.97 | 40.93 | 3680 | 40.8 | 40.75 | 33.6872 | -118.0063 | 71.236
GWD 3690 | Girth Weld |  | 8633.17 | 40.8 | 0.219 | 42000 | ERW | 6.625 | 728 | [10 empty] | MLV 2 | 746.18 | AGM 3 | 2030.77 | 40.93 | 40.8 | 40.97 | 40.93 | 40.8 | 3690 | 40.75 | 40.4 | 33.6873 | -118.0063 | 70.144
GWD 3700 | Girth Weld |  | 8673.97 | 40.76 | 0.219 | 42000 | ERW | 6.625 | 728 | [10 empty] | MLV 2 | 786.99 | AGM 3 | 1989.97 | 40.8 | 40.75 | 40.93 | 40.8 | 40.75 | 3700 | 40.4 | 39.82 | 33.6875 | -118.0063 | 69.295
GWD 3710 | Girth Weld |  | 8714.72 | 40.4 | 0.219 | 42000 | ERW | 6.625 | 728 | [10 empty] | MLV 2 | 827.74 | AGM 3 | 1949.21 | 40.75 | 40.4 | 40.8 | 40.75 | 40.4 | 3710 | 39.82 | 40.79 | 33.6876 | -118.0063 | 68.465
GWD 3720 | Girth Weld |  | 8755.12 | 39.82 | 0.219 | 42000 | ERW | 6.625 | 728 | [10 empty] | MLV 2 | 868.14 | AGM 3 | 1908.81 | 40.4 | 39.82 | 40.75 | 40.4 | 39.82 | 3720 | 40.79 | 40.93 | 33.6877 | -118.0063 | 68.243
GWD 3730 | Girth Weld |  | 8794.94 | 40.79 | 0.219 | 42000 | ERW | 6.625 | 728 | [10 empty] | MLV 2 | 907.96 | AGM 3 | 1868.99 | 39.82 | 40.79 | 40.4 | 39.82 | 40.79 | 3730 | 40.93 | 40.99 | 33.6878 | -118.0063 | 67.314
GWD 3740 | Girth Weld |  | 8835.73 | 40.94 | 0.219 | 42000 | ERW | 6.625 | 728 | [10 empty] | MLV 2 | 948.75 | AGM 3 | 1828.2 | 40.79 | 40.93 | 39.82 | 40.79 | 40.93 | 3740 | 40.99 | 40.91 | 33.6879 | -118.0063 | 65.53
GWD 3750 | Girth Weld |  | 8876.67 | 40.99 | 0.219 | 42000 | ERW | 6.625 | 728 | [10 empty] | MLV 2 | 989.68 | AGM 3 | 1787.27 | 40.93 | 40.99 | 40.79 | 40.93 | 40.99 | 3750 | 40.91 | 40.99 | 33.688 | -118.0063 | 65.394
GWD 3760 | Girth Weld |  | 8917.66 | 40.91 | 0.219 | 42000 | ERW | 6.625 | 728 | [10 empty] | MLV 2 | 1030.68 | AGM 3 | 1746.28 | 40.99 | 40.91 | 40.93 | 40.99 | 40.91 | 3760 | 40.99 | 40.82 | 33.6881 | -118.0063 | 64.747
GWD 3770 | Girth Weld |  | 8958.57 | 40.99 | 0.219 | 42000 | ERW | 6.625 | 728 | [10 empty] | MLV 2 | 1071.59 | AGM 3 | 1705.36 | 40.91 | 40.99 | 40.99 | 40.91 | 40.99 | 3770 | 40.82 | 41.02 | 33.6882 | -118.0063 | 64.416
GWD 3780 | Girth Weld |  | 8999.56 | 40.82 | 0.219 | 42000 | ERW | 6.625 | 728 | [10 empty] | MLV 2 | 1112.58 | AGM 3 | 1664.38 | 40.99 | 40.82 | 40.91 | 40.99 | 40.82 | 3780 | 41.02 | 40.81 | 33.6883 | -118.0063 | 63.736
GWD 3790 | Girth Weld |  | 9040.38 | 41.02 | 0.219 | 42000 | ERW | 6.625 | 728 | [10 empty] | MLV 2 | 1153.4 | AGM 3 | 1623.55 | 40.82 | 41.02 | 40.99 | 40.82 | 41.02 | 3790 | 40.81 | 40.88 | 33.6885 | -118.0063 | 62.582
GWD 3800 | Girth Weld |  | 9081.4 | 40.81 | 0.219 | 42000 | ERW | 6.625 | 728 | [10 empty] | MLV 2 | 1194.42 | AGM 3 | 1582.53 | 41.02 | 40.81 | 40.82 | 41.02 | 40.81 | 3800 | 40.88 | 40.88 | 33.6886 | -118.0063 | 61.121
GWD 3810 | Girth Weld |  | 9122.21 | 40.88 | 0.219 | 42000 | ERW | 6.625 | 728 | [10 empty] | MLV 2 | 1235.22 | AGM 3 | 1541.73 | 40.81 | 40.88 | 41.02 | 40.81 | 40.88 | 3810 | 40.88 | 40.88 | 33.6887 | -118.0063 | 59.087
GWD 3820 | Girth Weld |  | 9163.09 | 40.88 | 0.219 | 42000 | ERW | 6.625 | 728 | [10 empty] | MLV 2 | 1276.11 | AGM 3 | 1500.84 | 40.88 | 40.88 | 40.81 | 40.88 | 40.88 | 3820 | 40.88 | 39.8 | 33.6888 | -118.0063 | 60.264
GWD 3830 | Girth Weld |  | 9203.97 | 40.88 | 0.219 | 42000 | ERW | 6.625 | 728 | [10 empty] | MLV 2 | 1316.99 | AGM 3 | 1459.96 | 40.88 | 40.88 | 40.88 | 40.88 | 40.88 | 3830 | 39.8 | 40.97 | 33.6889 | -118.0063 | 62.394
GWD 3840 | Girth Weld |  | 9244.86 | 39.8 | 0.219 | 42000 | ERW | 6.625 | 728 | [10 empty] | MLV 2 | 1357.87 | AGM 3 | 1419.08 | 40.88 | 39.8 | 40.88 | 40.88 | 39.8 | 3840 | 40.97 | 40.91 | 33.689 | -118.0064 | 63.179
GWD 3850 | Girth Weld |  | 9284.66 | 40.96 | 0.219 | 42000 | ERW | 6.625 | 728 | [10 empty] | MLV 2 | 1397.67 | AGM 3 | 1379.28 | 39.8 | 40.97 | 40.88 | 39.8 | 40.97 | 3850 | 40.91 | 40.78 | 33.6891 | -118.0064 | 63.442
GWD 3860 | Girth Weld |  | 9325.62 | 40.91 | 0.219 | 42000 | ERW | 6.625 | 728 | [10 empty] | MLV 2 | 1438.64 | AGM 3 | 1338.31 | 40.97 | 40.91 | 39.8 | 40.97 | 40.91 | 3860 | 40.78 | 40.64 | 33.6892 | -118.0064 | 63.666
GWD 3870 | Girth Weld |  | 9366.54 | 40.78 | 0.219 | 42000 | ERW | 6.625 | 728 | [10 empty] | MLV 2 | 1479.55 | AGM 3 | 1297.4 | 40.91 | 40.78 | 40.97 | 40.91 | 40.78 | 3870 | 40.64 | 40.91 | 33.6893 | -118.0064 | 64.242
GWD 3880 | Girth Weld |  | 9407.32 | 40.64 | 0.219 | 42000 | ERW | 6.625 | 728 | [10 empty] | MLV 2 | 1520.33 | AGM 3 | 1256.62 | 40.78 | 40.64 | 40.91 | 40.78 | 40.64 | 3880 | 40.91 | 40.76 | 33.6895 | -118.0064 | 64.356
GWD 3890 | Girth Weld |  | 9447.96 | 40.92 | 0.219 | 42000 | ERW | 6.625 | 728 | [10 empty] | MLV 2 | 1560.97 | AGM 3 | 1215.98 | 40.64 | 40.91 | 40.78 | 40.64 | 40.91 | 3890 | 40.76 | 40.93 | 33.6896 | -118.0064 | 65.281
GWD 3900 | Girth Weld |  | 9488.87 | 40.76 | 0.219 | 42000 | ERW | 6.625 | 728 | [10 empty] | MLV 2 | 1601.89 | AGM 3 | 1175.07 | 40.91 | 40.76 | 40.64 | 40.91 | 40.76 | 3900 | 40.93 | 40.86 | 33.6897 | -118.0064 | 65.684
GWD 3910 | Girth Weld |  | 9529.64 | 40.93 | 0.219 | 42000 | ERW | 6.625 | 728 | [10 empty] | MLV 2 | 1642.65 | AGM 3 | 1134.3 | 40.76 | 40.93 | 40.91 | 40.76 | 40.93 | 3910 | 40.86 | 40.8 | 33.6898 | -118.0064 | 65.915
GWD 3920 | Girth Weld |  | 9570.57 | 40.85 | 0.219 | 42000 | ERW | 6.625 | 728 | [10 empty] | MLV 2 | 1683.58 | AGM 3 | 1093.37 | 40.93 | 40.86 | 40.76 | 40.93 | 40.86 | 3920 | 40.8 | 40.8 | 33.6899 | -118.0064 | 66.694
GWD 3930 | Girth Weld |  | 9611.42 | 40.8 | 0.219 | 42000 | ERW | 6.625 | 728 | [10 empty] | MLV 2 | 1724.44 | AGM 3 | 1052.51 | 40.86 | 40.8 | 40.93 | 40.86 | 40.8 | 3930 | 40.8 | 40.85 | 33.69 | -118.0064 | 66.228
GWD 3940 | Girth Weld |  | 9652.22 | 40.8 | 0.219 | 42000 | ERW | 6.625 | 728 | [10 empty] | MLV 2 | 1765.24 | AGM 3 | 1011.72 | 40.8 | 40.8 | 40.86 | 40.8 | 40.8 | 3940 | 40.85 | 40.97 | 33.6901 | -118.0064 | 66.583
GWD 3950 | Girth Weld |  | 9693.02 | 40.85 | 0.219 | 42000 | ERW | 6.625 | 728 | [10 empty] | MLV 2 | 1806.04 | AGM 3 | 970.92 | 40.8 | 40.85 | 40.8 | 40.8 | 40.85 | 3950 | 40.97 | 40.9 | 33.6902 | -118.0064 | 66.299
GWD 3960 | Girth Weld |  | 9733.87 | 40.97 | 0.219 | 42000 | ERW | 6.625 | 728 | [10 empty] | MLV 2 | 1846.88 | AGM 3 | 930.07 | 40.85 | 40.97 | 40.8 | 40.85 | 40.97 | 3960 | 40.9 | 40.82 | 33.6903 | -118.0064 | 65.538
GWD 3970 | Girth Weld |  | 9774.84 | 40.9 | 0.219 | 42000 | ERW | 6.625 | 728 | [10 empty] | MLV 2 | 1887.86 | AGM 3 | 889.1 | 40.97 | 40.9 | 40.85 | 40.97 | 40.9 | 3970 | 40.82 | 40.89 | 33.6905 | -118.0064 | 63.956
GWD 3980 | Girth Weld |  | 9815.74 | 40.82 | 0.219 | 42000 | ERW | 6.625 | 728 | [10 empty] | MLV 2 | 1928.75 | AGM 3 | 848.2 | 40.9 | 40.82 | 40.97 | 40.9 | 40.82 | 3980 | 40.89 | 40.94 | 33.6906 | -118.0064 | 62.72
GWD 3990 | Girth Weld |  | 9856.55 | 19.39 | 0.219 | 42000 | ERW | 6.625 | 728 | [10 empty] | MLV 2 | 1969.57 | AGM 3 | 807.38 | 40.82 | 40.89 | 40.9 | 40.82 | 40.89 | 3990 | 40.94 | 40.52 | 33.6907 | -118.0064 | 62.845
PMA 13 | Pipe Mill | Ext | 9875.94 | 21.51 | 0.219 | 42000 | ERW | 6.625 | 728 | 11.3278 | 0.025 | 0.712 | 0.639 | 6:01 | [5 empty] | MLV 2 | 1988.95 | AGM 3 | 788 | 19.39 | 21.51 | 40.9 | 40.82 | 40.89 | 3990 | 40.94 | 40.52 | 33.6907 | -118.0064 | 62.649
GWD 4000 | Girth Weld |  | 9897.45 | 40.94 | 0.219 | 42000 | ERW | 6.625 | 728 | [10 empty] | MLV 2 | 2010.46 | AGM 3 | 766.49 | 40.89 | 40.94 | 40.82 | 40.89 | 40.94 | 4000 | 40.52 | 40.88 | 33.6908 | -118.0064 | 61.527
GWD 4010 | Girth Weld |  | 9938.39 | 40.52 | 0.219 | 42000 | ERW | 6.625 | 728 | [10 empty] | MLV 2 | 2051.4 | AGM 3 | 725.55 | 40.94 | 40.52 | 40.89 | 40.94 | 40.52 | 4010 | 40.88 | 40.93 | 33.6909 | -118.0064 | 59.707
GWD 4020 | Girth Weld |  | 9978.91 | 40.88 | 0.219 | 42000 | ERW | 6.625 | 728 | [10 empty] | MLV 2 | 2091.92 | AGM 3 | 685.03 | 40.52 | 40.88 | 40.94 | 40.52 | 40.88 | 4020 | 40.93 | 40.81 | 33.691 | -118.0064 | 58.27
GWD 4030 | Girth Weld |  | 10019.79 | 40.93 | 0.219 | 42000 | ERW | 6.625 | 728 | [10 empty] | MLV 2 | 2132.8 | AGM 3 | 644.15 | 40.88 | 40.93 | 40.52 | 40.88 | 40.93 | 4030 | 40.81 | 40.88 | 33.6911 | -118.0064 | 57.79
GWD 4040 | Girth Weld |  | 10060.72 | 40.81 | 0.219 | 42000 | ERW | 6.625 | 728 | [10 empty] | MLV 2 | 2173.73 | AGM 3 | 603.22 | 40.93 | 40.81 | 40.88 | 40.93 | 40.81 | 4040 | 40.88 | 40.91 | 33.6912 | -118.0064 | 56.927
GWD 4050 | Girth Weld |  | 10101.53 | 40.88 | 0.219 | 42000 | ERW | 6.625 | 728 | [10 empty] | MLV 2 | 2214.55 | AGM 3 | 562.41 | 40.81 | 40.88 | 40.93 | 40.81 | 40.88 | 4050 | 40.91 | 40.89 | 33.6913 | -118.0064 | 56.726
GWD 4060 | Girth Weld |  | 10142.41 | 40.91 | 0.219 | 42000 | ERW | 6.625 | 728 | [10 empty] | MLV 2 | 2255.42 | AGM 3 | 521.53 | 40.88 | 40.91 | 40.81 | 40.88 | 40.91 | 4060 | 40.89 | 40.9 | 33.6915 | -118.0064 | 56.534
GWD 4070 | Girth Weld |  | 10183.32 | 40.89 | 0.219 | 42000 | ERW | 6.625 | 728 | [10 empty] | MLV 2 | 2296.33 | AGM 3 | 480.62 | 40.91 | 40.89 | 40.88 | 40.91 | 40.89 | 4070 | 40.9 | 40.54 | 33.6916 | -118.0064 | 56.606
GWD 4080 | Girth Weld |  | 10224.21 | 40.9 | 0.219 | 42000 | ERW | 6.625 | 728 | [10 empty] | MLV 2 | 2337.22 | AGM 3 | 439.73 | 40.89 | 40.9 | 40.91 | 40.89 | 40.9 | 4080 | 40.54 | 40.89 | 33.6917 | -118.0064 | 56.093
GWD 4090 | Girth Weld |  | 10265.11 | 40.54 | 0.219 | 42000 | ERW | 6.625 | 728 | [10 empty] | MLV 2 | 2378.13 | AGM 3 | 398.82 | 40.9 | 40.54 | 40.89 | 40.9 | 40.54 | 4090 | 40.89 | 40.84 | 33.6918 | -118.0064 | 54.096
GWD 4100 | Girth Weld |  | 10305.66 | 40.89 | 0.219 | 42000 | ERW | 6.625 | 728 | [10 empty] | MLV 2 | 2418.67 | AGM 3 | 358.28 | 40.54 | 40.89 | 40.9 | 40.54 | 40.89 | 4100 | 40.84 | 40.79 | 33.6919 | -118.0064 | 55.165
GWD 4110 | Girth Weld |  | 10346.55 | 40.85 | 0.219 | 42000 | ERW | 6.625 | 728 | [10 empty] | MLV 2 | 2459.56 | AGM 3 | 317.39 | 40.89 | 40.84 | 40.54 | 40.89 | 40.84 | 4110 | 40.79 | 40.85 | 33.692 | -118.0064 | 57.372
GWD 4120 | Girth Weld |  | 10387.39 | 40.41 | 0.219 | 42000 | ERW | 6.625 | 728 | [10 empty] | MLV 2 | 2500.41 | AGM 3 | 276.54 | 40.84 | 40.79 | 40.89 | 40.84 | 40.79 | 4120 | 40.85 | 40.94 | 33.6921 | -118.0064 | 57.911
PMA 14 | Pipe Mill | Ext | 10427.81 | 0.38 | 0.219 | 42000 | ERW | 6.625 | 728 | 10.6024 | 0.023 | 0.686 | 0.661 | 1:17 | [5 empty] | MLV 2 | 2540.82 | AGM 3 | 236.13 | 40.42 | 0.38 | 40.89 | 40.84 | 40.79 | 4120 | 40.85 | 40.94 | 33.6922 | -118.0064 | 58.275
GWD 4130 | Girth Weld |  | 10428.19 | 40.85 | 0.219 | 42000 | ERW | 6.625 | 728 | [10 empty] | MLV 2 | 2541.2 | AGM 3 | 235.75 | 40.79 | 40.85 | 40.84 | 40.79 | 40.85 | 4130 | 40.94 | 40.93 | 33.6922 | -118.0064 | 58.275
GWD 4140 | Girth Weld |  | 10469.04 | 40.94 | 0.219 | 42000 | ERW | 6.625 | 728 | [10 empty] | MLV 2 | 2582.05 | AGM 3 | 194.9 | 40.85 | 40.94 | 40.79 | 40.85 | 40.94 | 4140 | 40.93 | 40.85 | 33.6923 | -118.0064 | 58.842
GWD 4150 | Girth Weld |  | 10509.97 | 40.93 | 0.219 | 42000 | ERW | 6.625 | 728 | [10 empty] | MLV 2 | 2622.99 | AGM 3 | 153.96 | 40.94 | 40.93 | 40.85 | 40.94 | 40.93 | 4150 | 40.85 | 39.95 | 33.6925 | -118.0064 | 59.193
GWD 4160 | Girth Weld |  | 10550.91 | 40.85 | 0.219 | 42000 | ERW | 6.625 | 728 | [10 empty] | MLV 2 | 2663.92 | AGM 3 | 113.03 | 40.93 | 40.85 | 40.94 | 40.93 | 40.85 | 4160 | 39.95 | 40.91 | 33.6926 | -118.0064 | 59.783
GWD 4170 | Girth Weld |  | 10591.76 | 39.95 | 0.219 | 42000 | ERW | 6.625 | 728 | [10 empty] | MLV 2 | 2704.77 | AGM 3 | 72.18 | 40.85 | 39.95 | 40.93 | 40.85 | 39.95 | 4170 | 40.91 | 40.95 | 33.6927 | -118.0064 | 60.719
GWD 4180 | Girth Weld |  | 10631.71 | 32.23 | 0.219 | 42000 | ERW | 6.625 | 728 | [10 empty] | MLV 2 | 2744.72 | AGM 3 | 32.23 | 39.95 | 40.91 | 40.85 | 39.95 | 40.91 | 4180 | 40.95 | 40.97 | 33.6928 | -118.0064 | 60.363
AGM 2 | Above Ground Marker |  | 10663.94 | 8.68 | 0.219 | 42000 | ERW | 6.625 | 728 | [10 empty] | MLV 2 | 2776.95 | AGM 4 | 2712.04 | 32.23 | 8.68 | 40.85 | 39.95 | 40.91 | 4180 | 40.95 | 40.97 | 33.6929 | -118.0064 | 60.721 | AGM 3 9' East of Curb - Located in Goldenwest St
GWD 4190 | Girth Weld |  | 10672.61 | 40.95 | 0.219 | 42000 | ERW | 6.625 | 728 | [10 empty] | AGM 3 | 8.68 | AGM 4 | 2703.36 | 40.91 | 40.95 | 39.95 | 40.91 | 40.95 | 4190 | 40.97 | 40.79 | 33.6929 | -118.0064 | 60.854
GWD 4200 | Girth Weld |  | 10713.56 | 40.97 | 0.219 | 42000 | ERW | 6.625 | 728 | [10 empty] | AGM 3 | 49.62 | AGM 4 | 2662.42 | 40.95 | 40.97 | 40.91 | 40.95 | 40.97 | 4200 | 40.79 | 40.34 | 33.693 | -118.0064 | 60.864
GWD 4210 | Girth Weld |  | 10754.54 | 26.37 | 0.219 | 42000 | ERW | 6.625 | 728 | [10 empty] | AGM 3 | 90.6 | AGM 4 | 2621.44 | 40.97 | 40.79 | 40.95 | 40.97 | 40.79 | 4210 | 40.34 | 40.82 | 33.6931 | -118.0064 | 60.471
CLS 50 | Cluster | Ext | 10780.91 | 0.81 | 0.219 | 42000 | ERW | 6.625 | 728 | 13.1763 | 0.029 | 4.552 | 1.017 | 5:57 | 3169 | 0.31906 | 8 | 4.55 | 3250 | AGM 3 | 116.97 | AGM 4 | 2595.07 | 26.37 | 14.42 | 40.95 | 40.97 | 40.79 | 4210 | 40.34 | 40.82 | 33.6932 | -118.0064 | 59.803 | CLS C
DMA 323 | Metal Loss | Ext | 10781.71 | 0.14 | 0.219 | 42000 | ERW | 6.625 | 728 | 19.5454 | 0.043 | 0.524 | 0.549 | 5:33 | 3401 | 0.2973 | 20 | 0.52 | 3393 | AGM 3 | 117.78 | AGM 4 | 2594.26 | 27.18 | 13.61 | 40.95 | 40.97 | 40.79 | 4210 | 40.34 | 40.82 | 33.6932 | -118.0064 | 59.788
DMA 324 | Metal Loss | Ext | 10781.85 | 9.26 | 0.219 | 42000 | ERW | 6.625 | 728 | 10.0337 | 0.022 | 0.374 | 0.662 | 5:39 | 3429 | 0.29487 | 10 | 0.37 | 3427 | AGM 3 | 117.91 | AGM 4 | 2594.13 | 27.31 | 13.48 | 40.95 | 40.97 | 40.79 | 4210 | 40.34 | 40.82 | 33.6932 | -118.0064 | 59.786
DMA 325 | Metal Loss | Ext | 10791.11 | 4.21 | 0.219 | 42000 | ERW | 6.625 | 728 | 11.1702 | 0.024 | 0.661 | 0.546 | 5:52 | 3408 | 0.29669 | 11 | 0.66 | 3402 | AGM 3 | 127.17 | AGM 4 | 2584.87 | 36.58 | 4.21 | 40.95 | 40.97 | 40.79 | 4210 | 40.34 | 40.82 | 33.6932 | -118.0064 | 59.739
GWD 4220 | Girth Weld |  | 10795.33 | 40.34 | 0.219 | 42000 | ERW | 6.625 | 728 | [10 empty] | AGM 3 | 131.39 | AGM 4 | 2580.65 | 40.79 | 40.34 | 40.97 | 40.79 | 40.34 | 4220 | 40.82 | 40.79 | 33.6932 | -118.0064 | 59.759
GWD 4230 | Girth Weld |  | 10835.66 | 40.82 | 0.219 | 42000 | ERW | 6.625 | 728 | [10 empty] | AGM 3 | 171.73 | AGM 4 | 2540.31 | 40.34 | 40.82 | 40.79 | 40.34 | 40.82 | 4230 | 40.79 | 40.82 | 33.6933 | -118.0064 | 59.554
GWD 4240 | Girth Weld |  | 10876.48 | 40.79 | 0.219 | 42000 | ERW | 6.625 | 728 | [10 empty] | AGM 3 | 212.55 | AGM 4 | 2499.49 | 40.82 | 40.79 | 40.34 | 40.82 | 40.79 | 4240 | 40.82 | 40.81 | 33.6935 | -118.0064 | 60.006
GWD 4250 | Girth Weld |  | 10917.27 | 40.82 | 0.219 | 42000 | ERW | 6.625 | 728 | [10 empty] | AGM 3 | 253.33 | AGM 4 | 2458.71 | 40.79 | 40.82 | 40.82 | 40.79 | 40.82 | 4250 | 40.81 | 40.66 | 33.6936 | -118.0064 | 60.978
GWD 4260 | Girth Weld |  | 10958.09 | 40.81 | 0.219 | 42000 | ERW | 6.625 | 728 | [10 empty] | AGM 3 | 294.15 | AGM 4 | 2417.89 | 40.82 | 40.81 | 40.79 | 40.82 | 40.81 | 4260 | 40.66 | 29.09 | 33.6937 | -118.0064 | 62.536
GWD 4270 | Girth Weld |  | 10998.9 | 40.67 | 0.219 | 42000 | ERW | 6.625 | 728 | [10 empty] | AGM 3 | 334.96 | AGM 4 | 2377.08 | 40.81 | 40.66 | 40.82 | 40.81 | 40.66 | 4270 | 29.09 | 2.42 | 33.6938 | -118.0064 | 63.345
GWD 4280 | Girth Weld |  | 11039.56 | 29.09 | 0.219 | 42000 | ERW | 6.625 | 728 | [10 empty] | AGM 3 | 375.63 | AGM 4 | 2336.42 | 40.66 | 29.09 | 40.81 | 40.66 | 29.09 | 4280 | 2.42 | 3.45 | 33.6939 | -118.0064 | 62.899
GWD 4290 | Girth Weld |  | 11068.65 | 1.28 | 0.219 | 42000 | ERW | 6.625 | 728 | [10 empty] | AGM 3 | 404.71 | AGM 4 | 2307.33 | 29.09 | 2.42 | 40.66 | 29.09 | 2.42 | 4290 | 3.45 | 2.46 | 33.694 | -118.0064 | 60.585
BND 60 | Bend |  | 11069.93 | 1.15 | 0.219 | 42000 | ERW | 6.625 | 728 |  |  | 29.597 | [7 empty] | AGM 3 | 405.99 | AGM 4 | 2306.05 | 1.28 | 1.15 | 40.66 | 29.09 | 2.42 | 4290 | 3.45 | 2.46 | 33.694 | -118.0064 | 60.472 | 3.0D 91.2 deg right turn sag bend
GWD 4300 | Girth Weld |  | 11071.07 | 3.45 | 0.219 | 42000 | ERW | 6.625 | 728 | [10 empty] | AGM 3 | 407.13 | AGM 4 | 2304.91 | 2.42 | 3.45 | 29.09 | 2.42 | 3.45 | 4300 | 2.46 | 1.38 | 33.694 | -118.0064 | 60.408
GWD 4310 | Girth Weld |  | 11074.52 | 2.23 | 0.219 | 42000 | ERW | 6.625 | 728 | [10 empty] | AGM 3 | 410.59 | AGM 4 | 2301.45 | 3.45 | 2.46 | 2.42 | 3.45 | 2.46 | 4310 | 1.38 | 1.31 | 33.694 | -118.0064 | 60.271
BND 61 | Bend |  | 11076.75 | 0.23 | 0.219 | 42000 | ERW | 6.625 | 728 |  |  | 44.772 | [7 empty] | AGM 3 | 412.82 | AGM 4 | 2299.22 | 2.23 | 0.23 | 2.42 | 3.45 | 2.46 | 4310 | 1.38 | 1.31 | 33.694 | -118.0064 | 60.922 | 3.0D 91.5 deg left turn sag bend
GWD 4320 | Girth Weld |  | 11076.98 | 1.38 | 0.219 | 42000 | ERW | 6.625 | 728 | [10 empty] | AGM 3 | 413.05 | AGM 4 | 2298.99 | 2.46 | 1.38 | 3.45 | 2.46 | 1.38 | 4320 | 1.31 | 28.77 | 33.694 | -118.0064 | 61.083
GWD 4330 | Girth Weld |  | 11078.36 | 1.3 | 0.219 | 42000 | ERW | 6.625 | 728 | [10 empty] | AGM 3 | 414.42 | AGM 4 | 2297.62 | 1.38 | 1.31 | 2.46 | 1.38 | 1.31 | 4330 | 28.77 | 41.44 | 33.694 | -118.0064 | 61.764
GWD 4340 | Girth Weld |  | 11079.67 | 28.77 | 0.25 | 42000 | ERW | 6.625 | 728 | [10 empty] | AGM 3 | 415.73 | AGM 4 | 2296.31 | 1.31 | 28.77 | 1.38 | 1.31 | 28.77 | 4340 | 41.44 | 41.43 | 33.694 | -118.0064 | 61.762 | Estimated WT 0.250
GWD 4350 | Girth Weld |  | 11108.44 | 41.44 | 0.25 | 42000 | ERW | 6.625 | 728 | [10 empty] | AGM 3 | 444.5 | AGM 4 | 2267.54 | 28.77 | 41.44 | 1.31 | 28.77 | 41.44 | 4350 | 41.43 | 38.06 | 33.6941 | -118.0064 | 61.252
GWD 4360 | Girth Weld |  | 11149.88 | 41.43 | 0.25 | 42000 | ERW | 6.625 | 728 | [10 empty] | AGM 3 | 485.94 | AGM 4 | 2226.1 | 41.44 | 41.43 | 28.77 | 41.44 | 41.43 | 4360 | 38.06 | 41.37 | 33.6942 | -118.0064 | 61.136
GWD 4370 | Girth Weld |  | 11191.31 | 38.06 | 0.25 | 42000 | ERW | 6.625 | 728 | [10 empty] | AGM 3 | 527.37 | AGM 4 | 2184.67 | 41.43 | 38.06 | 41.44 | 41.43 | 38.06 | 4370 | 41.37 | 41.39 | 33.6943 | -118.0064 | 60.52
GWD 4380 | Girth Weld |  | 11229.37 | 41.36 | 0.25 | 42000 | ERW | 6.625 | 728 | [10 empty] | AGM 3 | 565.43 | AGM 4 | 2146.61 | 38.06 | 41.37 | 41.43 | 38.06 | 41.37 | 4380 | 41.39 | 41.43 | 33.6944 | -118.0064 | 60.099
GWD 4390 | Girth Weld |  | 11270.73 | 41.39 | 0.25 | 42000 | ERW | 6.625 | 728 | [10 empty] | AGM 3 | 606.8 | AGM 4 | 2105.24 | 41.37 | 41.39 | 38.06 | 41.37 | 41.39 | 4390 | 41.43 | 41.47 | 33.6945 | -118.0064 | 58.88
GWD 4400 | Girth Weld |  | 11312.12 | 41.44 | 0.25 | 42000 | ERW | 6.625 | 728 | [10 empty] | AGM 3 | 648.19 | AGM 4 | 2063.85 | 41.39 | 41.43 | 41.37 | 41.39 | 41.43 | 4400 | 41.47 | 41.27 | 33.6946 | -118.0064 | 57.924
GWD 4410 | Girth Weld |  | 11353.56 | 41.47 | 0.25 | 42000 | ERW | 6.625 | 728 | [10 empty] | AGM 3 | 689.62 | AGM 4 | 2022.42 | 41.43 | 41.47 | 41.39 | 41.43 | 41.47 | 4410 | 41.27 | 41.56 | 33.6947 | -118.0064 | 56.853
GWD 4420 | Girth Weld |  | 11395.03 | 41.27 | 0.25 | 42000 | ERW | 6.625 | 728 | [10 empty] | AGM 3 | 731.09 | AGM 4 | 1980.95 | 41.47 | 41.27 | 41.43 | 41.47 | 41.27 | 4420 | 41.56 | 42.22 | 33.6949 | -118.0065 | 56.572
GWD 4430 | Girth Weld |  | 11436.29 | 41.56 | 0.25 | 42000 | ERW | 6.625 | 728 | [10 empty] | AGM 3 | 772.35 | AGM 4 | 1939.69 | 41.27 | 41.56 | 41.47 | 41.27 | 41.56 | 4430 | 42.22 | 41.35 | 33.695 | -118.0065 | 55.523
GWD 4440 | Girth Weld |  | 11477.86 | 42.22 | 0.25 | 42000 | ERW | 6.625 | 728 | [10 empty] | AGM 3 | 813.92 | AGM 4 | 1898.12 | 41.56 | 42.22 | 41.27 | 41.56 | 42.22 | 4440 | 41.35 | 42.23 | 33.6951 | -118.0065 | 54.385
GWD 4450 | Girth Weld |  | 11520.08 | 41.35 | 0.25 | 42000 | ERW | 6.625 | 728 | [10 empty] | AGM 3 | 856.14 | AGM 4 | 1855.9 | 42.22 | 41.35 | 41.56 | 42.22 | 41.35 | 4450 | 42.23 | 41.99 | 33.6952 | -118.0065 | 53.579
GWD 4460 | Girth Weld |  | 11561.43 | 42.23 | 0.25 | 42000 | ERW | 6.625 | 728 | [10 empty] | AGM 3 | 897.49 | AGM 4 | 1814.55 | 41.35 | 42.23 | 42.22 | 41.35 | 42.23 | 4460 | 41.99 | 40.97 | 33.6953 | -118.0065 | 52.278
GWD 4470 | Girth Weld |  | 11603.66 | 41.99 | 0.25 | 42000 | ERW | 6.625 | 728 | [10 empty] | AGM 3 | 939.72 | AGM 4 | 1772.32 | 42.23 | 41.99 | 41.35 | 42.23 | 41.99 | 4470 | 40.97 | 41.5 | 33.6954 | -118.0065 | 51.159
GWD 4480 | Girth Weld |  | 11645.65 | 40.97 | 0.25 | 42000 | ERW | 6.625 | 728 | [10 empty] | AGM 3 | 981.71 | AGM 4 | 1730.33 | 41.99 | 40.97 | 42.23 | 41.99 | 40.97 | 4480 | 41.5 | 42.22 | 33.6955 | -118.0065 | 49.679
GWD 4490 | Girth Weld |  | 11686.62 | 41.5 | 0.25 | 42000 | ERW | 6.625 | 728 | [10 empty] | AGM 3 | 1022.68 | AGM 4 | 1689.36 | 40.97 | 41.5 | 41.99 | 40.97 | 41.5 | 4490 | 42.22 | 41.42 | 33.6957 | -118.0065 | 48.462
GWD 4500 | Girth Weld |  | 11728.12 | 42.22 | 0.25 | 42000 | ERW | 6.625 | 728 | [10 empty] | AGM 3 | 1064.18 | AGM 4 | 1647.86 | 41.5 | 42.22 | 40.97 | 41.5 | 42.22 | 4500 | 41.42 | 42.22 | 33.6958 | -118.0065 | 47.097
GWD 4510 | Girth Weld |  | 11770.34 | 41.42 | 0.25 | 42000 | ERW | 6.625 | 728 | [10 empty] | AGM 3 | 1106.41 | AGM 4 | 1605.64 | 42.22 | 41.42 | 41.5 | 42.22 | 41.42 | 4510 | 42.22 | 42.15 | 33.6959 | -118.0065 | 46.306
GWD 4520 | Girth Weld |  | 11811.76 | 42.22 | 0.25 | 42000 | ERW | 6.625 | 728 | [10 empty] | AGM 3 | 1147.82 | AGM 4 | 1564.22 | 41.42 | 42.22 | 42.22 | 41.42 | 42.22 | 4520 | 42.15 | 42.2 | 33.696 | -118.0065 | 45.26
GWD 4530 | Girth Weld |  | 11853.98 | 42.15 | 0.25 | 42000 | ERW | 6.625 | 728 | [10 empty] | AGM 3 | 1190.04 | AGM 4 | 1522 | 42.22 | 42.15 | 41.42 | 42.22 | 42.15 | 4530 | 42.2 | 42.25 | 33.6961 | -118.0065 | 44.719
GWD 4540 | Girth Weld |  | 11896.13 | 42.2 | 0.25 | 42000 | ERW | 6.625 | 728 | [10 empty] | AGM 3 | 1232.19 | AGM 4 | 1479.85 | 42.15 | 42.2 | 42.22 | 42.15 | 42.2 | 4540 | 42.25 | 42.19 | 33.6962 | -118.0065 | 44.239
GWD 4550 | Girth Weld |  | 11938.33 | 42.25 | 0.25 | 42000 | ERW | 6.625 | 728 | [10 empty] | AGM 3 | 1274.4 | AGM 4 | 1437.65 | 42.2 | 42.25 | 42.15 | 42.2 | 42.25 | 4550 | 42.19 | 42.23 | 33.6963 | -118.0065 | 44.023
GWD 4560 | Girth Weld |  | 11980.58 | 42.18 | 0.25 | 42000 | ERW | 6.625 | 728 | [10 empty] | AGM 3 | 1316.64 | AGM 4 | 1395.4 | 42.25 | 42.19 | 42.2 | 42.25 | 42.19 | 4560 | 42.23 | 41.38 | 33.6965 | -118.0065 | 43.099
GWD 4570 | Girth Weld |  | 12022.77 | 42.22 | 0.25 | 42000 | ERW | 6.625 | 728 | [10 empty] | AGM 3 | 1358.83 | AGM 4 | 1353.21 | 42.19 | 42.23 | 42.25 | 42.19 | 42.23 | 4570 | 41.38 | 42.21 | 33.6966 | -118.0065 | 43.789
GWD 4580 | Girth Weld |  | 12064.99 | 41.38 | 0.25 | 42000 | ERW | 6.625 | 728 | [10 empty] | AGM 3 | 1401.05 | AGM 4 | 1310.99 | 42.23 | 41.38 | 42.19 | 42.23 | 41.38 | 4580 | 42.21 | 41.44 | 33.6967 | -118.0065 | 45.73
GWD 4590 | Girth Weld |  | 12106.37 | 42.21 | 0.25 | 42000 | ERW | 6.625 | 728 | [10 empty] | AGM 3 | 1442.43 | AGM 4 | 1269.61 | 41.38 | 42.21 | 42.23 | 41.38 | 42.21 | 4590 | 41.44 | 40.13 | 33.6968 | -118.0065 | 46.243
GWD 4600 | Girth Weld |  | 12148.58 | 41.44 | 0.25 | 42000 | ERW | 6.625 | 728 | [10 empty] | AGM 3 | 1484.65 | AGM 4 | 1227.39 | 42.21 | 41.44 | 41.38 | 42.21 | 41.44 | 4600 | 40.13 | 41.41 | 33.6969 | -118.0065 | 46.304
GWD 4610 | Girth Weld |  | 12190.03 | 40.12 | 0.25 | 42000 | ERW | 6.625 | 728 | [10 empty] | AGM 3 | 1526.09 | AGM 4 | 1185.95 | 41.44 | 40.13 | 42.21 | 41.44 | 40.13 | 4610 | 41.41 | 42.22 | 33.697 | -118.0065 | 46.99
GWD 4620 | Girth Weld |  | 12230.15 | 41.41 | 0.25 | 42000 | ERW | 6.625 | 728 | [10 empty] | AGM 3 | 1566.21 | AGM 4 | 1145.83 | 40.13 | 41.41 | 41.44 | 40.13 | 41.41 | 4620 | 42.22 | 42.18 | 33.6971 | -118.0065 | 47.56
GWD 4630 | Girth Weld |  | 12271.56 | 42.22 | 0.25 | 42000 | ERW | 6.625 | 728 | [10 empty] | AGM 3 | 1607.62 | AGM 4 | 1104.42 | 41.41 | 42.22 | 40.13 | 41.41 | 42.22 | 4630 | 42.18 | 42.2 | 33.6973 | -118.0065 | 47.868
GWD 4640 | Girth Weld |  | 12313.78 | 42.18 | 0.25 | 42000 | ERW | 6.625 | 728 | [10 empty] | AGM 3 | 1649.84 | AGM 4 | 1062.2 | 42.22 | 42.18 | 41.41 | 42.22 | 42.18 | 4640 | 42.2 | 41.38 | 33.6974 | -118.0065 | 47.095
GWD 4650 | Girth Weld |  | 12355.96 | 42.2 | 0.25 | 42000 | ERW | 6.625 | 728 | [10 empty] | AGM 3 | 1692.03 | AGM 4 | 1020.02 | 42.18 | 42.2 | 42.22 | 42.18 | 42.2 | 4650 | 41.38 | 41.43 | 33.6975 | -118.0065 | 47.29
GWD 4660 | Girth Weld |  | 12398.16 | 41.38 | 0.25 | 42000 | ERW | 6.625 | 728 | [10 empty] | AGM 3 | 1734.22 | AGM 4 | 977.82 | 42.2 | 41.38 | 42.18 | 42.2 | 41.38 | 4660 | 41.43 | 40.44 | 33.6976 | -118.0065 | 48.827
GWD 4670 | Girth Weld |  | 12439.54 | 41.43 | 0.25 | 42000 | ERW | 6.625 | 728 | [10 empty] | AGM 3 | 1775.6 | AGM 4 | 936.44 | 41.38 | 41.43 | 42.2 | 41.38 | 41.43 | 4670 | 40.44 | 42.22 | 33.6977 | -118.0065 | 49.633
GWD 4680 | Girth Weld |  | 12480.97 | 40.44 | 0.25 | 42000 | ERW | 6.625 | 728 | [10 empty] | AGM 3 | 1817.04 | AGM 4 | 895 | 41.43 | 40.44 | 41.38 | 41.43 | 40.44 | 4680 | 42.22 | 41.32 | 33.6978 | -118.0065 | 49.727
GWD 4690 | Girth Weld |  | 12521.41 | 42.22 | 0.25 | 42000 | ERW | 6.625 | 728 | [10 empty] | AGM 3 | 1857.47 | AGM 4 | 854.57 | 40.44 | 42.22 | 41.43 | 40.44 | 42.22 | 4690 | 41.32 | 41.32 | 33.6979 | -118.0065 | 49.88
GWD 4700 | Girth Weld |  | 12563.63 | 41.32 | 0.25 | 42000 | ERW | 6.625 | 728 | [10 empty] | AGM 3 | 1899.69 | AGM 4 | 812.35 | 42.22 | 41.32 | 40.44 | 42.22 | 41.32 | 4700 | 41.32 | 41.43 | 33.698 | -118.0065 | 50.008
GWD 4710 | Girth Weld |  | 12604.95 | 41.32 | 0.25 | 42000 | ERW | 6.625 | 728 | [10 empty] | AGM 3 | 1941.02 | AGM 4 | 771.02 | 41.32 | 41.32 | 42.22 | 41.32 | 41.32 | 4710 | 41.43 | 40.41 | 33.6982 | -118.0065 | 50.11
GWD 4720 | Girth Weld |  | 12646.27 | 41.43 | 0.25 | 42000 | ERW | 6.625 | 728 | [10 empty] | AGM 3 | 1982.34 | AGM 4 | 729.71 | 41.32 | 41.43 | 41.32 | 41.32 | 41.43 | 4720 | 40.41 | 5.61 | 33.6983 | -118.0065 | 50.212
GWD 4730 | Girth Weld |  | 12687.7 | 40.41 | 0.25 | 42000 | ERW | 6.625 | 728 | [10 empty] | AGM 3 | 2023.77 | AGM 4 | 688.27 | 41.43 | 40.41 | 41.32 | 41.43 | 40.41 | 4730 | 5.61 | 17.24 | 33.6984 | -118.0065 | 50.044
GWD 4740 | Girth Weld |  | 12728.11 | 5.61 | 0.25 | 42000 | ERW | 6.625 | 728 | [10 empty] | AGM 3 | 2064.18 | AGM 4 | 647.86 | 40.41 | 5.61 | 41.43 | 40.41 | 5.61 | 4740 | 17.24 | 42.21 | 33.6985 | -118.0065 | 49.613
GWD 4750 | Girth Weld |  | 12733.72 | 17.24 | 0.25 | 42000 | ERW | 6.625 | 728 | [10 empty] | AGM 3 | 2069.79 | AGM 4 | 642.25 | 5.61 | 17.24 | 40.41 | 5.61 | 17.24 | 4750 | 42.21 | 41.89 | 33.6985 | -118.0065 | 49.482
GWD 4760 | Girth Weld |  | 12750.96 | 42.21 | 0.25 | 42000 | ERW | 6.625 | 728 | [10 empty] | AGM 3 | 2087.02 | AGM 4 | 625.02 | 17.24 | 42.21 | 5.61 | 17.24 | 42.21 | 4760 | 41.89 | 41.25 | 33.6986 | -118.0065 | 48.933
GWD 4770 | Girth Weld |  | 12793.17 | 41.89 | 0.25 | 42000 | ERW | 6.625 | 728 | [10 empty] | AGM 3 | 2129.23 | AGM 4 | 582.81 | 42.21 | 41.89 | 17.24 | 42.21 | 41.89 | 4770 | 41.25 | 41.42 | 33.6987 | -118.0065 | 47.768
GWD 4780 | Girth Weld |  | 12835.06 | 41.25 | 0.25 | 42000 | ERW | 6.625 | 728 | [10 empty] | AGM 3 | 2171.12 | AGM 4 | 540.92 | 41.89 | 41.25 | 42.21 | 41.89 | 41.25 | 4780 | 41.42 | 8.46 | 33.6988 | -118.0065 | 47.471
GWD 4790 | Girth Weld |  | 12876.3 | 41.42 | 0.25 | 42000 | ERW | 6.625 | 728 | [10 empty] | AGM 3 | 2212.37 | AGM 4 | 499.67 | 41.25 | 41.42 | 41.89 | 41.25 | 41.42 | 4790 | 8.46 | 42.12 | 33.6989 | -118.0065 | 47.413
GWD 4800 | Girth Weld |  | 12917.73 | 8.46 | 0.25 | 42000 | ERW | 6.625 | 728 | [10 empty] | AGM 3 | 2253.79 | AGM 4 | 458.25 | 41.42 | 8.46 | 41.25 | 41.42 | 8.46 | 4800 | 42.12 | 43.97 | 33.699 | -118.0065 | 48.269
GWD 4810 | Girth Weld |  | 12926.18 | 42.12 | 0.25 | 42000 | ERW | 6.625 | 728 | [10 empty] | AGM 3 | 2262.25 | AGM 4 | 449.79 | 8.46 | 42.12 | 41.42 | 8.46 | 42.12 | 4810 | 43.97 | 41.54 | 33.699 | -118.0065 | 48.269
GWD 4820 | Girth Weld |  | 12968.31 | 43.97 | 0.25 | 42000 | ERW | 6.625 | 728 | [10 empty] | AGM 3 | 2304.37 | AGM 4 | 407.67 | 42.12 | 43.97 | 8.46 | 42.12 | 43.97 | 4820 | 41.54 | 42.19 | 33.6992 | -118.0065 | 47.846
GWD 4830 | Girth Weld |  | 13012.28 | 41.54 | 0.25 | 42000 | ERW | 6.625 | 728 | [10 empty] | AGM 3 | 2348.34 | AGM 4 | 363.7 | 43.97 | 41.54 | 42.12 | 43.97 | 41.54 | 4830 | 42.19 | 42.87 | 33.6993 | -118.0065 | 47.579
GWD 4840 | Girth Weld |  | 13053.82 | 42.19 | 0.25 | 42000 | ERW | 6.625 | 728 | [10 empty] | AGM 3 | 2389.88 | AGM 4 | 322.16 | 41.54 | 42.19 | 43.97 | 41.54 | 42.19 | 4840 | 42.87 | 41.5 | 33.6994 | -118.0065 | 46.75
GWD 4850 | Girth Weld |  | 13096.01 | 42.87 | 0.25 | 42000 | ERW | 6.625 | 728 | [10 empty] | AGM 3 | 2432.07 | AGM 4 | 279.97 | 42.19 | 42.87 | 41.54 | 42.19 | 42.87 | 4850 | 41.5 | 42.23 | 33.6995 | -118.0065 | 46.378
GWD 4860 | Girth Weld |  | 13138.88 | 41.5 | 0.25 | 42000 | ERW | 6.625 | 728 | [10 empty] | AGM 3 | 2474.95 | AGM 4 | 237.09 | 42.87 | 41.5 | 42.19 | 42.87 | 41.5 | 4860 | 42.23 | 41.46 | 33.6996 | -118.0065 | 45.872
GWD 4870 | Girth Weld |  | 13180.38 | 42.23 | 0.25 | 42000 | ERW | 6.625 | 728 | [10 empty] | AGM 3 | 2516.44 | AGM 4 | 195.6 | 41.5 | 42.23 | 42.87 | 41.5 | 42.23 | 4870 | 41.46 | 42.2 | 33.6997 | -118.0065 | 45.39
GWD 4880 | Girth Weld |  | 13222.61 | 41.46 | 0.25 | 42000 | ERW | 6.625 | 728 | [10 empty] | AGM 3 | 2558.67 | AGM 4 | 153.37 | 42.23 | 41.46 | 41.5 | 42.23 | 41.46 | 4880 | 42.2 | 42.22 | 33.6998 | -118.0065 | 44.431
GWD 4890 | Girth Weld |  | 13264.07 | 42.2 | 0.25 | 42000 | ERW | 6.625 | 728 | [10 empty] | AGM 3 | 2600.13 | AGM 4 | 111.91 | 41.46 | 42.2 | 42.23 | 41.46 | 42.2 | 4890 | 42.22 | 42.19 | 33.7 | -118.0065 | 43.699
GWD 4900 | Girth Weld |  | 13306.27 | 42.22 | 0.25 | 42000 | ERW | 6.625 | 728 | [10 empty] | AGM 3 | 2642.33 | AGM 4 | 69.71 | 42.2 | 42.22 | 41.46 | 42.2 | 42.22 | 4900 | 42.19 | 41.48 | 33.7001 | -118.0065 | 42.909
GWD 4910 | Girth Weld |  | 13348.49 | 27.49 | 0.25 | 42000 | ERW | 6.625 | 728 | [10 empty] | AGM 3 | 2684.55 | AGM 4 | 27.49 | 42.22 | 42.19 | 42.2 | 42.22 | 42.19 | 4910 | 41.48 | 42.22 | 33.7002 | -118.0065 | 41.408
AGM 3 | Above Ground Marker |  | 13375.98 | 14.7 | 0.25 | 42000 | ERW | 6.625 | 728 | [10 empty] | AGM 3 | 2712.04 | AGM 5 | 2717.13 | 27.49 | 14.7 | 42.2 | 42.22 | 42.19 | 4910 | 41.48 | 42.22 | 33.7003 | -118.0065 | 40.626 | AGM 4 13' East of Curb - Located in Goldenwest St
GWD 4920 | Girth Weld |  | 13390.68 | 41.48 | 0.25 | 42000 | ERW | 6.625 | 728 | [10 empty] | AGM 4 | 14.7 | AGM 5 | 2702.43 | 42.19 | 41.48 | 42.22 | 42.19 | 41.48 | 4920 | 42.22 | 19.91 | 33.7003 | -118.0065 | 40.627
GWD 4930 | Girth Weld |  | 13432.16 | 42.22 | 0.25 | 42000 | ERW | 6.625 | 728 | [10 empty] | AGM 4 | 56.18 | AGM 5 | 2660.94 | 41.48 | 42.22 | 42.19 | 41.48 | 42.22 | 4930 | 19.91 | 10 | 33.7004 | -118.0065 | 39.974
GWD 4940 | Girth Weld |  | 13474.38 | 19.91 | 0.25 | 42000 | ERW | 6.625 | 728 | [10 empty] | AGM 4 | 98.4 | AGM 5 | 2618.73 | 42.22 | 19.91 | 41.48 | 42.22 | 19.91 | 4940 | 10 | 11.19 | 33.7005 | -118.0065 | 39.313
GWD 4950 | Girth Weld |  | 13494.29 | 9.99 | 0.25 | 42000 | ERW | 6.625 | 728 | [10 empty] | AGM 4 | 118.31 | AGM 5 | 2598.82 | 19.91 | 10 | 42.22 | 19.91 | 10 | 4950 | 11.19 | 41.33 | 33.7006 | -118.0065 | 38.944
GWD 4960 | Girth Weld |  | 13504.28 | 11.19 | 0.25 | 42000 | ERW | 6.625 | 728 | [10 empty] | AGM 4 | 128.3 | AGM 5 | 2588.82 | 10 | 11.19 | 19.91 | 10 | 11.19 | 4960 | 41.33 | 42.21 | 33.7006 | -118.0065 | 38.876
GWD 4970 | Girth Weld |  | 13515.47 | 41.33 | 0.25 | 42000 | ERW | 6.625 | 728 | [10 empty] | AGM 4 | 139.49 | AGM 5 | 2577.64 | 11.19 | 41.33 | 10 | 11.19 | 41.33 | 4970 | 42.21 | 40.48 | 33.7007 | -118.0065 | 38.693
GWD 4980 | Girth Weld |  | 13556.8 | 42.21 | 0.25 | 42000 | ERW | 6.625 | 728 | [10 empty] | AGM 4 | 180.82 | AGM 5 | 2536.3 | 41.33 | 42.21 | 11.19 | 41.33 | 42.21 | 4980 | 40.48 | 1.18 | 33.7008 | -118.0065 | 37.717
GWD 4990 | Girth Weld |  | 13599.01 | 40.48 | 0.25 | 42000 | ERW | 6.625 | 728 | [10 empty] | AGM 4 | 223.04 | AGM 5 | 2494.09 | 42.21 | 40.48 | 41.33 | 42.21 | 40.48 | 4990 | 1.18 | 4.67 | 33.7009 | -118.0065 | 35.56
GWD 5000 | Girth Weld |  | 13639.5 | 0.58 | 0.25 | 42000 | ERW | 6.625 | 728 | [10 empty] | AGM 4 | 263.52 | AGM 5 | 2453.61 | 40.48 | 1.18 | 42.21 | 40.48 | 1.18 | 5000 | 4.67 | 1.18 | 33.701 | -118.0065 | 34.926
BND 62 | Bend |  | 13640.08 | 0.6 | 0.25 | 42000 | ERW | 6.625 | 728 |  |  | 14.213 | [7 empty] | AGM 4 | 264.1 | AGM 5 | 2453.03 | 0.58 | 0.6 | 42.21 | 40.48 | 1.18 | 5000 | 4.67 | 1.18 | 33.701 | -118.0065 | 34.936 | 3.0D 49.0 deg left turn sag bend
GWD 5010 | Girth Weld |  | 13640.68 | 4.67 | 0.25 | 42000 | ERW | 6.625 | 728 | [10 empty] | AGM 4 | 264.7 | AGM 5 | 2452.42 | 1.18 | 4.67 | 40.48 | 1.18 | 4.67 | 5010 | 1.18 | 1.64 | 33.701 | -118.0065 | 34.971
GWD 5020 | Girth Weld |  | 13645.35 | 0.59 | 0.25 | 42000 | ERW | 6.625 | 728 | [10 empty] | AGM 4 | 269.37 | AGM 5 | 2447.75 | 4.67 | 1.18 | 1.18 | 4.67 | 1.18 | 5020 | 1.64 | 39.64 | 33.701 | -118.0065 | 35.283
BND 63 | Bend |  | 13645.94 | 0.59 | 0.25 | 42000 | ERW | 6.625 | 728 |  |  | 14.134 | [7 empty] | AGM 4 | 269.96 | AGM 5 | 2447.16 | 0.59 | 0.59 | 1.18 | 4.67 | 1.18 | 5020 | 1.64 | 39.64 | 33.701 | -118.0065 | 35.319 | 3.0D 50.9 deg right turn over bend
GWD 5030 | Girth Weld |  | 13646.53 | 1.64 | 0.25 | 42000 | ERW | 6.625 | 728 | [10 empty] | AGM 4 | 270.55 | AGM 5 | 2446.58 | 1.18 | 1.64 | 4.67 | 1.18 | 1.64 | 5030 | 39.64 | 26.48 | 33.701 | -118.0065 | 35.335
GWD 5040 | Girth Weld |  | 13648.17 | 39.63 | 0.25 | 42000 | SMLS | 6.625 | 728 | [10 empty] | AGM 4 | 272.19 | AGM 5 | 2444.94 | 1.64 | 39.64 | 1.18 | 1.64 | 39.64 | 5040 | 26.48 | 40.9 | 33.701 | -118.0065 | 35.329
GWD 5050 | Girth Weld |  | 13687.8 | 26.48 | 0.25 | 42000 | SMLS | 6.625 | 728 | [10 empty] | AGM 4 | 311.83 | AGM 5 | 2405.3 | 39.64 | 26.48 | 1.64 | 39.64 | 26.48 | 5050 | 40.9 | 44.67 | 33.7011 | -118.0065 | 33.489
GWD 5060 | Girth Weld |  | 13714.28 | 12.73 | 0.25 | 42000 | SMLS | 6.625 | 728 | [10 empty] | AGM 4 | 338.31 | AGM 5 | 2378.82 | 26.48 | 40.9 | 39.64 | 26.48 | 40.9 | 5060 | 44.67 | 44.15 | 33.7012 | -118.0065 | 32.124
PMA 15 | Pipe Mill | Ext | 13727.01 | 28.18 | 0.25 | 42000 | SMLS | 6.625 | 728 | 14.4541 | 0.036 | 0.662 | 0.635 | 6:44 | [5 empty] | AGM 4 | 351.03 | AGM 5 | 2366.1 | 12.72 | 28.18 | 39.64 | 26.48 | 40.9 | 5060 | 44.67 | 44.15 | 33.7012 | -118.0065 | 31.655
GWD 5070 | Girth Weld |  | 13755.19 | 4.22 | 0.25 | 42000 | SMLS | 6.625 | 728 | [10 empty] | AGM 4 | 379.21 | AGM 5 | 2337.92 | 40.9 | 44.67 | 26.48 | 40.9 | 44.67 | 5070 | 44.15 | 46.35 | 33.7013 | -118.0065 | 30.385
PMA 16 | Pipe Mill | Ext | 13759.41 | 1.63 | 0.25 | 42000 | SMLS | 6.625 | 728 | 15.248 | 0.038 | 0.415 | 0.532 | 10:22 | [5 empty] | AGM 4 | 383.43 | AGM 5 | 2333.7 | 4.22 | 40.45 | 26.48 | 40.9 | 44.67 | 5070 | 44.15 | 46.35 | 33.7013 | -118.0065 | 30.171
PMA 17 | Pipe Mill | Ext | 13761.04 | 0.15 | 0.25 | 42000 | SMLS | 6.625 | 728 | 10.7334 | 0.027 | 0.462 | 0.612 | 9:57 | [5 empty] | AGM 4 | 385.06 | AGM 5 | 2332.07 | 5.85 | 38.82 | 26.48 | 40.9 | 44.67 | 5070 | 44.15 | 46.35 | 33.7013 | -118.0065 | 30.089
PMA 18 | Pipe Mill | Ext | 13761.18 | 0.7 | 0.25 | 42000 | SMLS | 6.625 | 728 | 11.1596 | 0.028 | 0.645 | 0.605 | 9:28 | [5 empty] | AGM 4 | 385.2 | AGM 5 | 2331.92 | 6 | 38.68 | 26.48 | 40.9 | 44.67 | 5070 | 44.15 | 46.35 | 33.7013 | -118.0065 | 30.085
PMA 19 | Pipe Mill | Ext | 13761.88 | 1.81 | 0.25 | 42000 | SMLS | 6.625 | 728 | 15.0974 | 0.038 | 0.482 | 0.538 | 9:13 | [5 empty] | AGM 4 | 385.9 | AGM 5 | 2331.23 | 6.69 | 37.98 | 26.48 | 40.9 | 44.67 | 5070 | 44.15 | 46.35 | 33.7013 | -118.0065 | 30.051
PMA 20 | Pipe Mill | Ext | 13763.68 | 36.17 | 0.25 | 42000 | SMLS | 6.625 | 728 | 14.1559 | 0.035 | 0.531 | 0.584 | 3:10 | [5 empty] | AGM 4 | 387.71 | AGM 5 | 2329.42 | 8.5 | 36.17 | 26.48 | 40.9 | 44.67 | 5070 | 44.15 | 46.35 | 33.7013 | -118.0065 | 29.971
GWD 5080 | Girth Weld |  | 13799.86 | 7.85 | 0.25 | 42000 | SMLS | 6.625 | 728 | [10 empty] | AGM 4 | 423.88 | AGM 5 | 2293.25 | 44.67 | 44.15 | 40.9 | 44.67 | 44.15 | 5080 | 46.35 | 44.69 | 33.7014 | -118.0065 | 27.876
PMA 21 | Pipe Mill | Ext | 13807.7 | 0.67 | 0.25 | 42000 | SMLS | 6.625 | 728 | 14.5455 | 0.036 | 0.42 | 0.561 | 6:23 | [5 empty] | AGM 4 | 431.73 | AGM 5 | 2285.4 | 7.85 | 36.3 | 40.9 | 44.67 | 44.15 | 5080 | 46.35 | 44.69 | 33.7014 | -118.0065 | 27.355
PMA 22 | Pipe Mill | Ext | 13808.37 | 35.63 | 0.25 | 42000 | SMLS | 6.625 | 728 | 17.0345 | 0.043 | 0.397 | 0.521 | 4:39 | [5 empty] | AGM 4 | 432.39 | AGM 5 | 2284.73 | 8.51 | 35.64 | 40.9 | 44.67 | 44.15 | 5080 | 46.35 | 44.69 | 33.7014 | -118.0065 | 27.316
GWD 5090 | Girth Weld |  | 13844.01 | 46.35 | 0.25 | 42000 | SMLS | 6.625 | 728 | [10 empty] | AGM 4 | 468.03 | AGM 5 | 2249.1 | 44.15 | 46.35 | 44.67 | 44.15 | 46.35 | 5090 | 44.69 | 44.37 | 33.7015 | -118.0065 | 25.968
GWD 5100 | Girth Weld |  | 13890.35 | 44.69 | 0.25 | 42000 | SMLS | 6.625 | 728 | [10 empty] | AGM 4 | 514.38 | AGM 5 | 2202.75 | 46.35 | 44.69 | 44.15 | 46.35 | 44.69 | 5100 | 44.37 | 44.79 | 33.7017 | -118.0065 | 24.053
GWD 5110 | Girth Weld |  | 13935.05 | 44.37 | 0.25 | 42000 | SMLS | 6.625 | 728 | [10 empty] | AGM 4 | 559.07 | AGM 5 | 2158.06 | 44.69 | 44.37 | 46.35 | 44.69 | 44.37 | 5110 | 44.79 | 46.9 | 33.7018 | -118.0065 | 21.457
GWD 5120 | Girth Weld |  | 13979.42 | 44.79 | 0.25 | 42000 | SMLS | 6.625 | 728 | [10 empty] | AGM 4 | 603.44 | AGM 5 | 2113.69 | 44.37 | 44.79 | 44.69 | 44.37 | 44.79 | 5120 | 46.9 | 44.82 | 33.7019 | -118.0065 | 19.876
GWD 5130 | Girth Weld |  | 14024.21 | 46.9 | 0.25 | 42000 | SMLS | 6.625 | 728 | [10 empty] | AGM 4 | 648.23 | AGM 5 | 2068.89 | 44.79 | 46.9 | 44.37 | 44.79 | 46.9 | 5130 | 44.82 | 10.24 | 33.702 | -118.0065 | 17.085
GWD 5140 | Girth Weld |  | 14071.11 | 12.53 | 0.25 | 42000 | SMLS | 6.625 | 728 | [10 empty] | AGM 4 | 695.13 | AGM 5 | 2022 | 46.9 | 44.82 | 44.79 | 46.9 | 44.82 | 5140 | 10.24 | 22.58 | 33.7022 | -118.0065 | 13.615
PMA 23 | Pipe Mill | Ext | 14083.64 | 32.28 | 0.25 | 42000 | SMLS | 6.625 | 728 | 11.5046 | 0.029 | 1.553 | 1.223 | 12:16 | [5 empty] | AGM 4 | 707.66 | AGM 5 | 2009.46 | 12.53 | 32.28 | 44.79 | 46.9 | 44.82 | 5140 | 10.24 | 22.58 | 33.7022 | -118.0065 | 13.083
GWD 5150 | Girth Weld |  | 14115.92 | 10.24 | 0.25 | 42000 | SMLS | 6.625 | 728 | [10 empty] | AGM 4 | 739.95 | AGM 5 | 1977.18 | 44.82 | 10.24 | 46.9 | 44.82 | 10.24 | 5150 | 22.58 | 20.12 | 33.7023 | -118.0065 | 11.942
GWD 5160 | Girth Weld |  | 14126.16 | 0.41 | 0.25 | 42000 | SMLS | 6.625 | 728 | [10 empty] | AGM 4 | 750.18 | AGM 5 | 1966.94 | 10.24 | 22.58 | 44.82 | 10.24 | 22.58 | 5160 | 20.12 | 14.84 | 33.7023 | -118.0065 | 11.711
DMA 326 | Metal Loss | Ext | 14126.57 | 0.4 | 0.25 | 42000 | SMLS | 6.625 | 728 | 11.3064 | 0.028 | 0.528 | 0.606 | 8:33 | 3904 | 0.25899 | 11 | 0.53 | 3900 | AGM 4 | 750.59 | AGM 5 | 1966.53 | 0.41 | 22.17 | 44.82 | 10.24 | 22.58 | 5160 | 20.12 | 14.84 | 33.7023 | -118.0065 | 11.698
DNT 4 | Deformation |  | 14126.97 | 0.02 | 0.25 | 42000 | SMLS | 6.625 | 728 | 2.4944 | 0.165 | 4.152 | 2.581 | 11:22 | [5 empty] | AGM 4 | 750.99 | AGM 5 | 1966.13 | 0.81 | 21.77 | 44.82 | 10.24 | 22.58 | 5160 | 20.12 | 14.84 | 33.7023 | -118.0065 | 11.688 | Dent w/ Metal Loss¦On DMA
CLS 51 | Cluster | Ext | 14126.99 | 0.18 | 0.25 | 42000 | SMLS | 6.625 | 728 | 11.1276 | 0.028 | 2.548 | 3.465 | 9:39 | 3745 | 0.26999 | 8 | 2.55 | 3765 | AGM 4 | 751.01 | AGM 5 | 1966.11 | 0.83 | 21.75 | 44.82 | 10.24 | 22.58 | 5160 | 20.12 | 14.84 | 33.7023 | -118.0065 | 11.688 | CLS C ¦ On DNT
DMA 330 | Metal Loss | Ext | 14127.17 | 0.07 | 0.25 | 42000 | SMLS | 6.625 | 728 | 11.7364 | 0.029 | 0.545 | 0.572 | 5:59 | 3902 | 0.25913 | 12 | 0.54 | 3898 | AGM 4 | 751.19 | AGM 5 | 1965.93 | 1.01 | 21.57 | 44.82 | 10.24 | 22.58 | 5160 | 20.12 | 14.84 | 33.7023 | -118.0065 | 11.679
DMA 331 | Metal Loss | Ext | 14127.24 | 0.18 | 0.25 | 42000 | SMLS | 6.625 | 728 | 12.1153 | 0.03 | 0.875 | 0.627 | 8:55 | 3871 | 0.2612 | 12 | 0.88 | 3861 | AGM 4 | 751.26 | AGM 5 | 1965.86 | 1.08 | 21.5 | 44.82 | 10.24 | 22.58 | 5160 | 20.12 | 14.84 | 33.7023 | -118.0065 | 11.676
DMA 332 | Metal Loss | Ext | 14127.42 | 6.49 | 0.25 | 42000 | SMLS | 6.625 | 728 | 11.1269 | 0.028 | 1.126 | 0.741 | 8:26 | 3853 | 0.26242 | 11 | 1.13 | 3839 | AGM 4 | 751.44 | AGM 5 | 1965.69 | 1.26 | 21.32 | 44.82 | 10.24 | 22.58 | 5160 | 20.12 | 14.84 | 33.7023 | -118.0065 | 11.673
DNT 5 | Deformation |  | 14133.91 | 10.94 | 0.25 | 42000 | SMLS | 6.625 | 728 | 2.0016 | 0.133 | 1.16 | 2.261 | 5:08 | [5 empty] | AGM 4 | 757.93 | AGM 5 | 1959.19 | 7.75 | 14.83 | 44.82 | 10.24 | 22.58 | 5160 | 20.12 | 14.84 | 33.7023 | -118.0065 | 11.472
CLS 52 | Cluster | Ext | 14144.85 | 0.12 | 0.25 | 42000 | SMLS | 6.625 | 728 | 11.6634 | 0.029 | 1.274 | 2.659 | 6:01 | 3835 | 0.26365 | 11 | 1.27 | 3823 | AGM 4 | 768.88 | AGM 5 | 1948.25 | 18.69 | 3.89 | 44.82 | 10.24 | 22.58 | 5160 | 20.12 | 14.84 | 33.7024 | -118.0065 | 11.077 | CLS C
DMA 335 | Metal Loss | Ext | 14144.97 | 0.07 | 0.25 | 42000 | SMLS | 6.625 | 728 | 11.4187 | 0.029 | 0.873 | 0.763 | 10:24 | 3875 | 0.26093 | 11 | 0.87 | 3865 | AGM 4 | 768.99 | AGM 5 | 1948.13 | 18.81 | 3.77 | 44.82 | 10.24 | 22.58 | 5160 | 20.12 | 14.84 | 33.7024 | -118.0065 | 11.073
DMA 336 | Metal Loss | Ext | 14145.03 | 0.18 | 0.25 | 42000 | SMLS | 6.625 | 728 | 10.6614 | 0.027 | 0.62 | 0.548 | 7:04 | 3899 | 0.25933 | 11 | 0.62 | 3894 | AGM 4 | 769.06 | AGM 5 | 1948.07 | 18.87 | 3.71 | 44.82 | 10.24 | 22.58 | 5160 | 20.12 | 14.84 | 33.7024 | -118.0065 | 11.071
CLS 53 | Cluster | Ext | 14145.21 | 0.34 | 0.25 | 42000 | SMLS | 6.625 | 728 | 15.0109 | 0.038 | 1.363 | 2.295 | 5:43 | 3795 | 0.26643 | 15 | 1.36 | 3770 | AGM 4 | 769.24 | AGM 5 | 1947.89 | 19.05 | 3.53 | 44.82 | 10.24 | 22.58 | 5160 | 20.12 | 14.84 | 33.7024 | -118.0065 | 11.059 | CLS C
DMA 339 | Metal Loss | Ext | 14145.55 | 0.44 | 0.25 | 42000 | SMLS | 6.625 | 728 | 10.1509 | 0.025 | 0.765 | 0.593 | 3:51 | 3890 | 0.25993 | 10 | 0.76 | 3883 | AGM 4 | 769.58 | AGM 5 | 1947.55 | 19.39 | 3.19 | 44.82 | 10.24 | 22.58 | 5160 | 20.12 | 14.84 | 33.7024 | -118.0065 | 11.044
CLS 54 | Cluster | Ext | 14145.99 | 0.7 | 0.25 | 42000 | SMLS | 6.625 | 728 | 14.5845 | 0.036 | 3.096 | 3.547 | 5:31 | 3651 | 0.27694 | 11 | 3.1 | 3686 | AGM 4 | 770.01 | AGM 5 | 1947.11 | 19.83 | 2.75 | 44.82 | 10.24 | 22.58 | 5160 | 20.12 | 14.84 | 33.7024 | -118.0065 | 11.025 | CLS C
CLS 55 | Cluster | Ext | 14146.69 | 0.3 | 0.25 | 42000 | SMLS | 6.625 | 728 | 11.3356 | 0.028 | 2.533 | 1.024 | 5:27 | 3743 | 0.27013 | 7 | 2.53 | 3786 | AGM 4 | 770.71 | AGM 5 | 1946.42 | 20.52 | 2.06 | 44.82 | 10.24 | 22.58 | 5160 | 20.12 | 14.84 | 33.7024 | -118.0065 | 10.992 | CLS C
DMA 346 | Metal Loss | Ext | 14146.99 | 0.14 | 0.25 | 42000 | SMLS | 6.625 | 728 | 10.6333 | 0.027 | 1.063 | 0.541 | 3:29 | 3862 | 0.26181 | 11 | 1.06 | 3850 | AGM 4 | 771.01 | AGM 5 | 1946.12 | 20.83 | 1.75 | 44.82 | 10.24 | 22.58 | 5160 | 20.12 | 14.84 | 33.7024 | -118.0065 | 10.977
DMA 347 | Metal Loss | Ext | 14147.13 | 0.49 | 0.25 | 42000 | SMLS | 6.625 | 728 | 10.0775 | 0.025 | 0.574 | 0.62 | 6:59 | 3904 | 0.25899 | 10 | 0.57 | 3900 | AGM 4 | 771.15 | AGM 5 | 1945.98 | 20.97 | 1.61 | 44.82 | 10.24 | 22.58 | 5160 | 20.12 | 14.84 | 33.7024 | -118.0065 | 10.969
DMA 348 | Metal Loss | Ext | 14147.62 | 1.13 | 0.25 | 42000 | SMLS | 6.625 | 728 | 10.5535 | 0.026 | 0.624 | 0.604 | 4:08 | 3899 | 0.25933 | 11 | 0.62 | 3894 | AGM 4 | 771.64 | AGM 5 | 1945.49 | 21.45 | 1.13 | 44.82 | 10.24 | 22.58 | 5160 | 20.12 | 14.84 | 33.7024 | -118.0065 | 10.947
GWD 5170 | Girth Weld |  | 14148.74 | 2.3 | 0.25 | 42000 | SMLS | 6.625 | 728 | [10 empty] | AGM 4 | 772.76 | AGM 5 | 1944.36 | 22.58 | 20.12 | 10.24 | 22.58 | 20.12 | 5170 | 14.84 | 3.87 | 33.7024 | -118.0065 | 10.883
DMA 349 | Metal Loss | Ext | 14151.04 | 0.51 | 0.25 | 42000 | SMLS | 6.625 | 728 | 11.15 | 0.028 | 0.669 | 0.811 | 4:14 | 3894 | 0.25966 | 11 | 0.67 | 3888 | AGM 4 | 775.06 | AGM 5 | 1942.06 | 2.3 | 17.82 | 10.24 | 22.58 | 20.12 | 5170 | 14.84 | 3.87 | 33.7024 | -118.0065 | 10.717
DMA 350 | Metal Loss | Ext | 14151.55 | 0.19 | 0.25 | 42000 | SMLS | 6.625 | 728 | 12.6521 | 0.032 | 0.797 | 0.742 | 12:59 | 3877 | 0.2608 | 13 | 0.8 | 3867 | AGM 4 | 775.57 | AGM 5 | 1941.55 | 2.81 | 17.31 | 10.24 | 22.58 | 20.12 | 5170 | 14.84 | 3.87 | 33.7024 | -118.0065 | 10.68
DMA 351 | Metal Loss | Ext | 14151.74 | 0.13 | 0.25 | 42000 | SMLS | 6.625 | 728 | 12.0896 | 0.03 | 1.927 | 0.952 | 10:36 | 3772 | 0.26806 | 12 | 1.93 | 3743 | AGM 4 | 775.77 | AGM 5 | 1941.36 | 3 | 17.12 | 10.24 | 22.58 | 20.12 | 5170 | 14.84 | 3.87 | 33.7024 | -118.0065 | 10.66
DMA 352 | Metal Loss | Ext | 14151.87 | 0.16 | 0.25 | 42000 | SMLS | 6.625 | 728 | 12.2766 | 0.031 | 0.76 | 0.603 | 4:26 | 3882 | 0.26046 | 12 | 0.76 | 3874 | AGM 4 | 775.9 | AGM 5 | 1941.23 | 3.13 | 16.99 | 10.24 | 22.58 | 20.12 | 5170 | 14.84 | 3.87 | 33.7024 | -118.0065 | 10.652
DMA 353 | Metal Loss | Ext | 14152.04 | 0.14 | 0.25 | 42000 | SMLS | 6.625 | 728 | 11.7125 | 0.029 | 0.528 | 0.581 | 4:09 | 3903 | 0.25906 | 12 | 0.53 | 3899 | AGM 4 | 776.06 | AGM 5 | 1941.07 | 3.29 | 16.82 | 10.24 | 22.58 | 20.12 | 5170 | 14.84 | 3.87 | 33.7024 | -118.0065 | 10.637
CLS 56 | Cluster | Ext | 14152.17 | 0.03 | 0.25 | 42000 | SMLS | 6.625 | 728 | 14.1357 | 0.035 | 1.817 | 2.583 | 10:57 | 3755 | 0.26927 | 12 | 1.82 | 3754 | AGM 4 | 776.19 | AGM 5 | 1940.93 | 3.43 | 16.69 | 10.24 | 22.58 | 20.12 | 5170 | 14.84 | 3.87 | 33.7024 | -118.0065 | 10.628 | CLS C
DMA 355 | Metal Loss | Ext | 14152.2 | 0.74 | 0.25 | 42000 | SMLS | 6.625 | 728 | 11.8865 | 0.03 | 0.654 | 0.822 | 4:36 | 3893 | 0.25973 | 12 | 0.65 | 3887 | AGM 4 | 776.23 | AGM 5 | 1940.9 | 3.46 | 16.66 | 10.24 | 22.58 | 20.12 | 5170 | 14.84 | 3.87 | 33.7024 | -118.0065 | 10.625
CLS 57 | Cluster | Ext | 14152.94 | 0.35 | 0.25 | 42000 | SMLS | 6.625 | 728 | 11.8564 | 0.03 | 2.691 | 1.345 | 10:02 | 3725 | 0.27144 | 10 | 2.69 | 3723 | AGM 4 | 776.96 | AGM 5 | 1940.16 | 4.2 | 15.92 | 10.24 | 22.58 | 20.12 | 5170 | 14.84 | 3.87 | 33.7024 | -118.0065 | 10.564 | CLS C
DMA 359 | Metal Loss | Ext | 14153.29 | 1.84 | 0.25 | 42000 | SMLS | 6.625 | 728 | 10.3171 | 0.026 | 0.969 | 0.831 | 9:49 | 3872 | 0.26113 | 10 | 0.97 | 3862 | AGM 4 | 777.32 | AGM 5 | 1939.81 | 4.55 | 15.57 | 10.24 | 22.58 | 20.12 | 5170 | 14.84 | 3.87 | 33.7024 | -118.0065 | 10.535
DMA 360 | Metal Loss | Ext | 14155.13 | 0.32 | 0.25 | 42000 | SMLS | 6.625 | 728 | 15.222 | 0.038 | 1.321 | 2.072 | 11:19 | 3799 | 0.26615 | 15 | 1.32 | 3773 | AGM 4 | 779.15 | AGM 5 | 1937.97 | 6.39 | 13.73 | 10.24 | 22.58 | 20.12 | 5170 | 14.84 | 3.87 | 33.7024 | -118.0065 | 10.378
CLS 58 | Cluster | Ext | 14155.45 | 0.28 | 0.25 | 42000 | SMLS | 6.625 | 728 | 26.0899 | 0.065 | 2.715 | 1.385 | 11:19 | 3451 | 0.29299 | 22 | 2.71 | 3462 | AGM 4 | 779.47 | AGM 5 | 1937.65 | 6.71 | 13.41 | 10.24 | 22.58 | 20.12 | 5170 | 14.84 | 3.87 | 33.7024 | -118.0065 | 10.35 | CLS C
DMA 363 | Metal Loss | Ext | 14155.73 | 0.31 | 0.25 | 42000 | SMLS | 6.625 | 728 | 13.8909 | 0.035 | 1.022 | 0.71 | 9:56 | 3846 | 0.2629 | 14 | 1.02 | 3830 | AGM 4 | 779.76 | AGM 5 | 1937.37 | 6.99 | 13.13 | 10.24 | 22.58 | 20.12 | 5170 | 14.84 | 3.87 | 33.7024 | -118.0065 | 10.323
CLS 59 | Cluster | Ext | 14156.04 | 0.59 | 0.25 | 42000 | SMLS | 6.625 | 728 | 11.6152 | 0.029 | 0.895 | 1.816 | 10:15 | 3872 | 0.26113 | 10 | 0.9 | 3873 | AGM 4 | 780.06 | AGM 5 | 1937.06 | 7.3 | 12.82 | 10.24 | 22.58 | 20.12 | 5170 | 14.84 | 3.87 | 33.7024 | -118.0065 | 10.297 | CLS C
DMA 366 | Metal Loss | Ext | 14156.63 | 0.27 | 0.25 | 42000 | SMLS | 6.625 | 728 | 19.1338 | 0.048 | 1.482 | 0.796 | 11:17 | 3736 | 0.27064 | 19 | 1.48 | 3697 | AGM 4 | 780.65 | AGM 5 | 1936.47 | 7.89 | 12.23 | 10.24 | 22.58 | 20.12 | 5170 | 14.84 | 3.87 | 33.7024 | -118.0065 | 10.245
DMA 367 | Metal Loss | Ext | 14156.9 | 0.35 | 0.25 | 42000 | SMLS | 6.625 | 728 | 14.4299 | 0.036 | 0.615 | 0.648 | 1:55 | 3889 | 0.25999 | 14 | 0.61 | 3882 | AGM 4 | 780.92 | AGM 5 | 1936.2 | 8.16 | 11.96 | 10.24 | 22.58 | 20.12 | 5170 | 14.84 | 3.87 | 33.7024 | -118.0065 | 10.217
DMA 368 | Metal Loss | Ext | 14157.26 | 0.28 | 0.25 | 42000 | SMLS | 6.625 | 728 | 10.1771 | 0.025 | 0.899 | 0.626 | 8:55 | 3879 | 0.26066 | 10 | 0.9 | 3870 | AGM 4 | 781.28 | AGM 5 | 1935.85 | 8.51 | 11.6 | 10.24 | 22.58 | 20.12 | 5170 | 14.84 | 3.87 | 33.7024 | -118.0065 | 10.185
DMA 369 | Metal Loss | Ext | 14157.53 | 2.56 | 0.25 | 42000 | SMLS | 6.625 | 728 | 14.183 | 0.035 | 0.828 | 0.695 | 3:07 | 3867 | 0.26147 | 14 | 0.83 | 3855 | AGM 4 | 781.56 | AGM 5 | 1935.57 | 8.79 | 11.33 | 10.24 | 22.58 | 20.12 | 5170 | 14.84 | 3.87 | 33.7024 | -118.0065 | 10.158
CLS 60 | Cluster | Ext | 14160.09 | 0.37 | 0.25 | 42000 | SMLS | 6.625 | 728 | 21.8602 | 0.055 | 3.101 | 1.884 | 6:25 | 3501 | 0.28881 | 11 | 3.1 | 3690 | AGM 4 | 784.11 | AGM 5 | 1933.01 | 11.35 | 8.77 | 10.24 | 22.58 | 20.12 | 5170 | 14.84 | 3.87 | 33.7024 | -118.0065 | 9.915 | CLS C
DMA 373 | Metal Loss | Ext | 14160.46 | 0.71 | 0.25 | 42000 | SMLS | 6.625 | 728 | 11.4011 | 0.029 | 0.826 | 0.888 | 1:33 | 3879 | 0.26066 | 11 | 0.83 | 3871 | AGM 4 | 784.49 | AGM 5 | 1932.64 | 11.72 | 8.4 | 10.24 | 22.58 | 20.12 | 5170 | 14.84 | 3.87 | 33.7024 | -118.0065 | 9.877
DMA 374 | Metal Loss | Ext | 14161.17 | 7.69 | 0.25 | 42000 | SMLS | 6.625 | 728 | 14.6976 | 0.037 | 0.482 | 0.607 | 2:28 | 3902 | 0.25913 | 15 | 0.48 | 3897 | AGM 4 | 785.2 | AGM 5 | 1931.93 | 12.43 | 7.69 | 10.24 | 22.58 | 20.12 | 5170 | 14.84 | 3.87 | 33.7024 | -118.0065 | 9.811
GWD 5180 | Girth Weld |  | 14168.86 | 14.84 | 0.28 | 42000 | SMLS | 6.625 | 728 | [10 empty] | AGM 4 | 792.88 | AGM 5 | 1924.24 | 20.12 | 14.84 | 22.58 | 20.12 | 14.84 | 5180 | 3.87 | 0.34 | 33.7024 | -118.0065 | 9.004
GWD 5190 | Girth Weld |  | 14183.7 | 3.87 | 0.25 | 42000 | SMLS | 6.625 | 728 | [10 empty] | AGM 4 | 807.72 | AGM 5 | 1909.41 | 14.84 | 3.87 | 20.12 | 14.84 | 3.87 | 5190 | 0.34 | 20.45 | 33.7025 | -118.0065 | 6.799 | Estimated WT 0.250
GWD 5200 | Girth Weld |  | 14187.57 | 0.33 | 0.25 | 42000 | SMLS | 6.625 | 728 | [10 empty] | AGM 4 | 811.59 | AGM 5 | 1905.53 | 3.87 | 0.34 | 14.84 | 3.87 | 0.34 | 5200 | 20.45 | 20.06 | 33.7025 | -118.0065 | 6.117
BND 64 | Bend |  | 14187.89 | 0.01 | 0.25 | 42000 | SMLS | 6.625 | 728 |  |  | 4.055 | [7 empty] | AGM 4 | 811.92 | AGM 5 | 1905.21 | 0.33 | 0.01 | 14.84 | 3.87 | 0.34 | 5200 | 20.45 | 20.06 | 33.7025 | -118.0065 | 6.044 | 3.0D 9.8 deg right turn over bend
GWD 5210 | Girth Weld |  | 14187.91 | 0.94 | 0.28 | 42000 | SMLS | 6.625 | 728 | [10 empty] | AGM 4 | 811.93 | AGM 5 | 1905.2 | 0.34 | 20.45 | 3.87 | 0.34 | 20.45 | 5210 | 20.06 | 20.09 | 33.7025 | -118.0065 | 6.04
PMA 24 | Pipe Mill | Ext | 14188.84 | 0.08 | 0.28 | 42000 | SMLS | 6.625 | 728 | 14.6636 | 0.041 | 0.475 | 0.568 | 4:38 | [5 empty] | AGM 4 | 812.87 | AGM 5 | 1904.26 | 0.94 | 19.52 | 3.87 | 0.34 | 20.45 | 5210 | 20.06 | 20.09 | 33.7025 | -118.0065 | 5.76
PMA 25 | Pipe Mill | Ext | 14188.93 | 0.14 | 0.28 | 42000 | SMLS | 6.625 | 728 | 16.2852 | 0.046 | 0.727 | 0.793 | 5:21 | [5 empty] | AGM 4 | 812.95 | AGM 5 | 1904.18 | 1.02 | 19.44 | 3.87 | 0.34 | 20.45 | 5210 | 20.06 | 20.09 | 33.7025 | -118.0065 | 5.732
PMA 26 | Pipe Mill | Ext | 14189.07 | 9.03 | 0.28 | 42000 | SMLS | 6.625 | 728 | 11.4427 | 0.032 | 0.96 | 1.094 | 5:38 | [5 empty] | AGM 4 | 813.09 | AGM 5 | 1904.03 | 1.16 | 19.29 | 3.87 | 0.34 | 20.45 | 5210 | 20.06 | 20.09 | 33.7025 | -118.0065 | 5.681
BND 65 | Bend |  | 14198.1 | 10.26 | 0.28 | 42000 | SMLS | 6.625 | 728 |  |  | 20.46 | [7 empty] | AGM 4 | 822.12 | AGM 5 | 1895 | 10.19 | 10.26 | 3.87 | 0.34 | 20.45 | 5210 | 20.06 | 20.09 | 33.7025 | -118.0065 | 2.662 | 18.5D 10.1 deg left turn sag bend
GWD 5220 | Girth Weld |  | 14208.36 | 10.1 | 0.312 | 42000 | SMLS | 6.625 | 728 | [10 empty] | AGM 4 | 832.38 | AGM 5 | 1884.74 | 20.45 | 20.06 | 0.34 | 20.45 | 20.06 | 5220 | 20.09 | 19.76 | 33.7025 | -118.0065 | 0.129 | Estimated WT 0.312
CLS 61 | Cluster | Ext | 14218.47 | 9.95 | 0.312 | 42000 | SMLS | 6.625 | 728 | 20.6421 | 0.064 | 2.867 | 5.821 | 6:42 | 4460 | 0.22671 | 12 | 2.87 | 4606 | AGM 4 | 842.49 | AGM 5 | 1874.64 | 10.1 | 9.95 | 0.34 | 20.45 | 20.06 | 5220 | 20.09 | 19.76 | 33.7026 | -118.0065 | -2.223 | CLS C ¦ ID Restriction
GWD 5230 | Girth Weld |  | 14228.42 | 20.09 | 0.312 | 42000 | SMLS | 6.625 | 728 | [10 empty] | AGM 4 | 852.44 | AGM 5 | 1864.68 | 20.06 | 20.09 | 20.45 | 20.06 | 20.09 | 5230 | 19.76 | 20.36 | 33.7026 | -118.0065 | -4.002
GWD 5240 | Girth Weld |  | 14248.51 | 19.76 | 0.28 | 42000 | SMLS | 6.625 | 728 | [10 empty] | AGM 4 | 872.54 | AGM 5 | 1844.59 | 20.09 | 19.76 | 20.06 | 20.09 | 19.76 | 5240 | 20.36 | 16.79 | 33.7026 | -118.0065 | -6.716
GWD 5250 | Girth Weld |  | 14268.27 | 9.72 | 0.312 | 42000 | SMLS | 6.625 | 728 | [10 empty] | AGM 4 | 892.29 | AGM 5 | 1824.83 | 19.76 | 20.36 | 20.09 | 19.76 | 20.36 | 5250 | 16.79 | 2.71 | 33.7027 | -118.0065 | -8.43 | Estimated WT 0.312
DMA 380 | Metal Loss | Ext | 14277.99 | 10.64 | 0.312 | 42000 | SMLS | 6.625 | 728 | 18.6478 | 0.058 | 0.586 | 0.911 | 2:24 | 4854 | 0.2083 | 19 | 0.59 | 4844 | AGM 4 | 902.02 | AGM 5 | 1815.11 | 9.72 | 10.64 | 20.09 | 19.76 | 20.36 | 5250 | 16.79 | 2.71 | 33.7027 | -118.0065 | -8.775
GWD 5260 | Girth Weld |  | 14288.63 | 16.79 | 0.28 | 42000 | SMLS | 6.625 | 728 | [10 empty] | AGM 4 | 912.66 | AGM 5 | 1804.47 | 20.36 | 16.79 | 19.76 | 20.36 | 16.79 | 5260 | 2.71 | 47.37 | 33.7028 | -118.0065 | -8.735
GWD 5270 | Girth Weld |  | 14305.43 | 2.71 | 0.25 | 42000 | SMLS | 6.625 | 728 | [10 empty] | AGM 4 | 929.45 | AGM 5 | 1787.68 | 16.79 | 2.71 | 20.36 | 16.79 | 2.71 | 5270 | 47.37 | 45.79 | 33.7028 | -118.0065 | -8.275 | Estimated WT 0.250
GWD 5280 | Girth Weld |  | 14308.14 | 47.36 | 0.25 | 42000 | SMLS | 6.625 | 728 | [10 empty] | AGM 4 | 932.16 | AGM 5 | 1784.97 | 2.71 | 47.37 | 16.79 | 2.71 | 47.37 | 5280 | 45.79 | 48.38 | 33.7028 | -118.0065 | -8.148
GWD 5290 | Girth Weld |  | 14355.5 | 35.45 | 0.25 | 42000 | SMLS | 6.625 | 728 | [10 empty] | AGM 4 | 979.52 | AGM 5 | 1737.6 | 47.37 | 45.79 | 2.71 | 47.37 | 45.79 | 5290 | 48.38 | 46.65 | 33.7029 | -118.0065 | -7.634
PMA 27 | Pipe Mill | Ext | 14390.95 | 10.33 | 0.25 | 42000 | SMLS | 6.625 | 728 | 10.4681 | 0.026 | 0.445 | 0.705 | 3:42 | [5 empty] | AGM 4 | 1014.98 | AGM 5 | 1702.15 | 35.45 | 10.34 | 2.71 | 47.37 | 45.79 | 5290 | 48.38 | 46.65 | 33.703 | -118.0065 | -7.791
GWD 5300 | Girth Weld |  | 14401.29 | 15.5 | 0.25 | 42000 | SMLS | 6.625 | 728 | [10 empty] | AGM 4 | 1025.31 | AGM 5 | 1691.81 | 45.79 | 48.38 | 47.37 | 45.79 | 48.38 | 5300 | 46.65 | 46.72 | 33.7031 | -118.0065 | -7.974
CLS 62 | Cluster | Ext | 14416.78 | 0.94 | 0.25 | 42000 | SMLS | 6.625 | 728 | 18.2539 | 0.046 | 1.818 | 0.976 | 3:09 | 3699 | 0.27335 | 15 | 1.82 | 3710 | AGM 4 | 1040.81 | AGM 5 | 1676.32 | 15.49 | 32.88 | 47.37 | 45.79 | 48.38 | 5300 | 46.65 | 46.72 | 33.7031 | -118.0065 | -8.199 | CLS C
DMA 383 | Metal Loss | Ext | 14417.72 | 1.19 | 0.25 | 42000 | SMLS | 6.625 | 728 | 34.6868 | 0.087 | 0.575 | 0.813 | 3:35 | 3833 | 0.26379 | 35 | 0.58 | 3809 | AGM 4 | 1041.74 | AGM 5 | 1675.38 | 16.43 | 31.95 | 47.37 | 45.79 | 48.38 | 5300 | 46.65 | 46.72 | 33.7031 | -118.0065 | -8.21
CLS 63 | Cluster | Ext | 14418.91 | 0.38 | 0.25 | 42000 | SMLS | 6.625 | 728 | 17.6697 | 0.044 | 1.918 | 1.172 | 2:47 | 3695 | 0.27364 | 12 | 1.92 | 3749 | AGM 4 | 1042.93 | AGM 5 | 1674.19 | 17.62 | 30.76 | 47.37 | 45.79 | 48.38 | 5300 | 46.65 | 46.72 | 33.7031 | -118.0065 | -8.228 | CLS C
CLS 64 | Cluster | Ext | 14419.3 | 0.58 | 0.25 | 42000 | SMLS | 6.625 | 728 | 15.7548 | 0.039 | 2.145 | 1.183 | 3:18 | 3700 | 0.27327 | 8 | 2.14 | 3790 | AGM 4 | 1043.32 | AGM 5 | 1673.81 | 18.01 | 30.37 | 47.37 | 45.79 | 48.38 | 5300 | 46.65 | 46.72 | 33.7031 | -118.0065 | -8.232 | CLS C
DMA 389 | Metal Loss | Ext | 14419.88 | 0.55 | 0.25 | 42000 | SMLS | 6.625 | 728 | 18.1699 | 0.045 | 0.45 | 0.818 | 3:10 | 3899 | 0.25933 | 18 | 0.45 | 3893 | AGM 4 | 1043.9 | AGM 5 | 1673.23 | 18.59 | 29.79 | 47.37 | 45.79 | 48.38 | 5300 | 46.65 | 46.72 | 33.7031 | -118.0065 | -8.239
DMA 390 | Metal Loss | Ext | 14420.42 | 0.47 | 0.25 | 42000 | SMLS | 6.625 | 728 | 12.4383 | 0.031 | 0.811 | 0.687 | 2:32 | 3876 | 0.26086 | 12 | 0.81 | 3867 | AGM 4 | 1044.44 | AGM 5 | 1672.68 | 19.13 | 29.25 | 47.37 | 45.79 | 48.38 | 5300 | 46.65 | 46.72 | 33.7031 | -118.0065 | -8.245
DMA 391 | Metal Loss | Ext | 14420.9 | 0.5 | 0.25 | 42000 | SMLS | 6.625 | 728 | 10.2887 | 0.026 | 0.821 | 0.853 | 2:41 | 3885 | 0.26026 | 10 | 0.82 | 3877 | AGM 4 | 1044.92 | AGM 5 | 1672.21 | 19.61 | 28.77 | 47.37 | 45.79 | 48.38 | 5300 | 46.65 | 46.72 | 33.7031 | -118.0065 | -8.251
DMA 392 | Metal Loss | Ext | 14421.39 | 3.76 | 0.25 | 42000 | SMLS | 6.625 | 728 | 10.5459 | 0.026 | 0.871 | 0.874 | 3:08 | 3879 | 0.26066 | 11 | 0.87 | 3871 | AGM 4 | 1045.42 | AGM 5 | 1671.71 | 20.1 | 28.27 | 47.37 | 45.79 | 48.38 | 5300 | 46.65 | 46.72 | 33.7031 | -118.0065 | -8.256
DMA 393 | Metal Loss | Ext | 14425.15 | 0.92 | 0.25 | 42000 | SMLS | 6.625 | 728 | 24.1362 | 0.06 | 1.161 | 0.67 | 8:24 | 3745 | 0.26999 | 24 | 1.16 | 3705 | AGM 4 | 1049.18 | AGM 5 | 1667.95 | 23.86 | 24.51 | 47.37 | 45.79 | 48.38 | 5300 | 46.65 | 46.72 | 33.7031 | -118.0065 | -8.307
DMA 394 | Metal Loss | Ext | 14426.08 | 2.47 | 0.25 | 42000 | SMLS | 6.625 | 728 | 20.0696 | 0.05 | 1.288 | 0.852 | 9:00 | 3758 | 0.26906 | 20 | 1.29 | 3723 | AGM 4 | 1050.1 | AGM 5 | 1667.03 | 24.79 | 23.59 | 47.37 | 45.79 | 48.38 | 5300 | 46.65 | 46.72 | 33.7031 | -118.0065 | -8.32
DMA 395 | Metal Loss | Ext | 14428.55 | 0.14 | 0.25 | 42000 | SMLS | 6.625 | 728 | 17.9911 | 0.045 | 0.507 | 0.676 | 9:04 | 3893 | 0.25973 | 18 | 0.51 | 3886 | AGM 4 | 1052.57 | AGM 5 | 1664.56 | 27.26 | 21.12 | 47.37 | 45.79 | 48.38 | 5300 | 46.65 | 46.72 | 33.7031 | -118.0065 | -8.357
DMA 396 | Metal Loss | Ext | 14428.69 | 0.32 | 0.25 | 42000 | SMLS | 6.625 | 728 | 10.207 | 0.026 | 0.718 | 0.913 | 9:14 | 3893 | 0.25973 | 10 | 0.72 | 3887 | AGM 4 | 1052.71 | AGM 5 | 1664.41 | 27.4 | 20.98 | 47.37 | 45.79 | 48.38 | 5300 | 46.65 | 46.72 | 33.7031 | -118.0065 | -8.36
DMA 397 | Metal Loss | Ext | 14429.01 | 1.45 | 0.25 | 42000 | SMLS | 6.625 | 728 | 11.011 | 0.028 | 1.686 | 1.622 | 8:48 | 3805 | 0.26573 | 11 | 1.69 | 3782 | AGM 4 | 1053.03 | AGM 5 | 1664.09 | 27.72 | 20.66 | 47.37 | 45.79 | 48.38 | 5300 | 46.65 | 46.72 | 33.7031 | -118.0065 | -8.365
DMA 398 | Metal Loss | Ext | 14430.46 | 0.6 | 0.25 | 42000 | SMLS | 6.625 | 728 | 10.7798 | 0.027 | 1.199 | 0.82 | 9:08 | 3849 | 0.26269 | 11 | 1.2 | 3834 | AGM 4 | 1054.48 | AGM 5 | 1662.65 | 29.17 | 19.21 | 47.37 | 45.79 | 48.38 | 5300 | 46.65 | 46.72 | 33.7031 | -118.0065 | -8.386
DMA 399 | Metal Loss | Ext | 14431.06 | 0.4 | 0.25 | 42000 | SMLS | 6.625 | 728 | 27.0442 | 0.068 | 0.688 | 0.852 | 8:27 | 3834 | 0.26372 | 27 | 0.69 | 3813 | AGM 4 | 1055.08 | AGM 5 | 1662.04 | 29.77 | 18.61 | 47.37 | 45.79 | 48.38 | 5300 | 46.65 | 46.72 | 33.7031 | -118.0065 | -8.399
CLS 65 | Cluster | Ext | 14431.46 | 0.47 | 0.25 | 42000 | SMLS | 6.625 | 728 | 36.828 | 0.092 | 1.376 | 2.104 | 9:00 | 3543 | 0.28538 | 24 | 1.38 | 3659 | AGM 4 | 1055.48 | AGM 5 | 1661.64 | 30.17 | 18.21 | 47.37 | 45.79 | 48.38 | 5300 | 46.65 | 46.72 | 33.7031 | -118.0065 | -8.405 | CLS C
DMA 402 | Metal Loss | Ext | 14431.93 | 0.47 | 0.25 | 42000 | SMLS | 6.625 | 728 | 16.0721 | 0.04 | 0.495 | 0.605 | 9:15 | 3898 | 0.25939 | 16 | 0.49 | 3892 | AGM 4 | 1055.96 | AGM 5 | 1661.17 | 30.64 | 17.74 | 47.37 | 45.79 | 48.38 | 5300 | 46.65 | 46.72 | 33.7031 | -118.0065 | -8.413
CLS 66 | Cluster | Ext | 14432.4 | 0.38 | 0.25 | 42000 | SMLS | 6.625 | 728 | 24.6852 | 0.062 | 3.414 | 1.509 | 9:29 | 3414 | 0.29617 | 15 | 3.41 | 3570 | AGM 4 | 1056.43 | AGM 5 | 1660.7 | 31.11 | 17.27 | 47.37 | 45.79 | 48.38 | 5300 | 46.65 | 46.72 | 33.7031 | -118.0065 | -8.419 | CLS C
DMA 407 | Metal Loss | Ext | 14432.78 | 0.22 | 0.25 | 42000 | SMLS | 6.625 | 728 | 31.6258 | 0.079 | 0.751 | 1.037 | 9:21 | 3796 | 0.26636 | 32 | 0.75 | 3764 | AGM 4 | 1056.8 | AGM 5 | 1660.33 | 31.49 | 16.89 | 47.37 | 45.79 | 48.38 | 5300 | 46.65 | 46.72 | 33.7031 | -118.0065 | -8.426
DMA 408 | Metal Loss | Ext | 14433 | 0.5 | 0.25 | 42000 | SMLS | 6.625 | 728 | 45.9233 | 0.115 | 0.997 | 1.053 | 9:11 | 3586 | 0.28196 | 46 | 1 | 3488 | AGM 4 | 1057.02 | AGM 5 | 1660.1 | 31.71 | 16.67 | 47.37 | 45.79 | 48.38 | 5300 | 46.65 | 46.72 | 33.7031 | -118.0065 | -8.432
DMA 409 | Metal Loss | Ext | 14433.5 | 0.41 | 0.25 | 42000 | SMLS | 6.625 | 728 | 22.9507 | 0.057 | 1.016 | 0.951 | 9:14 | 3785 | 0.26714 | 23 | 1.02 | 3755 | AGM 4 | 1057.52 | AGM 5 | 1659.6 | 32.21 | 16.17 | 47.37 | 45.79 | 48.38 | 5300 | 46.65 | 46.72 | 33.7032 | -118.0065 | -8.442
DMA 410 | Metal Loss | Ext | 14433.91 | 0.43 | 0.25 | 42000 | SMLS | 6.625 | 728 | 23.1177 | 0.058 | 0.912 | 0.873 | 9:43 | 3806 | 0.26566 | 23 | 0.91 | 3779 | AGM 4 | 1057.93 | AGM 5 | 1659.2 | 32.62 | 15.76 | 47.37 | 45.79 | 48.38 | 5300 | 46.65 | 46.72 | 33.7032 | -118.0065 | -8.452
DMA 411 | Metal Loss | Ext | 14434.33 | 0.47 | 0.25 | 42000 | SMLS | 6.625 | 728 | 23.5388 | 0.059 | 0.862 | 0.749 | 9:48 | 3814 | 0.26511 | 24 | 0.86 | 3789 | AGM 4 | 1058.36 | AGM 5 | 1658.77 | 33.04 | 15.34 | 47.37 | 45.79 | 48.38 | 5300 | 46.65 | 46.72 | 33.7032 | -118.0065 | -8.458
DMA 412 | Metal Loss | Ext | 14434.8 | 2.5 | 0.25 | 42000 | SMLS | 6.625 | 728 | 15.4011 | 0.039 | 1.198 | 1.366 | 9:31 | 3813 | 0.26517 | 15 | 1.2 | 3790 | AGM 4 | 1058.82 | AGM 5 | 1658.3 | 33.51 | 14.87 | 47.37 | 45.79 | 48.38 | 5300 | 46.65 | 46.72 | 33.7032 | -118.0065 | -8.468
DMA 413 | Metal Loss | Ext | 14437.3 | 0.32 | 0.25 | 42000 | SMLS | 6.625 | 728 | 24.882 | 0.062 | 1.378 | 2.003 | 8:56 | 3690 | 0.27401 | 25 | 1.38 | 3640 | AGM 4 | 1061.32 | AGM 5 | 1655.8 | 36.01 | 12.37 | 47.37 | 45.79 | 48.38 | 5300 | 46.65 | 46.72 | 33.7032 | -118.0065 | -8.521
DMA 414 | Metal Loss | Ext | 14437.62 | 1.69 | 0.25 | 42000 | SMLS | 6.625 | 728 | 19.6974 | 0.049 | 0.722 | 0.672 | 9:11 | 3858 | 0.26208 | 20 | 0.72 | 3843 | AGM 4 | 1061.64 | AGM 5 | 1655.48 | 36.33 | 12.05 | 47.37 | 45.79 | 48.38 | 5300 | 46.65 | 46.72 | 33.7032 | -118.0065 | -8.528
DMA 415 | Metal Loss | Ext | 14439.31 | 1.87 | 0.25 | 42000 | SMLS | 6.625 | 728 | 33.5854 | 0.084 | 0.888 | 0.684 | 8:35 | 3742 | 0.27021 | 34 | 0.89 | 3696 | AGM 4 | 1063.33 | AGM 5 | 1653.79 | 38.02 | 10.36 | 47.37 | 45.79 | 48.38 | 5300 | 46.65 | 46.72 | 33.7032 | -118.0065 | -8.57
DMA 416 | Metal Loss | Ext | 14441.18 | 1.62 | 0.25 | 42000 | SMLS | 6.625 | 728 | 33.953 | 0.085 | 0.85 | 0.76 | 8:32 | 3751 | 0.26956 | 34 | 0.85 | 3708 | AGM 4 | 1065.21 | AGM 5 | 1651.92 | 39.89 | 8.48 | 47.37 | 45.79 | 48.38 | 5300 | 46.65 | 46.72 | 33.7032 | -118.0065 | -8.611
DMA 417 | Metal Loss | Ext | 14442.81 | 0.43 | 0.25 | 42000 | SMLS | 6.625 | 728 | 19.0881 | 0.048 | 0.769 | 0.847 | 8:26 | 3853 | 0.26242 | 19 | 0.77 | 3838 | AGM 4 | 1066.83 | AGM 5 | 1650.3 | 41.52 | 6.86 | 47.37 | 45.79 | 48.38 | 5300 | 46.65 | 46.72 | 33.7032 | -118.0065 | -8.647
DMA 418 | Metal Loss | Ext | 14443.23 | 0.39 | 0.25 | 42000 | SMLS | 6.625 | 728 | 41.1831 | 0.103 | 1.571 | 0.72 | 8:37 | 3411 | 0.29643 | 41 | 1.57 | 3282 | AGM 4 | 1067.26 | AGM 5 | 1649.87 | 41.94 | 6.43 | 47.37 | 45.79 | 48.38 | 5300 | 46.65 | 46.72 | 33.7032 | -118.0065 | -8.656
CLS 67 | Cluster | Ext | 14443.62 | 0.84 | 0.25 | 42000 | SMLS | 6.625 | 728 | 23.016 | 0.058 | 3.964 | 1.038 | 8:24 | 3416 | 0.29599 | 15 | 3.96 | 3553 | AGM 4 | 1067.65 | AGM 5 | 1649.48 | 42.33 | 6.05 | 47.37 | 45.79 | 48.38 | 5300 | 46.65 | 46.72 | 33.7032 | -118.0065 | -8.663 | CLS C
DMA 422 | Metal Loss | Ext | 14444.46 | 0.45 | 0.25 | 42000 | SMLS | 6.625 | 728 | 34.7459 | 0.087 | 1.001 | 0.871 | 8:29 | 3695 | 0.27364 | 35 | 1 | 3638 | AGM 4 | 1068.49 | AGM 5 | 1648.64 | 43.17 | 5.21 | 47.37 | 45.79 | 48.38 | 5300 | 46.65 | 46.72 | 33.7032 | -118.0065 | -8.676
DMA 423 | Metal Loss | Ext | 14444.91 | 4.76 | 0.25 | 42000 | SMLS | 6.625 | 728 | 15.6588 | 0.039 | 0.738 | 0.808 | 8:13 | 3871 | 0.2612 | 16 | 0.74 | 3860 | AGM 4 | 1068.93 | AGM 5 | 1648.2 | 43.62 | 4.76 | 47.37 | 45.79 | 48.38 | 5300 | 46.65 | 46.72 | 33.7032 | -118.0065 | -8.689
GWD 5310 | Girth Weld |  | 14449.67 | 46.65 | 0.25 | 42000 | SMLS | 6.625 | 728 | [10 empty] | AGM 4 | 1073.69 | AGM 5 | 1643.43 | 48.38 | 46.65 | 45.79 | 48.38 | 46.65 | 5310 | 46.72 | 47.2 | 33.7032 | -118.0065 | -8.766
GWD 5320 | Girth Weld |  | 14496.32 | 46.72 | 0.25 | 42000 | SMLS | 6.625 | 728 | [10 empty] | AGM 4 | 1120.34 | AGM 5 | 1596.78 | 46.65 | 46.72 | 48.38 | 46.65 | 46.72 | 5320 | 47.2 | 46.55 | 33.7033 | -118.0065 | -8.42
GWD 5330 | Girth Weld |  | 14543.04 | 47.2 | 0.25 | 42000 | SMLS | 6.625 | 728 | [10 empty] | AGM 4 | 1167.06 | AGM 5 | 1550.07 | 46.72 | 47.2 | 46.65 | 46.72 | 47.2 | 5330 | 46.55 | 47.71 | 33.7035 | -118.0065 | -7.332
GWD 5340 | Girth Weld |  | 14590.24 | 25.2 | 0.25 | 42000 | SMLS | 6.625 | 728 | [10 empty] | AGM 4 | 1214.26 | AGM 5 | 1502.87 | 47.2 | 46.55 | 46.72 | 47.2 | 46.55 | 5340 | 47.71 | 46.8 | 33.7036 | -118.0065 | -7.956
PMA 28 | Pipe Mill | Ext | 14615.43 | 21.36 | 0.25 | 42000 | SMLS | 6.625 | 728 | 10.025 | 0.025 | 1.172 | 0.877 | 8:05 | [5 empty] | AGM 4 | 1239.45 | AGM 5 | 1477.67 | 25.2 | 21.35 | 46.72 | 47.2 | 46.55 | 5340 | 47.71 | 46.8 | 33.7036 | -118.0065 | -8.144
GWD 5350 | Girth Weld |  | 14636.79 | 47.71 | 0.25 | 42000 | SMLS | 6.625 | 728 | [10 empty] | AGM 4 | 1260.81 | AGM 5 | 1456.32 | 46.55 | 47.71 | 47.2 | 46.55 | 47.71 | 5350 | 46.8 | 48.87 | 33.7037 | -118.0065 | -8.338
GWD 5360 | Girth Weld |  | 14684.49 | 46.8 | 0.25 | 42000 | SMLS | 6.625 | 728 | [10 empty] | AGM 4 | 1308.52 | AGM 5 | 1408.61 | 47.71 | 46.8 | 46.55 | 47.71 | 46.8 | 5360 | 48.87 | 43.42 | 33.7038 | -118.0065 | -8.526
GWD 5370 | Girth Weld |  | 14731.3 | 48.87 | 0.25 | 42000 | SMLS | 6.625 | 728 | [10 empty] | AGM 4 | 1355.32 | AGM 5 | 1361.81 | 46.8 | 48.87 | 47.71 | 46.8 | 48.87 | 5370 | 43.42 | 47.33 | 33.704 | -118.0065 | -9.386
GWD 5380 | Girth Weld |  | 14780.17 | 43.42 | 0.25 | 42000 | SMLS | 6.625 | 728 | [10 empty] | AGM 4 | 1404.19 | AGM 5 | 1312.93 | 48.87 | 43.42 | 46.8 | 48.87 | 43.42 | 5380 | 47.33 | 44.39 | 33.7041 | -118.0065 | -10.39
GWD 5390 | Girth Weld |  | 14823.59 | 34.13 | 0.25 | 42000 | SMLS | 6.625 | 728 | [10 empty] | AGM 4 | 1447.61 | AGM 5 | 1269.52 | 43.42 | 47.33 | 48.87 | 43.42 | 47.33 | 5390 | 44.39 | 48.64 | 33.7042 | -118.0065 | -10.76
DMA 424 | Metal Loss | Ext | 14857.72 | 0.48 | 0.25 | 42000 | SMLS | 6.625 | 728 | 11.6509 | 0.029 | 0.884 | 0.683 | 4:26 | 3873 | 0.26107 | 12 | 0.88 | 3863 | AGM 4 | 1481.74 | AGM 5 | 1235.38 | 34.13 | 13.19 | 48.87 | 43.42 | 47.33 | 5390 | 44.39 | 48.64 | 33.7043 | -118.0065 | -10.901
DMA 425 | Metal Loss | Ext | 14858.2 | 12.72 | 0.25 | 42000 | SMLS | 6.625 | 728 | 10.0881 | 0.025 | 0.618 | 0.676 | 4:19 | 3901 | 0.25919 | 10 | 0.62 | 3896 | AGM 4 | 1482.22 | AGM 5 | 1234.91 | 34.61 | 12.72 | 48.87 | 43.42 | 47.33 | 5390 | 44.39 | 48.64 | 33.7043 | -118.0065 | -10.904
GWD 5400 | Girth Weld |  | 14870.91 | 44.39 | 0.25 | 42000 | SMLS | 6.625 | 728 | [10 empty] | AGM 4 | 1494.94 | AGM 5 | 1222.19 | 47.33 | 44.39 | 43.42 | 47.33 | 44.39 | 5400 | 48.64 | 22.14 | 33.7043 | -118.0065 | -10.869
GWD 5410 | Girth Weld |  | 14915.31 | 48.64 | 0.25 | 42000 | SMLS | 6.625 | 728 | [10 empty] | AGM 4 | 1539.33 | AGM 5 | 1177.8 | 44.39 | 48.64 | 47.33 | 44.39 | 48.64 | 5410 | 22.14 | 18.87 | 33.7045 | -118.0065 | -9.906
GWD 5420 | Girth Weld |  | 14963.94 | 22.15 | 0.25 | 42000 | SMLS | 6.625 | 728 | [10 empty] | AGM 4 | 1587.97 | AGM 5 | 1129.16 | 48.64 | 22.14 | 44.39 | 48.64 | 22.14 | 5420 | 18.87 | 1.08 | 33.7046 | -118.0065 | -6.938
GWD 5430 | Girth Weld |  | 14986.09 | 18.87 | 0.25 | 42000 | SMLS | 6.625 | 728 | [10 empty] | AGM 4 | 1610.11 | AGM 5 | 1107.02 | 22.14 | 18.87 | 48.64 | 22.14 | 18.87 | 5430 | 1.08 | 1.23 | 33.7047 | -118.0065 | -6.554 | Weld+End
GWD 5440 | Girth Weld |  | 15004.96 | 1.08 | 0.25 | 42000 | SMLS | 6.625 | 728 | [10 empty] | AGM 4 | 1628.99 | AGM 5 | 1088.14 | 18.87 | 1.08 | 22.14 | 18.87 | 1.08 | 5440 | 1.23 | 1.07 | 33.7047 | -118.0065 | -6.299 | Weld+End
GWD 5450 | Girth Weld |  | 15006.04 | 0.56 | 0.25 | 42000 | SMLS | 6.625 | 728 | [10 empty] | AGM 4 | 1630.06 | AGM 5 | 1087.06 | 1.08 | 1.23 | 18.87 | 1.08 | 1.23 | 5450 | 1.07 | 1.21 | 33.7047 | -118.0065 | -6.256
BND 66 | Bend |  | 15006.6 | 0.66 | 0.25 | 42000 | SMLS | 6.625 | 728 |  |  | 14.764 | [7 empty] | AGM 4 | 1630.63 | AGM 5 | 1086.5 | 0.56 | 0.67 | 18.87 | 1.08 | 1.23 | 5450 | 1.07 | 1.21 | 33.7047 | -118.0065 | -6.362 | 3.0D 50.3 deg over bend
GWD 5460 | Girth Weld |  | 15007.27 | 1.07 | 0.25 | 42000 | SMLS | 6.625 | 728 | [10 empty] | AGM 4 | 1631.29 | AGM 5 | 1085.83 | 1.23 | 1.07 | 1.08 | 1.23 | 1.07 | 5460 | 1.21 | 1.03 | 33.7047 | -118.0065 | -6.71
GWD 5470 | Girth Weld |  | 15008.34 | 0.63 | 0.25 | 42000 | SMLS | 6.625 | 728 | [10 empty] | AGM 4 | 1632.37 | AGM 5 | 1084.76 | 1.07 | 1.21 | 1.23 | 1.07 | 1.21 | 5470 | 1.03 | 5.06 | 33.7047 | -118.0065 | -7.465
BND 67 | Bend |  | 15008.97 | 0.58 | 0.25 | 42000 | SMLS | 6.625 | 728 |  |  | 14.488 | [7 empty] | AGM 4 | 1632.99 | AGM 5 | 1084.13 | 0.63 | 0.58 | 1.23 | 1.07 | 1.21 | 5470 | 1.03 | 5.06 | 33.7047 | -118.0065 | -7.776 | 3.0D 51.0 deg left turn sag bend
GWD 5480 | Girth Weld |  | 15009.55 | 1.03 | 0.25 | 42000 | SMLS | 6.625 | 728 | [10 empty] | AGM 4 | 1633.57 | AGM 5 | 1083.55 | 1.21 | 1.03 | 1.07 | 1.21 | 1.03 | 5480 | 5.06 | 30.82 | 33.7047 | -118.0065 | -7.876
GWD 5490 | Girth Weld |  | 15010.58 | 5.06 | 0.25 | 42000 | SMLS | 6.625 | 728 | [10 empty] | AGM 4 | 1634.6 | AGM 5 | 1082.53 | 1.03 | 5.06 | 1.21 | 1.03 | 5.06 | 5490 | 30.82 | 41.78 | 33.7047 | -118.0065 | -7.824 | Weld+End
GWD 5500 | Girth Weld |  | 15015.64 | 30.82 | 0.25 | 42000 | SMLS | 6.625 | 728 | [10 empty] | AGM 4 | 1639.66 | AGM 5 | 1077.47 | 5.06 | 30.82 | 1.03 | 5.06 | 30.82 | 5500 | 41.78 | 46.61 | 33.7047 | -118.0065 | -7.494 | Weld+End
GWD 5510 | Girth Weld |  | 15046.45 | 41.78 | 0.25 | 42000 | SMLS | 6.625 | 728 | [10 empty] | AGM 4 | 1670.48 | AGM 5 | 1046.65 | 30.82 | 41.78 | 5.06 | 30.82 | 41.78 | 5510 | 46.61 | 45.46 | 33.7048 | -118.0065 | -7.169
GWD 5520 | Girth Weld |  | 15088.23 | 46.61 | 0.25 | 42000 | SMLS | 6.625 | 728 | [10 empty] | AGM 4 | 1712.25 | AGM 5 | 1004.88 | 41.78 | 46.61 | 30.82 | 41.78 | 46.61 | 5520 | 45.46 | 44.65 | 33.7049 | -118.0065 | -6.528
GWD 5530 | Girth Weld |  | 15134.84 | 45.46 | 0.25 | 42000 | SMLS | 6.625 | 728 | [10 empty] | AGM 4 | 1758.86 | AGM 5 | 958.27 | 46.61 | 45.46 | 41.78 | 46.61 | 45.46 | 5530 | 44.65 | 46.7 | 33.7051 | -118.0065 | -7.547
GWD 5540 | Girth Weld |  | 15180.3 | 44.65 | 0.25 | 42000 | SMLS | 6.625 | 728 | [10 empty] | AGM 4 | 1804.32 | AGM 5 | 912.8 | 45.46 | 44.65 | 46.61 | 45.46 | 44.65 | 5540 | 46.7 | 45.9 | 33.7052 | -118.0065 | -7.845
GWD 5550 | Girth Weld |  | 15224.95 | 46.7 | 0.25 | 42000 | SMLS | 6.625 | 728 | [10 empty] | AGM 4 | 1848.97 | AGM 5 | 868.15 | 44.65 | 46.7 | 45.46 | 44.65 | 46.7 | 5550 | 45.9 | 42.27 | 33.7053 | -118.0066 | -8.423
GWD 5560 | Girth Weld |  | 15271.65 | 45.91 | 0.25 | 42000 | SMLS | 6.625 | 728 | [10 empty] | AGM 4 | 1895.67 | AGM 5 | 821.46 | 46.7 | 45.9 | 44.65 | 46.7 | 45.9 | 5560 | 42.27 | 45.65 | 33.7054 | -118.0066 | -8.566
GWD 5570 | Girth Weld |  | 15317.55 | 42.27 | 0.25 | 42000 | SMLS | 6.625 | 728 | [10 empty] | AGM 4 | 1941.57 | AGM 5 | 775.55 | 45.9 | 42.27 | 46.7 | 45.9 | 42.27 | 5570 | 45.65 | 45.89 | 33.7056 | -118.0066 | -9.055
GWD 5580 | Girth Weld |  | 15359.82 | 45.65 | 0.25 | 42000 | SMLS | 6.625 | 728 | [10 empty] | AGM 4 | 1983.84 | AGM 5 | 733.28 | 42.27 | 45.65 | 45.9 | 42.27 | 45.65 | 5580 | 45.89 | 45.46 | 33.7057 | -118.0066 | -9.276
GWD 5590 | Girth Weld |  | 15405.47 | 45.89 | 0.25 | 42000 | SMLS | 6.625 | 728 | [10 empty] | AGM 4 | 2029.49 | AGM 5 | 687.63 | 45.65 | 45.89 | 42.27 | 45.65 | 45.89 | 5590 | 45.46 | 45.53 | 33.7058 | -118.0066 | -9.908
GWD 5600 | Girth Weld |  | 15451.37 | 45.46 | 0.25 | 42000 | SMLS | 6.625 | 728 | [10 empty] | AGM 4 | 2075.39 | AGM 5 | 641.74 | 45.89 | 45.46 | 45.65 | 45.89 | 45.46 | 5600 | 45.53 | 45.83 | 33.7059 | -118.0066 | -10.356
GWD 5610 | Girth Weld |  | 15496.83 | 45.53 | 0.25 | 42000 | SMLS | 6.625 | 728 | [10 empty] | AGM 4 | 2120.85 | AGM 5 | 596.27 | 45.46 | 45.53 | 45.89 | 45.46 | 45.53 | 5610 | 45.83 | 46.67 | 33.7061 | -118.0066 | -9.889
GWD 5620 | Girth Weld |  | 15542.36 | 45.83 | 0.25 | 42000 | SMLS | 6.625 | 728 | [10 empty] | AGM 4 | 2166.38 | AGM 5 | 550.75 | 45.53 | 45.83 | 45.46 | 45.53 | 45.83 | 5620 | 46.67 | 45.36 | 33.7062 | -118.0066 | -9.271
GWD 5630 | Girth Weld |  | 15588.19 | 46.67 | 0.25 | 42000 | SMLS | 6.625 | 728 | [10 empty] | AGM 4 | 2212.21 | AGM 5 | 504.92 | 45.83 | 46.67 | 45.53 | 45.83 | 46.67 | 5630 | 45.36 | 45.21 | 33.7063 | -118.0066 | -8.499
GWD 5640 | Girth Weld |  | 15634.86 | 45.36 | 0.25 | 42000 | SMLS | 6.625 | 728 | [10 empty] | AGM 4 | 2258.88 | AGM 5 | 458.25 | 46.67 | 45.36 | 45.83 | 46.67 | 45.36 | 5640 | 45.21 | 47.14 | 33.7064 | -118.0066 | -7.347
GWD 5650 | Girth Weld |  | 15680.22 | 45.21 | 0.25 | 42000 | SMLS | 6.625 | 728 | [10 empty] | AGM 4 | 2304.24 | AGM 5 | 412.88 | 45.36 | 45.21 | 46.67 | 45.36 | 45.21 | 5650 | 47.14 | 46.8 | 33.7066 | -118.0065 | -6.213
GWD 5660 | Girth Weld |  | 15725.43 | 47.14 | 0.25 | 42000 | SMLS | 6.625 | 728 | [10 empty] | AGM 4 | 2349.46 | AGM 5 | 367.67 | 45.21 | 47.14 | 45.36 | 45.21 | 47.14 | 5660 | 46.8 | 16.05 | 33.7067 | -118.0065 | -5.076
GWD 5670 | Girth Weld |  | 15772.57 | 46.8 | 0.25 | 42000 | SMLS | 6.625 | 728 | [10 empty] | AGM 4 | 2396.59 | AGM 5 | 320.53 | 47.14 | 46.8 | 45.21 | 47.14 | 46.8 | 5670 | 16.05 | 1.16 | 33.7068 | -118.0065 | -3.707
GWD 5680 | Girth Weld |  | 15819.37 | 16.05 | 0.25 | 42000 | SMLS | 6.625 | 728 | [10 empty] | AGM 4 | 2443.39 | AGM 5 | 273.74 | 46.8 | 16.05 | 47.14 | 46.8 | 16.05 | 5680 | 1.16 | 40.43 | 33.7069 | -118.0066 | -2.694
GWD 5690 | Girth Weld |  | 15835.42 | 0.6 | 0.25 | 42000 | SMLS | 6.625 | 728 | [10 empty] | AGM 4 | 2459.44 | AGM 5 | 257.69 | 16.05 | 1.16 | 46.8 | 16.05 | 1.16 | 5690 | 40.43 | 41.61 | 33.707 | -118.0066 | -2.113
BND 68 | Bend |  | 15836.02 | 0.55 | 0.25 | 42000 | SMLS | 6.625 | 728 |  |  | 21.474 | [7 empty] | AGM 4 | 2460.04 | AGM 5 | 257.08 | 0.6 | 0.56 | 46.8 | 16.05 | 1.16 | 5690 | 40.43 | 41.61 | 33.707 | -118.0066 | -2.069 | 5.0D 46.1 deg right turn sag bend
GWD 5700 | Girth Weld |  | 15836.58 | 40.44 | 0.25 | 42000 | SMLS | 6.625 | 728 | [10 empty] | AGM 4 | 2460.6 | AGM 5 | 256.53 | 1.16 | 40.43 | 16.05 | 1.16 | 40.43 | 5700 | 41.61 | 15.54 | 33.707 | -118.0066 | -2.025
GWD 5710 | Girth Weld |  | 15877.01 | 41.61 | 0.25 | 42000 | SMLS | 6.625 | 728 | [10 empty] | AGM 4 | 2501.03 | AGM 5 | 216.09 | 40.43 | 41.61 | 1.16 | 40.43 | 41.61 | 5710 | 15.54 | 1.16 | 33.7071 | -118.0065 | 1.074
GWD 5720 | Girth Weld |  | 15918.62 | 15.54 | 0.25 | 42000 | SMLS | 6.625 | 728 | [10 empty] | AGM 4 | 2542.64 | AGM 5 | 174.48 | 41.61 | 15.54 | 40.43 | 41.61 | 15.54 | 5720 | 1.16 | 3.98 | 33.7072 | -118.0064 | 1.93
GWD 5730 | Girth Weld |  | 15934.16 | 0.61 | 0.25 | 42000 | SMLS | 6.625 | 728 | [10 empty] | AGM 4 | 2558.19 | AGM 5 | 158.94 | 15.54 | 1.16 | 41.61 | 15.54 | 1.16 | 5730 | 3.98 | 7.19 | 33.7072 | -118.0063 | 1.976
BND 69 | Bend |  | 15934.78 | 0.55 | 0.25 | 42000 | SMLS | 6.625 | 728 |  |  | 13.976 | [7 empty] | AGM 4 | 2558.8 | AGM 5 | 158.33 | 0.61 | 0.55 | 41.61 | 15.54 | 1.16 | 5730 | 3.98 | 7.19 | 33.7072 | -118.0063 | 1.981 | 3.0D 43.9 deg left turn sag bend
GWD 5740 | Girth Weld |  | 15935.33 | 3.98 | 0.25 | 42000 | SMLS | 6.625 | 728 | [10 empty] | AGM 4 | 2559.35 | AGM 5 | 157.77 | 1.16 | 3.98 | 15.54 | 1.16 | 3.98 | 5740 | 7.19 | 41.24 | 33.7072 | -118.0063 | 2.001
GWD 5750 | Girth Weld |  | 15939.31 | 7.19 | 0.25 | 42000 | SMLS | 6.625 | 728 | [10 empty] | AGM 4 | 2563.33 | AGM 5 | 153.79 | 3.98 | 7.19 | 1.16 | 3.98 | 7.19 | 5750 | 41.24 | 41.77 | 33.7072 | -118.0063 | 2.14
GWD 5760 | Girth Weld |  | 15946.5 | 41.24 | 0.219 | 42000 | ERW | 6.625 | 728 | [10 empty] | AGM 4 | 2570.52 | AGM 5 | 146.61 | 7.19 | 41.24 | 3.98 | 7.19 | 41.24 | 5760 | 41.77 | 41.75 | 33.7072 | -118.0063 | 2.347
GWD 5770 | Girth Weld |  | 15987.73 | 41.77 | 0.219 | 42000 | ERW | 6.625 | 728 | [10 empty] | AGM 4 | 2611.75 | AGM 5 | 105.37 | 41.24 | 41.77 | 7.19 | 41.24 | 41.77 | 5770 | 41.75 | 41.74 | 33.7073 | -118.0063 | 4.56
GWD 5780 | Girth Weld |  | 16029.5 | 41.76 | 0.219 | 42000 | ERW | 6.625 | 728 | [10 empty] | AGM 4 | 2653.52 | AGM 5 | 63.6 | 41.77 | 41.75 | 41.24 | 41.77 | 41.75 | 5780 | 41.74 | 40.18 | 33.7075 | -118.0063 | 5.856
GWD 5790 | Girth Weld |  | 16071.26 | 21.85 | 0.219 | 42000 | ERW | 6.625 | 728 | [10 empty] | AGM 4 | 2695.28 | AGM 5 | 21.85 | 41.75 | 41.74 | 41.77 | 41.75 | 41.74 | 5790 | 40.18 | 6.37 | 33.7076 | -118.0064 | 6.659
MRK 3 | Marker |  | 16093.1 | 19.89 | 0.219 | 42000 | ERW | 6.625 | 728 |  |  |  |  | 12:37 | [5 empty] | AGM 4 | 2717.13 | AGM 6 | 3558.07 | 21.85 | 19.89 | 41.77 | 41.75 | 41.74 | 5790 | 40.18 | 6.37 | 33.7076 | -118.0064 | 7.214 | AGM 5 7' West of Curb - Located in Goldenwest St
GWD 5800 | Girth Weld |  | 16113 | 40.18 | 0.219 | 42000 | ERW | 6.625 | 728 | [10 empty] | AGM 5 | 19.89 | AGM 6 | 3538.18 | 41.74 | 40.18 | 41.75 | 41.74 | 40.18 | 5800 | 6.37 | 1.22 | 33.7077 | -118.0064 | 7.634
GWD 5810 | Girth Weld |  | 16153.17 | 6.37 | 0.219 | 42000 | ERW | 6.625 | 728 | [10 empty] | AGM 5 | 60.07 | AGM 6 | 3498 | 40.18 | 6.37 | 41.74 | 40.18 | 6.37 | 5810 | 1.22 | 3.97 | 33.7078 | -118.0064 | 8.049
GWD 5820 | Girth Weld |  | 16159.54 | 0.74 | 0.219 | 42000 | ERW | 6.625 | 728 | [10 empty] | AGM 5 | 66.44 | AGM 6 | 3491.63 | 6.37 | 1.22 | 40.18 | 6.37 | 1.22 | 5820 | 3.97 | 1.21 | 33.7078 | -118.0064 | 8.115
BND 70 | Bend |  | 16160.28 | 0.47 | 0.219 | 42000 | ERW | 6.625 | 728 |  |  | 14.606 | [7 empty] | AGM 5 | 67.18 | AGM 6 | 3490.89 | 0.74 | 0.48 | 40.18 | 6.37 | 1.22 | 5820 | 3.97 | 1.21 | 33.7078 | -118.0064 | 8.116 | 3.0D 49.5 deg left turn over bend
GWD 5830 | Girth Weld |  | 16160.76 | 3.97 | 0.219 | 42000 | ERW | 6.625 | 728 | [10 empty] | AGM 5 | 67.65 | AGM 6 | 3490.42 | 1.22 | 3.97 | 6.37 | 1.22 | 3.97 | 5830 | 1.21 | 1.61 | 33.7078 | -118.0064 | 8.116
GWD 5840 | Girth Weld |  | 16164.72 | 0.73 | 0.219 | 42000 | ERW | 6.625 | 728 | [10 empty] | AGM 5 | 71.62 | AGM 6 | 3486.45 | 3.97 | 1.21 | 1.22 | 3.97 | 1.21 | 5840 | 1.61 | 29.9 | 33.7078 | -118.0064 | 8.054
BND 71 | Bend |  | 16165.45 | 0.49 | 0.219 | 42000 | ERW | 6.625 | 728 |  |  | 14.567 | [7 empty] | AGM 5 | 72.35 | AGM 6 | 3485.72 | 0.73 | 0.49 | 1.22 | 3.97 | 1.21 | 5840 | 1.61 | 29.9 | 33.7078 | -118.0064 | 8.051 | 3.0D 49.6 deg right turn sag bend
GWD 5850 | Girth Weld |  | 16165.94 | 1.61 | 0.219 | 42000 | ERW | 6.625 | 728 | [10 empty] | AGM 5 | 72.84 | AGM 6 | 3485.24 | 1.21 | 1.61 | 3.97 | 1.21 | 1.61 | 5850 | 29.9 | 45.49 | 33.7078 | -118.0064 | 8.059
GWD 5860 | Girth Weld |  | 16167.55 | 1.19 | 0.25 | 42000 | SMLS | 6.625 | 728 | [10 empty] | AGM 5 | 74.45 | AGM 6 | 3483.62 | 1.61 | 29.9 | 1.21 | 1.61 | 29.9 | 5860 | 45.49 | 46.13 | 33.7078 | -118.0064 | 8.11 | Estimated WT 0.250
TAP 11 | TAP |  | 16168.74 | 28.71 | 0.25 | 42000 | SMLS | 6.625 | 728 |  |  |  |  | 12:06 | [5 empty] | AGM 5 | 75.64 | AGM 6 | 3482.44 | 1.19 | 28.71 | 1.21 | 1.61 | 29.9 | 5860 | 45.49 | 46.13 | 33.7078 | -118.0064 | 8.139
GWD 5870 | Girth Weld |  | 16197.45 | 45.5 | 0.25 | 42000 | SMLS | 6.625 | 728 | [10 empty] | AGM 5 | 104.35 | AGM 6 | 3453.73 | 29.9 | 45.49 | 1.61 | 29.9 | 45.49 | 5870 | 46.13 | 45.17 | 33.7079 | -118.0064 | 8.385
GWD 5880 | Girth Weld |  | 16242.94 | 46.13 | 0.25 | 42000 | SMLS | 6.625 | 728 | [10 empty] | AGM 5 | 149.84 | AGM 6 | 3408.23 | 45.49 | 46.13 | 29.9 | 45.49 | 46.13 | 5880 | 45.17 | 45.95 | 33.708 | -118.0064 | 8.912
GWD 5890 | Girth Weld |  | 16289.07 | 45.17 | 0.25 | 42000 | SMLS | 6.625 | 728 | [10 empty] | AGM 5 | 195.97 | AGM 6 | 3362.1 | 46.13 | 45.17 | 45.49 | 46.13 | 45.17 | 5890 | 45.95 | 45.44 | 33.7082 | -118.0064 | 9.017
GWD 5900 | Girth Weld |  | 16334.24 | 45.95 | 0.25 | 42000 | SMLS | 6.625 | 728 | [10 empty] | AGM 5 | 241.14 | AGM 6 | 3316.93 | 45.17 | 45.95 | 46.13 | 45.17 | 45.95 | 5900 | 45.44 | 47.36 | 33.7083 | -118.0064 | 9.066
GWD 5910 | Girth Weld |  | 16380.19 | 45.44 | 0.25 | 42000 | SMLS | 6.625 | 728 | [10 empty] | AGM 5 | 287.08 | AGM 6 | 3270.99 | 45.95 | 45.44 | 45.17 | 45.95 | 45.44 | 5910 | 47.36 | 46.9 | 33.7084 | -118.0064 | 8.818
GWD 5920 | Girth Weld |  | 16425.63 | 47.36 | 0.25 | 42000 | SMLS | 6.625 | 728 | [10 empty] | AGM 5 | 332.52 | AGM 6 | 3225.55 | 45.44 | 47.36 | 45.95 | 45.44 | 47.36 | 5920 | 46.9 | 6.02 | 33.7085 | -118.0064 | 9.002
GWD 5930 | Girth Weld |  | 16472.98 | 46.9 | 0.25 | 42000 | SMLS | 6.625 | 728 | [10 empty] | AGM 5 | 379.88 | AGM 6 | 3178.19 | 47.36 | 46.9 | 45.44 | 47.36 | 46.9 | 5930 | 6.02 | 40.43 | 33.7087 | -118.0064 | 9.506
GWD 5940 | Girth Weld |  | 16519.88 | 6.02 | 0.25 | 42000 | SMLS | 6.625 | 728 | [10 empty] | AGM 5 | 426.78 | AGM 6 | 3131.29 | 46.9 | 6.02 | 47.36 | 46.9 | 6.02 | 5940 | 40.43 | 41.82 | 33.7088 | -118.0064 | 8.056
GWD 5950 | Girth Weld |  | 16525.9 | 40.43 | 0.25 | 42000 | ERW | 6.625 | 728 | [10 empty] | AGM 5 | 432.8 | AGM 6 | 3125.27 | 6.02 | 40.43 | 46.9 | 6.02 | 40.43 | 5950 | 41.82 | 41.66 | 33.7088 | -118.0064 | 7.779 | Weld+End
GWD 5960 | Girth Weld |  | 16566.33 | 41.82 | 0.25 | 42000 | ERW | 6.625 | 728 | [10 empty] | AGM 5 | 473.23 | AGM 6 | 3084.84 | 40.43 | 41.82 | 6.02 | 40.43 | 41.82 | 5960 | 41.66 | 42.45 | 33.7089 | -118.0064 | 7.931
GWD 5970 | Girth Weld |  | 16608.15 | 41.66 | 0.25 | 42000 | ERW | 6.625 | 728 | [10 empty] | AGM 5 | 515.05 | AGM 6 | 3043.02 | 41.82 | 41.66 | 40.43 | 41.82 | 41.66 | 5970 | 42.45 | 42.69 | 33.709 | -118.0064 | 7.629
GWD 5980 | Girth Weld |  | 16649.81 | 42.45 | 0.25 | 42000 | ERW | 6.625 | 728 | [10 empty] | AGM 5 | 556.71 | AGM 6 | 3001.36 | 41.66 | 42.45 | 41.82 | 41.66 | 42.45 | 5980 | 42.69 | 41.4 | 33.7092 | -118.0064 | 6.684
GWD 5990 | Girth Weld |  | 16692.26 | 42.69 | 0.25 | 42000 | ERW | 6.625 | 728 | [10 empty] | AGM 5 | 599.16 | AGM 6 | 2958.91 | 42.45 | 42.69 | 41.66 | 42.45 | 42.69 | 5990 | 41.4 | 15.28 | 33.7093 | -118.0064 | 5.834
GWD 6000 | Girth Weld |  | 16734.95 | 41.4 | 0.25 | 42000 | ERW | 6.625 | 728 | [10 empty] | AGM 5 | 641.85 | AGM 6 | 2916.22 | 42.69 | 41.4 | 42.45 | 42.69 | 41.4 | 6000 | 15.28 | 30.06 | 33.7094 | -118.0064 | 4.621
GWD 6010 | Girth Weld |  | 16776.35 | 15.28 | 0.25 | 42000 | ERW | 6.625 | 728 | [10 empty] | AGM 5 | 683.25 | AGM 6 | 2874.82 | 41.4 | 15.28 | 42.69 | 41.4 | 15.28 | 6010 | 30.06 | 43.22 | 33.7095 | -118.0064 | 4.618
GWD 6020 | Girth Weld |  | 16791.63 | 30.06 | 0.25 | 42000 | SMLS | 6.625 | 728 | [10 empty] | AGM 5 | 698.53 | AGM 6 | 2859.54 | 15.28 | 30.06 | 41.4 | 15.28 | 30.06 | 6020 | 43.22 | 40.58 | 33.7095 | -118.0064 | 5.225
GWD 6030 | Girth Weld |  | 16821.69 | 43.22 | 0.25 | 42000 | SMLS | 6.625 | 728 | [10 empty] | AGM 5 | 728.59 | AGM 6 | 2829.49 | 30.06 | 43.22 | 15.28 | 30.06 | 43.22 | 6030 | 40.58 | 43.97 | 33.7096 | -118.0064 | 4.869
GWD 6040 | Girth Weld |  | 16864.91 | 40.58 | 0.25 | 42000 | SMLS | 6.625 | 728 | [10 empty] | AGM 5 | 771.81 | AGM 6 | 2786.26 | 43.22 | 40.58 | 30.06 | 43.22 | 40.58 | 6040 | 43.97 | 42.53 | 33.7097 | -118.0064 | 3.893
GWD 6050 | Girth Weld |  | 16905.49 | 43.97 | 0.25 | 42000 | SMLS | 6.625 | 728 | [10 empty] | AGM 5 | 812.38 | AGM 6 | 2745.69 | 40.58 | 43.97 | 43.22 | 40.58 | 43.97 | 6050 | 42.53 | 41.91 | 33.7099 | -118.0064 | 3.333
GWD 6060 | Girth Weld |  | 16949.46 | 42.53 | 0.25 | 42000 | SMLS | 6.625 | 728 | [10 empty] | AGM 5 | 856.36 | AGM 6 | 2701.72 | 43.97 | 42.53 | 40.58 | 43.97 | 42.53 | 6060 | 41.91 | 42.81 | 33.71 | -118.0064 | 2.921
GWD 6070 | Girth Weld |  | 16991.99 | 41.91 | 0.25 | 42000 | SMLS | 6.625 | 728 | [10 empty] | AGM 5 | 898.89 | AGM 6 | 2659.18 | 42.53 | 41.91 | 43.97 | 42.53 | 41.91 | 6070 | 42.81 | 45.5 | 33.7101 | -118.0064 | 2.213
GWD 6080 | Girth Weld |  | 17033.9 | 42.81 | 0.25 | 42000 | SMLS | 6.625 | 728 | [10 empty] | AGM 5 | 940.8 | AGM 6 | 2617.28 | 41.91 | 42.81 | 42.53 | 41.91 | 42.81 | 6080 | 45.5 | 43.21 | 33.7102 | -118.0064 | 1.994
GWD 6090 | Girth Weld |  | 17076.7 | 45.5 | 0.25 | 42000 | SMLS | 6.625 | 728 | [10 empty] | AGM 5 | 983.6 | AGM 6 | 2574.47 | 42.81 | 45.5 | 41.91 | 42.81 | 45.5 | 6090 | 43.21 | 42.28 | 33.7103 | -118.0064 | 1.59
GWD 6100 | Girth Weld |  | 17122.2 | 43.21 | 0.25 | 42000 | SMLS | 6.625 | 728 | [10 empty] | AGM 5 | 1029.1 | AGM 6 | 2528.97 | 45.5 | 43.21 | 42.81 | 45.5 | 43.21 | 6100 | 42.28 | 42.59 | 33.7104 | -118.0064 | 0.73
GWD 6110 | Girth Weld |  | 17165.41 | 42.28 | 0.25 | 42000 | SMLS | 6.625 | 728 | [10 empty] | AGM 5 | 1072.31 | AGM 6 | 2485.77 | 43.21 | 42.28 | 45.5 | 43.21 | 42.28 | 6110 | 42.59 | 44.31 | 33.7106 | -118.0064 | 0.435
GWD 6120 | Girth Weld |  | 17207.69 | 42.59 | 0.25 | 42000 | SMLS | 6.625 | 728 | [10 empty] | AGM 5 | 1114.59 | AGM 6 | 2443.48 | 42.28 | 42.59 | 43.21 | 42.28 | 42.59 | 6120 | 44.31 | 42.65 | 33.7107 | -118.0064 | -0.336
GWD 6130 | Girth Weld |  | 17250.28 | 44.31 | 0.25 | 42000 | SMLS | 6.625 | 728 | [10 empty] | AGM 5 | 1157.17 | AGM 6 | 2400.9 | 42.59 | 44.31 | 42.28 | 42.59 | 44.31 | 6130 | 42.65 | 43.16 | 33.7108 | -118.0064 | -0.902
GWD 6140 | Girth Weld |  | 17294.59 | 42.65 | 0.25 | 42000 | SMLS | 6.625 | 728 | [10 empty] | AGM 5 | 1201.48 | AGM 6 | 2356.59 | 44.31 | 42.65 | 42.59 | 44.31 | 42.65 | 6140 | 43.16 | 43.34 | 33.7109 | -118.0064 | -1.225
GWD 6150 | Girth Weld |  | 17337.24 | 43.16 | 0.25 | 42000 | SMLS | 6.625 | 728 | [10 empty] | AGM 5 | 1244.13 | AGM 6 | 2313.94 | 42.65 | 43.16 | 44.31 | 42.65 | 43.16 | 6150 | 43.34 | 43.2 | 33.711 | -118.0064 | -2.441
GWD 6160 | Girth Weld |  | 17380.39 | 43.34 | 0.25 | 42000 | SMLS | 6.625 | 728 | [10 empty] | AGM 5 | 1287.29 | AGM 6 | 2270.78 | 43.16 | 43.34 | 42.65 | 43.16 | 43.34 | 6160 | 43.2 | 33.29 | 33.7112 | -118.0064 | -2.491
GWD 6170 | Girth Weld |  | 17423.73 | 43.2 | 0.25 | 42000 | SMLS | 6.625 | 728 | [10 empty] | AGM 5 | 1330.63 | AGM 6 | 2227.44 | 43.34 | 43.2 | 43.16 | 43.34 | 43.2 | 6170 | 33.29 | 42.36 | 33.7113 | -118.0064 | -2.263
GWD 6180 | Girth Weld |  | 17466.94 | 33.29 | 0.25 | 42000 | SMLS | 6.625 | 728 | [10 empty] | AGM 5 | 1373.83 | AGM 6 | 2184.24 | 43.2 | 33.29 | 43.34 | 43.2 | 33.29 | 6180 | 42.36 | 43.88 | 33.7114 | -118.0064 | -2.413
GWD 6190 | Girth Weld |  | 17500.22 | 42.36 | 0.25 | 42000 | SMLS | 6.625 | 728 | [10 empty] | AGM 5 | 1407.12 | AGM 6 | 2150.95 | 33.29 | 42.36 | 43.2 | 33.29 | 42.36 | 6190 | 43.88 | 43.84 | 33.7115 | -118.0064 | -2.527
GWD 6200 | Girth Weld |  | 17542.58 | 43.88 | 0.25 | 42000 | SMLS | 6.625 | 728 | [10 empty] | AGM 5 | 1449.48 | AGM 6 | 2108.59 | 42.36 | 43.88 | 33.29 | 42.36 | 43.88 | 6200 | 43.84 | 39.23 | 33.7116 | -118.0064 | -2.429
GWD 6210 | Girth Weld |  | 17586.46 | 43.84 | 0.25 | 42000 | SMLS | 6.625 | 728 | [10 empty] | AGM 5 | 1493.36 | AGM 6 | 2064.71 | 43.88 | 43.84 | 42.36 | 43.88 | 43.84 | 6210 | 39.23 | 47.64 | 33.7117 | -118.0064 | -2.622
GWD 6220 | Girth Weld |  | 17630.3 | 39.23 | 0.25 | 42000 | SMLS | 6.625 | 728 | [10 empty] | AGM 5 | 1537.19 | AGM 6 | 2020.88 | 43.84 | 39.23 | 43.88 | 43.84 | 39.23 | 6220 | 47.64 | 46.8 | 33.7118 | -118.0064 | -2.135
GWD 6230 | Girth Weld |  | 17669.53 | 47.64 | 0.25 | 42000 | SMLS | 6.625 | 728 | [10 empty] | AGM 5 | 1576.43 | AGM 6 | 1981.65 | 39.23 | 47.64 | 43.84 | 39.23 | 47.64 | 6230 | 46.8 | 48.06 | 33.712 | -118.0064 | -1.974
GWD 6240 | Girth Weld |  | 17717.17 | 46.8 | 0.25 | 42000 | SMLS | 6.625 | 728 | [10 empty] | AGM 5 | 1624.06 | AGM 6 | 1934.01 | 47.64 | 46.8 | 39.23 | 47.64 | 46.8 | 6240 | 48.06 | 45.71 | 33.7121 | -118.0064 | -2.222
GWD 6250 | Girth Weld |  | 17763.96 | 48.06 | 0.25 | 42000 | SMLS | 6.625 | 728 | [10 empty] | AGM 5 | 1670.86 | AGM 6 | 1887.21 | 46.8 | 48.06 | 47.64 | 46.8 | 48.06 | 6250 | 45.71 | 47.17 | 33.7122 | -118.0064 | -1.439
GWD 6260 | Girth Weld |  | 17812.03 | 45.71 | 0.25 | 42000 | SMLS | 6.625 | 728 | [10 empty] | AGM 5 | 1718.92 | AGM 6 | 1839.15 | 48.06 | 45.71 | 46.8 | 48.06 | 45.71 | 6260 | 47.17 | 47.8 | 33.7123 | -118.0064 | -1.253
GWD 6270 | Girth Weld |  | 17857.74 | 47.17 | 0.25 | 42000 | SMLS | 6.625 | 728 | [10 empty] | AGM 5 | 1764.64 | AGM 6 | 1793.44 | 45.71 | 47.17 | 48.06 | 45.71 | 47.17 | 6270 | 47.8 | 21.33 | 33.7125 | -118.0064 | -1.303
GWD 6280 | Girth Weld |  | 17904.91 | 47.8 | 0.25 | 42000 | SMLS | 6.625 | 728 | [10 empty] | AGM 5 | 1811.81 | AGM 6 | 1746.27 | 47.17 | 47.8 | 45.71 | 47.17 | 47.8 | 6280 | 21.33 | 20.92 | 33.7126 | -118.0064 | -1.456
GWD 6290 | Girth Weld |  | 17952.71 | 21.33 | 0.25 | 42000 | SMLS | 6.625 | 728 | [10 empty] | AGM 5 | 1859.61 | AGM 6 | 1698.46 | 47.8 | 21.33 | 47.17 | 47.8 | 21.33 | 6290 | 20.92 | 20.93 | 33.7127 | -118.0064 | -1.226
GWD 6300 | Girth Weld |  | 17974.04 | 20.92 | 0.25 | 42000 | SMLS | 6.625 | 728 | [10 empty] | AGM 5 | 1880.93 | AGM 6 | 1677.14 | 21.33 | 20.92 | 47.8 | 21.33 | 20.92 | 6300 | 20.93 | 18.58 | 33.7128 | -118.0064 | -1.365
GWD 6310 | Girth Weld |  | 17994.96 | 20.93 | 0.25 | 42000 | SMLS | 6.625 | 728 | [10 empty] | AGM 5 | 1901.85 | AGM 6 | 1656.22 | 20.92 | 20.93 | 21.33 | 20.92 | 20.93 | 6310 | 18.58 | 8.17 | 33.7128 | -118.0064 | -1.204
GWD 6320 | Girth Weld |  | 18015.89 | 18.58 | 0.25 | 42000 | SMLS | 6.625 | 728 | [10 empty] | AGM 5 | 1922.79 | AGM 6 | 1635.28 | 20.93 | 18.58 | 20.92 | 20.93 | 18.58 | 6320 | 8.17 | 39.47 | 33.7129 | -118.0064 | -0.998
GWD 6330 | Girth Weld |  | 18034.48 | 2.99 | 0.203 | 42000 | SMLS | 6.625 | 728 | [10 empty] | AGM 5 | 1941.37 | AGM 6 | 1616.7 | 18.58 | 8.17 | 20.93 | 18.58 | 8.17 | 6330 | 39.47 | 40.79 | 33.713 | -118.0064 | -1.24 | Estimated WT 0.203
PMA 29 | Pipe Mill | Ext | 18037.47 | 5.18 | 0.203 | 42000 | SMLS | 6.625 | 728 | 10.9978 | 0.022 | 1.724 | 1.243 | 3:05 | [5 empty] | AGM 5 | 1944.37 | AGM 6 | 1613.71 | 2.99 | 5.18 | 20.93 | 18.58 | 8.17 | 6330 | 39.47 | 40.79 | 33.713 | -118.0064 | -1.243
GWD 6340 | Girth Weld |  | 18042.65 | 39.47 | 0.203 | 42000 | SMLS | 6.625 | 728 | [10 empty] | AGM 5 | 1949.54 | AGM 6 | 1608.53 | 8.17 | 39.47 | 18.58 | 8.17 | 39.47 | 6340 | 40.79 | 38.86 | 33.713 | -118.0064 | -1.186
GWD 6350 | Girth Weld |  | 18082.12 | 40.79 | 0.203 | 42000 | SMLS | 6.625 | 728 | [10 empty] | AGM 5 | 1989.02 | AGM 6 | 1569.06 | 39.47 | 40.79 | 8.17 | 39.47 | 40.79 | 6350 | 38.86 | 39.58 | 33.7131 | -118.0064 | -0.609
GWD 6360 | Girth Weld |  | 18122.91 | 38.86 | 0.203 | 42000 | SMLS | 6.625 | 728 | [10 empty] | AGM 5 | 2029.81 | AGM 6 | 1528.27 | 40.79 | 38.86 | 39.47 | 40.79 | 38.86 | 6360 | 39.58 | 37.9 | 33.7132 | -118.0064 | -0.79
GWD 6370 | Girth Weld |  | 18161.77 | 39.58 | 0.203 | 42000 | SMLS | 6.625 | 728 | [10 empty] | AGM 5 | 2068.67 | AGM 6 | 1489.4 | 38.86 | 39.58 | 40.79 | 38.86 | 39.58 | 6370 | 37.9 | 39.99 | 33.7133 | -118.0064 | -0.817
GWD 6380 | Girth Weld |  | 18201.35 | 37.9 | 0.203 | 42000 | SMLS | 6.625 | 728 | [10 empty] | AGM 5 | 2108.25 | AGM 6 | 1449.82 | 39.58 | 37.9 | 38.86 | 39.58 | 37.9 | 6380 | 39.99 | 39.49 | 33.7134 | -118.0064 | -0.3
GWD 6390 | Girth Weld |  | 18239.26 | 39.99 | 0.203 | 42000 | SMLS | 6.625 | 728 | [10 empty] | AGM 5 | 2146.15 | AGM 6 | 1411.92 | 37.9 | 39.99 | 39.58 | 37.9 | 39.99 | 6390 | 39.49 | 24.73 | 33.7135 | -118.0064 | 0.296
GWD 6400 | Girth Weld |  | 18279.25 | 39.49 | 0.203 | 42000 | SMLS | 6.625 | 728 | [10 empty] | AGM 5 | 2186.14 | AGM 6 | 1371.93 | 39.99 | 39.49 | 37.9 | 39.99 | 39.49 | 6400 | 24.73 | 27.96 | 33.7136 | -118.0064 | 0.391
GWD 6410 | Girth Weld |  | 18318.74 | 24.73 | 0.203 | 42000 | SMLS | 6.625 | 728 | [10 empty] | AGM 5 | 2225.63 | AGM 6 | 1332.44 | 39.49 | 24.73 | 39.99 | 39.49 | 24.73 | 6410 | 27.96 | 44.29 | 33.7137 | -118.0064 | 1.069
GWD 6420 | Girth Weld |  | 18343.46 | 15.85 | 0.203 | 42000 | SMLS | 6.625 | 728 | [10 empty] | AGM 5 | 2250.36 | AGM 6 | 1307.71 | 24.73 | 27.96 | 39.49 | 24.73 | 27.96 | 6420 | 44.29 | 46.9 | 33.7138 | -118.0064 | 1.628
PMA 30 | Pipe Mill | Ext | 18359.31 | 12.11 | 0.203 | 42000 | SMLS | 6.625 | 728 | 11.8054 | 0.024 | 0.827 | 0.957 | 9:17 | [5 empty] | AGM 5 | 2266.21 | AGM 6 | 1291.86 | 15.85 | 12.11 | 39.49 | 24.73 | 27.96 | 6420 | 44.29 | 46.9 | 33.7138 | -118.0064 | 2.547
GWD 6430 | Girth Weld |  | 18371.42 | 44.29 | 0.219 | 42000 | ERW | 6.625 | 728 | [10 empty] | AGM 5 | 2278.32 | AGM 6 | 1279.75 | 27.96 | 44.29 | 24.73 | 27.96 | 44.29 | 6430 | 46.9 | 46.74 | 33.7139 | -118.0064 | 2.819
GWD 6440 | Girth Weld |  | 18415.71 | 46.9 | 0.219 | 42000 | ERW | 6.625 | 728 | [10 empty] | AGM 5 | 2322.61 | AGM 6 | 1235.46 | 44.29 | 46.9 | 27.96 | 44.29 | 46.9 | 6440 | 46.74 | 46.75 | 33.714 | -118.0064 | 3.608
GWD 6450 | Girth Weld |  | 18462.62 | 38.84 | 0.219 | 42000 | ERW | 6.625 | 728 | [10 empty] | AGM 5 | 2369.51 | AGM 6 | 1188.56 | 46.9 | 46.74 | 44.29 | 46.9 | 46.74 | 6450 | 46.75 | 46.75 | 33.7141 | -118.0064 | 4.222
PMA 31 | Pipe Mill | Ext | 18501.45 | 7.9 | 0.219 | 42000 | ERW | 6.625 | 728 | 11.3232 | 0.025 | 0.894 | 0.602 | 3:46 | [5 empty] | AGM 5 | 2408.35 | AGM 6 | 1149.72 | 38.84 | 7.9 | 44.29 | 46.9 | 46.74 | 6450 | 46.75 | 46.75 | 33.7142 | -118.0064 | 4.451
GWD 6460 | Girth Weld |  | 18509.35 | 46.75 | 0.219 | 42000 | ERW | 6.625 | 728 | [10 empty] | AGM 5 | 2416.25 | AGM 6 | 1141.82 | 46.74 | 46.75 | 46.9 | 46.74 | 46.75 | 6460 | 46.75 | 47.01 | 33.7143 | -118.0064 | 4.489
GWD 6470 | Girth Weld |  | 18556.1 | 46.75 | 0.219 | 42000 | ERW | 6.625 | 728 | [10 empty] | AGM 5 | 2463 | AGM 6 | 1095.07 | 46.75 | 46.75 | 46.74 | 46.75 | 46.75 | 6470 | 47.01 | 45.31 | 33.7144 | -118.0064 | 5.583
GWD 6480 | Girth Weld |  | 18602.85 | 47.01 | 0.219 | 42000 | ERW | 6.625 | 728 | [10 empty] | AGM 5 | 2509.75 | AGM 6 | 1048.32 | 46.75 | 47.01 | 46.75 | 46.75 | 47.01 | 6480 | 45.31 | 42.71 | 33.7145 | -118.0064 | 5.669
GWD 6490 | Girth Weld |  | 18649.87 | 45.31 | 0.219 | 42000 | ERW | 6.625 | 728 | [10 empty] | AGM 5 | 2556.76 | AGM 6 | 1001.31 | 47.01 | 45.31 | 46.75 | 47.01 | 45.31 | 6490 | 42.71 | 4.69 | 33.7146 | -118.0064 | 5.995
GWD 6500 | Girth Weld |  | 18695.18 | 42.71 | 0.219 | 42000 | ERW | 6.625 | 728 | [10 empty] | AGM 5 | 2602.07 | AGM 6 | 956 | 45.31 | 42.71 | 47.01 | 45.31 | 42.71 | 6500 | 4.69 | 9.41 | 33.7148 | -118.0064 | 6.709
GWD 6510 | Girth Weld |  | 18737.89 | 1.33 | 0.25 | 42000 | SMLS | 6.625 | 728 | [10 empty] | AGM 5 | 2644.79 | AGM 6 | 913.28 | 42.71 | 4.69 | 45.31 | 42.71 | 4.69 | 6510 | 9.41 | 46.13 | 33.7149 | -118.0064 | 8.324 | Estimated WT 0.250
TAP 12 | TAP |  | 18739.22 | 3.36 | 0.25 | 42000 | SMLS | 6.625 | 728 |  |  |  |  | 12:06 | [5 empty] | AGM 5 | 2646.11 | AGM 6 | 911.96 | 1.33 | 3.36 | 45.31 | 42.71 | 4.69 | 6510 | 9.41 | 46.13 | 33.7149 | -118.0064 | 8.391 | Offtake
GWD 6520 | Girth Weld |  | 18742.58 | 9.41 | 0.25 | 42000 | SMLS | 6.625 | 728 | [10 empty] | AGM 5 | 2649.48 | AGM 6 | 908.59 | 4.69 | 9.41 | 42.71 | 4.69 | 9.41 | 6520 | 46.13 | 47.09 | 33.7149 | -118.0064 | 8.563
GWD 6530 | Girth Weld |  | 18752 | 46.13 | 0.25 | 42000 | SMLS | 6.625 | 728 | [10 empty] | AGM 5 | 2658.89 | AGM 6 | 899.18 | 9.41 | 46.13 | 4.69 | 9.41 | 46.13 | 6530 | 47.09 | 46.5 | 33.7149 | -118.0064 | 8.96
GWD 6540 | Girth Weld |  | 18798.12 | 47.09 | 0.25 | 42000 | SMLS | 6.625 | 728 | [10 empty] | AGM 5 | 2705.02 | AGM 6 | 853.05 | 46.13 | 47.09 | 9.41 | 46.13 | 47.09 | 6540 | 46.5 | 47.36 | 33.715 | -118.0064 | 9.491
GWD 6550 | Girth Weld |  | 18845.21 | 46.5 | 0.25 | 42000 | SMLS | 6.625 | 728 | [10 empty] | AGM 5 | 2752.11 | AGM 6 | 805.97 | 47.09 | 46.5 | 46.13 | 47.09 | 46.5 | 6550 | 47.36 | 47.55 | 33.7152 | -118.0064 | 10.397
GWD 6560 | Girth Weld |  | 18891.71 | 10.05 | 0.25 | 42000 | SMLS | 6.625 | 728 | [10 empty] | AGM 5 | 2798.6 | AGM 6 | 759.47 | 46.5 | 47.36 | 47.09 | 46.5 | 47.36 | 6560 | 47.55 | 35.1 | 33.7153 | -118.0064 | 10.738
PMA 32 | Pipe Mill | Ext | 18901.76 | 1.97 | 0.25 | 42000 | SMLS | 6.625 | 728 | 14.8357 | 0.037 | 0.315 | 0.518 | 1:40 | [5 empty] | AGM 5 | 2808.66 | AGM 6 | 749.42 | 10.05 | 37.31 | 47.09 | 46.5 | 47.36 | 6560 | 47.55 | 35.1 | 33.7153 | -118.0064 | 10.563
PMA 33 | Pipe Mill | Ext | 18903.73 | 35.34 | 0.25 | 42000 | SMLS | 6.625 | 728 | 27.6063 | 0.069 | 0.355 | 0.541 | 12:56 | [5 empty] | AGM 5 | 2810.63 | AGM 6 | 747.44 | 12.02 | 35.34 | 47.09 | 46.5 | 47.36 | 6560 | 47.55 | 35.1 | 33.7153 | -118.0064 | 10.528
GWD 6570 | Girth Weld |  | 18939.07 | 47.55 | 0.25 | 42000 | SMLS | 6.625 | 728 | [10 empty] | AGM 5 | 2845.96 | AGM 6 | 712.11 | 47.36 | 47.55 | 46.5 | 47.36 | 47.55 | 6570 | 35.1 | 43.19 | 33.7154 | -118.0064 | 10.878
GWD 6580 | Girth Weld |  | 18986.61 | 13.99 | 0.25 | 42000 | SMLS | 6.625 | 728 | [10 empty] | AGM 5 | 2893.51 | AGM 6 | 664.56 | 47.55 | 35.1 | 47.36 | 47.55 | 35.1 | 6580 | 43.19 | 42.67 | 33.7156 | -118.0064 | 12.056
PMA 34 | Pipe Mill | Ext | 19000.6 | 0.19 | 0.25 | 42000 | SMLS | 6.625 | 728 | 11.6198 | 0.029 | 0.748 | 0.695 | 6:50 | [5 empty] | AGM 5 | 2907.5 | AGM 6 | 650.58 | 13.99 | 21.11 | 47.36 | 47.55 | 35.1 | 6580 | 43.19 | 42.67 | 33.7156 | -118.0064 | 12.128
PMA 35 | Pipe Mill | Ext | 19000.79 | 20.92 | 0.25 | 42000 | SMLS | 6.625 | 728 | 10.8612 | 0.027 | 0.315 | 0.545 | 7:28 | [5 empty] | AGM 5 | 2907.69 | AGM 6 | 650.38 | 14.18 | 20.92 | 47.36 | 47.55 | 35.1 | 6580 | 43.19 | 42.67 | 33.7156 | -118.0064 | 12.125
GWD 6590 | Girth Weld |  | 19021.71 | 43.19 | 0.25 | 42000 | SMLS | 6.625 | 728 | [10 empty] | AGM 5 | 2928.61 | AGM 6 | 629.47 | 35.1 | 43.19 | 47.55 | 35.1 | 43.19 | 6590 | 42.67 | 33.12 | 33.7157 | -118.0064 | 11.843
GWD 6600 | Girth Weld |  | 19064.9 | 42.67 | 0.25 | 42000 | SMLS | 6.625 | 728 | [10 empty] | AGM 5 | 2971.8 | AGM 6 | 586.28 | 43.19 | 42.67 | 35.1 | 43.19 | 42.67 | 6600 | 33.12 | 30.24 | 33.7158 | -118.0064 | 10.944
GWD 6610 | Girth Weld |  | 19107.57 | 33.12 | 0.25 | 42000 | SMLS | 6.625 | 728 | [10 empty] | AGM 5 | 3014.47 | AGM 6 | 543.6 | 42.67 | 33.12 | 43.19 | 42.67 | 33.12 | 6610 | 30.24 | 43.52 | 33.7159 | -118.0064 | 10.659
GWD 6620 | Girth Weld |  | 19140.69 | 30.24 | 0.25 | 42000 | SMLS | 6.625 | 728 | [10 empty] | AGM 5 | 3047.58 | AGM 6 | 510.49 | 33.12 | 30.24 | 42.67 | 33.12 | 30.24 | 6620 | 43.52 | 45.6 | 33.716 | -118.0064 | 10.627
GWD 6630 | Girth Weld |  | 19170.93 | 1.99 | 0.25 | 42000 | SMLS | 6.625 | 728 | [10 empty] | AGM 5 | 3077.83 | AGM 6 | 480.24 | 30.24 | 43.52 | 33.12 | 30.24 | 43.52 | 6630 | 45.6 | 1.21 | 33.7161 | -118.0065 | 10.844
DMA 426 | Metal Loss | Ext | 19172.92 | 41.53 | 0.25 | 42000 | SMLS | 6.625 | 728 | 13.9054 | 0.035 | 0.407 | 0.546 | 2:45 | 3909 | 0.25866 | 14 | 0.41 | 3906 | AGM 5 | 3079.82 | AGM 6 | 478.25 | 1.99 | 41.53 | 33.12 | 30.24 | 43.52 | 6630 | 45.6 | 1.21 | 33.7161 | -118.0065 | 10.851
GWD 6640 | Girth Weld |  | 19214.45 | 45.6 | 0.25 | 42000 | SMLS | 6.625 | 728 | [10 empty] | AGM 5 | 3121.35 | AGM 6 | 436.72 | 43.52 | 45.6 | 30.24 | 43.52 | 45.6 | 6640 | 1.21 | 9.01 | 33.7162 | -118.0065 | 10.821
GWD 6650 | Girth Weld |  | 19260.05 | 0.74 | 0.25 | 42000 | SMLS | 6.625 | 728 | [10 empty] | AGM 5 | 3166.95 | AGM 6 | 391.12 | 45.6 | 1.21 | 43.52 | 45.6 | 1.21 | 6650 | 9.01 | 1.21 | 33.7163 | -118.0065 | 10.996
BND 72 | Bend |  | 19260.79 | 0.47 | 0.25 | 42000 | SMLS | 6.625 | 728 |  |  | 14.528 | [7 empty] | AGM 5 | 3167.69 | AGM 6 | 390.38 | 0.74 | 0.47 | 43.52 | 45.6 | 1.21 | 6650 | 9.01 | 1.21 | 33.7163 | -118.0065 | 11.019 | 3.0D 49.4 deg right turn sag bend
GWD 6660 | Girth Weld |  | 19261.26 | 9.01 | 0.25 | 42000 | SMLS | 6.625 | 728 | [10 empty] | AGM 5 | 3168.16 | AGM 6 | 389.91 | 1.21 | 9.01 | 45.6 | 1.21 | 9.01 | 6660 | 1.21 | 0.98 | 33.7163 | -118.0065 | 11.035
GWD 6670 | Girth Weld |  | 19270.27 | 0.78 | 0.25 | 42000 | SMLS | 6.625 | 728 | [10 empty] | AGM 5 | 3177.17 | AGM 6 | 380.9 | 9.01 | 1.21 | 1.21 | 9.01 | 1.21 | 6670 | 0.98 | 5.82 | 33.7163 | -118.0064 | 11.457
BND 73 | Bend |  | 19271.05 | 0.43 | 0.25 | 42000 | SMLS | 6.625 | 728 |  |  | 14.567 | [7 empty] | AGM 5 | 3177.94 | AGM 6 | 380.13 | 0.78 | 0.43 | 1.21 | 9.01 | 1.21 | 6670 | 0.98 | 5.82 | 33.7163 | -118.0064 | 11.501 | 3.0D 49.0 deg left turn over bend
GWD 6680 | Girth Weld |  | 19271.48 | 0.98 | 0.25 | 42000 | SMLS | 6.625 | 728 | [10 empty] | AGM 5 | 3178.38 | AGM 6 | 379.69 | 1.21 | 0.98 | 9.01 | 1.21 | 0.98 | 6680 | 5.82 | 7.96 | 33.7163 | -118.0064 | 11.52
GWD 6690 | Girth Weld |  | 19272.46 | 5.82 | 0.25 | 42000 | SMLS | 6.625 | 728 | [10 empty] | AGM 5 | 3179.36 | AGM 6 | 378.71 | 0.98 | 5.82 | 1.21 | 0.98 | 5.82 | 6690 | 7.96 | 18.89 | 33.7163 | -118.0064 | 11.557
GWD 6700 | Girth Weld |  | 19278.28 | 6.04 | 0.25 | 42000 | SMLS | 6.625 | 728 | [10 empty] | AGM 5 | 3185.18 | AGM 6 | 372.89 | 5.82 | 7.96 | 0.98 | 5.82 | 7.96 | 6700 | 18.89 | 17.32 | 33.7164 | -118.0064 | 11.765
PMA 36 | Pipe Mill | Ext | 19284.33 | 1.92 | 0.25 | 42000 | SMLS | 6.625 | 728 | 10.9029 | 0.027 | 0.761 | 0.752 | 10:21 | [5 empty] | AGM 5 | 3191.22 | AGM 6 | 366.85 | 6.04 | 1.92 | 0.98 | 5.82 | 7.96 | 6700 | 18.89 | 17.32 | 33.7164 | -118.0064 | 11.979
GWD 6710 | Girth Weld |  | 19286.24 | 18.89 | 0.25 | 42000 | SMLS | 6.625 | 728 | [10 empty] | AGM 5 | 3193.14 | AGM 6 | 364.93 | 7.96 | 18.89 | 5.82 | 7.96 | 18.89 | 6710 | 17.32 | 18.79 | 33.7164 | -118.0064 | 12.043
GWD 6720 | Girth Weld |  | 19305.13 | 17.32 | 0.312 | 42000 | SMLS | 6.625 | 728 | [10 empty] | AGM 5 | 3212.03 | AGM 6 | 346.04 | 18.89 | 17.32 | 7.96 | 18.89 | 17.32 | 6720 | 18.79 | 17.91 | 33.7164 | -118.0064 | 12.349 | Estimated WT 0.312
GWD 6730 | Girth Weld |  | 19322.45 | 10.75 | 0.25 | 42000 | SMLS | 6.625 | 728 | [10 empty] | AGM 5 | 3229.35 | AGM 6 | 328.72 | 17.32 | 18.79 | 18.89 | 17.32 | 18.79 | 6730 | 17.91 | 16.12 | 33.7165 | -118.0064 | 12.448 | Estimated WT 0.250
CLS 68 | Cluster | Ext | 19333.21 | 0.23 | 0.25 | 42000 | SMLS | 6.625 | 728 | 11.4584 | 0.029 | 1.637 | 2.832 | 10:10 | 3804 | 0.2658 | 11 | 1.64 | 3781 | AGM 5 | 3240.1 | AGM 6 | 317.97 | 10.75 | 8.04 | 18.89 | 17.32 | 18.79 | 6730 | 17.91 | 16.12 | 33.7165 | -118.0064 | 12.459 | CLS C
DMA 429 | Metal Loss | Ext | 19333.44 | 0.18 | 0.25 | 42000 | SMLS | 6.625 | 728 | 12.4592 | 0.031 | 0.983 | 0.583 | 11:44 | 3859 | 0.26201 | 12 | 0.98 | 3846 | AGM 5 | 3240.34 | AGM 6 | 317.74 | 10.98 | 7.81 | 18.89 | 17.32 | 18.79 | 6730 | 17.91 | 16.12 | 33.7165 | -118.0064 | 12.455
DMA 430 | Metal Loss | Ext | 19333.62 | 0.64 | 0.25 | 42000 | SMLS | 6.625 | 728 | 13.1926 | 0.033 | 0.612 | 0.594 | 10:58 | 3893 | 0.25973 | 13 | 0.61 | 3887 | AGM 5 | 3240.52 | AGM 6 | 317.55 | 11.17 | 7.63 | 18.89 | 17.32 | 18.79 | 6730 | 17.91 | 16.12 | 33.7165 | -118.0064 | 12.455
DMA 431 | Metal Loss | Ext | 19334.26 | 0.15 | 0.25 | 42000 | SMLS | 6.625 | 728 | 10.7948 | 0.027 | 0.826 | 0.882 | 3:41 | 3882 | 0.26046 | 11 | 0.83 | 3874 | AGM 5 | 3241.16 | AGM 6 | 316.92 | 11.81 | 6.99 | 18.89 | 17.32 | 18.79 | 6730 | 17.91 | 16.12 | 33.7165 | -118.0064 | 12.455
DMA 432 | Metal Loss | Ext | 19334.41 | 0.04 | 0.25 | 42000 | SMLS | 6.625 | 728 | 11.9667 | 0.03 | 1.559 | 0.732 | 6:18 | 3805 | 0.26573 | 12 | 1.56 | 3782 | AGM 5 | 3241.31 | AGM 6 | 316.76 | 11.96 | 6.84 | 18.89 | 17.32 | 18.79 | 6730 | 17.91 | 16.12 | 33.7165 | -118.0064 | 12.455
DMA 433 | Metal Loss | Ext | 19334.45 | 0.32 | 0.25 | 42000 | SMLS | 6.625 | 728 | 11.7148 | 0.029 | 1.06 | 0.867 | 12:02 | 3855 | 0.26229 | 12 | 1.06 | 3842 | AGM 5 | 3241.35 | AGM 6 | 316.72 | 12 | 6.8 | 18.89 | 17.32 | 18.79 | 6730 | 17.91 | 16.12 | 33.7165 | -118.0064 | 12.455
DMA 434 | Metal Loss | Ext | 19334.78 | 4.15 | 0.25 | 42000 | SMLS | 6.625 | 728 | 11.6859 | 0.029 | 0.888 | 0.604 | 10:46 | 3872 | 0.26113 | 12 | 0.89 | 3862 | AGM 5 | 3241.67 | AGM 6 | 316.4 | 12.32 | 6.47 | 18.89 | 17.32 | 18.79 | 6730 | 17.91 | 16.12 | 33.7165 | -118.0064 | 12.452
DMA 435 | Metal Loss | Ext | 19338.92 | 0.15 | 0.25 | 42000 | SMLS | 6.625 | 728 | 10.7002 | 0.027 | 0.604 | 0.686 | 4:01 | 3900 | 0.25926 | 11 | 0.6 | 3895 | AGM 5 | 3245.82 | AGM 6 | 312.25 | 16.47 | 2.33 | 18.89 | 17.32 | 18.79 | 6730 | 17.91 | 16.12 | 33.7165 | -118.0064 | 12.436
DMA 436 | Metal Loss | Ext | 19339.07 | 0.31 | 0.25 | 42000 | SMLS | 6.625 | 728 | 10.5287 | 0.026 | 0.85 | 0.629 | 4:33 | 3881 | 0.26053 | 11 | 0.85 | 3873 | AGM 5 | 3245.97 | AGM 6 | 312.1 | 16.62 | 2.18 | 18.89 | 17.32 | 18.79 | 6730 | 17.91 | 16.12 | 33.7165 | -118.0064 | 12.432
DMA 437 | Metal Loss | Ext | 19339.38 | 1.87 | 0.25 | 42000 | SMLS | 6.625 | 728 | 10.2549 | 0.026 | 0.628 | 0.668 | 6:43 | 3900 | 0.25926 | 10 | 0.63 | 3895 | AGM 5 | 3246.27 | AGM 6 | 311.8 | 16.92 | 1.87 | 18.89 | 17.32 | 18.79 | 6730 | 17.91 | 16.12 | 33.7165 | -118.0064 | 12.432
GWD 6740 | Girth Weld |  | 19341.25 | 1.08 | 0.25 | 42000 | SMLS | 6.625 | 728 | [10 empty] | AGM 5 | 3248.14 | AGM 6 | 309.93 | 18.79 | 17.91 | 17.32 | 18.79 | 17.91 | 6740 | 16.12 | 14.25 | 33.7165 | -118.0064 | 12.418
DMA 438 | Metal Loss | Ext | 19342.32 | 1.91 | 0.25 | 42000 | SMLS | 6.625 | 728 | 10.0238 | 0.025 | 1.14 | 0.921 | 7:16 | 3859 | 0.26201 | 10 | 1.14 | 3847 | AGM 5 | 3249.22 | AGM 6 | 308.85 | 1.08 | 16.84 | 17.32 | 18.79 | 17.91 | 6740 | 16.12 | 14.25 | 33.7165 | -118.0064 | 12.405
DMA 439 | Metal Loss | Ext | 19344.23 | 0.17 | 0.25 | 42000 | SMLS | 6.625 | 728 | 10.4914 | 0.026 | 1.435 | 0.998 | 6:37 | 3831 | 0.26393 | 10 | 1.44 | 3813 | AGM 5 | 3251.13 | AGM 6 | 306.94 | 2.98 | 14.93 | 17.32 | 18.79 | 17.91 | 6740 | 16.12 | 14.25 | 33.7165 | -118.0064 | 12.392
DMA 440 | Metal Loss | Ext | 19344.4 | 0.24 | 0.25 | 42000 | SMLS | 6.625 | 728 | 11.7355 | 0.029 | 1.053 | 1.081 | 1:44 | 3856 | 0.26222 | 12 | 1.05 | 3843 | AGM 5 | 3251.29 | AGM 6 | 306.78 | 3.15 | 14.76 | 17.32 | 18.79 | 17.91 | 6740 | 16.12 | 14.25 | 33.7165 | -118.0064 | 12.392
DMA 441 | Metal Loss | Ext | 19344.64 | 12.92 | 0.25 | 42000 | SMLS | 6.625 | 728 | 10.1778 | 0.025 | 0.906 | 0.743 | 5:08 | 3878 | 0.26073 | 10 | 0.91 | 3869 | AGM 5 | 3251.53 | AGM 6 | 306.54 | 3.39 | 14.52 | 17.32 | 18.79 | 17.91 | 6740 | 16.12 | 14.25 | 33.7165 | -118.0064 | 12.389
DMA 442 | Metal Loss | Ext | 19357.55 | 1.61 | 0.25 | 42000 | SMLS | 6.625 | 728 | 12.6001 | 0.032 | 0.685 | 0.651 | 1:55 | 3888 | 0.26006 | 13 | 0.68 | 3881 | AGM 5 | 3264.45 | AGM 6 | 293.62 | 16.31 | 1.61 | 17.32 | 18.79 | 17.91 | 6740 | 16.12 | 14.25 | 33.7166 | -118.0064 | 12.292
GWD 6750 | Girth Weld |  | 19359.16 | 16.12 | 0.312 | 42000 | SMLS | 6.625 | 728 | [10 empty] | AGM 5 | 3266.06 | AGM 6 | 292.01 | 17.91 | 16.12 | 18.79 | 17.91 | 16.12 | 6750 | 14.25 | 19.7 | 33.7166 | -118.0064 | 12.283 | Estimated WT 0.312
GWD 6760 | Girth Weld |  | 19375.29 | 14.25 | 0.312 | 42000 | SMLS | 6.625 | 728 | [10 empty] | AGM 5 | 3282.18 | AGM 6 | 275.89 | 16.12 | 14.25 | 17.91 | 16.12 | 14.25 | 6760 | 19.7 | 16.64 | 33.7166 | -118.0064 | 12.159
GWD 6770 | Girth Weld |  | 19389.54 | 19.7 | 0.312 | 42000 | SMLS | 6.625 | 728 | [10 empty] | AGM 5 | 3296.43 | AGM 6 | 261.64 | 14.25 | 19.7 | 16.12 | 14.25 | 19.7 | 6770 | 16.64 | 20.36 | 33.7167 | -118.0064 | 12.183
GWD 6780 | Girth Weld |  | 19409.23 | 16.64 | 0.28 | 42000 | SMLS | 6.625 | 728 | [10 empty] | AGM 5 | 3316.13 | AGM 6 | 241.94 | 19.7 | 16.64 | 14.25 | 19.7 | 16.64 | 6780 | 20.36 | 19.25 | 33.7167 | -118.0064 | 12.196
GWD 6790 | Girth Weld |  | 19425.88 | 20.36 | 0.203 | 42000 | SMLS | 6.625 | 728 | [10 empty] | AGM 5 | 3332.78 | AGM 6 | 225.3 | 16.64 | 20.36 | 19.7 | 16.64 | 20.36 | 6790 | 19.25 | 17.51 | 33.7168 | -118.0064 | 12.052 | Estimated WT 0.203
GWD 6800 | Girth Weld |  | 19446.24 | 19.25 | 0.25 | 42000 | SMLS | 6.625 | 728 | [10 empty] | AGM 5 | 3353.14 | AGM 6 | 204.93 | 20.36 | 19.25 | 16.64 | 20.36 | 19.25 | 6800 | 17.51 | 17.78 | 33.7168 | -118.0065 | 12.066 | Estimated WT 0.250
GWD 6810 | Girth Weld |  | 19465.49 | 17.51 | 0.25 | 42000 | SMLS | 6.625 | 728 | [10 empty] | AGM 5 | 3372.39 | AGM 6 | 185.68 | 19.25 | 17.51 | 20.36 | 19.25 | 17.51 | 6810 | 17.78 | 18.69 | 33.7169 | -118.0065 | 12.087
GWD 6820 | Girth Weld |  | 19483 | 0.47 | 0.312 | 42000 | SMLS | 6.625 | 728 | [10 empty] | AGM 5 | 3389.89 | AGM 6 | 168.18 | 17.51 | 17.78 | 19.25 | 17.51 | 17.78 | 6820 | 18.69 | 19.89 | 33.7169 | -118.0065 | 11.988 | Estimated WT 0.312
PMA 37 | Pipe Mill | Int | 19483.46 | 3.42 | 0.312 | 42000 | SMLS | 6.625 | 728 | 17.2511 | 0.054 | 0.336 | 0.917 | 3:35 | [5 empty] | AGM 5 | 3390.36 | AGM 6 | 167.71 | 0.47 | 17.31 | 19.25 | 17.51 | 17.78 | 6820 | 18.69 | 19.89 | 33.7169 | -118.0065 | 11.985
PMA 38 | Pipe Mill | Int | 19486.88 | 1.29 | 0.312 | 42000 | SMLS | 6.625 | 728 | 12.3093 | 0.038 | 0.315 | 1.016 | 6:41 | [5 empty] | AGM 5 | 3393.78 | AGM 6 | 164.29 | 3.88 | 13.9 | 19.25 | 17.51 | 17.78 | 6820 | 18.69 | 19.89 | 33.7169 | -118.0065 | 11.952
PMA 39 | Pipe Mill | Int | 19488.17 | 0.12 | 0.312 | 42000 | SMLS | 6.625 | 728 | 47.6274 | 0.149 | 0.333 | 0.601 | 5:51 | [5 empty] | AGM 5 | 3395.06 | AGM 6 | 163.01 | 5.17 | 12.61 | 19.25 | 17.51 | 17.78 | 6820 | 18.69 | 19.89 | 33.7169 | -118.0065 | 11.941
PMA 40 | Pipe Mill | Int | 19488.29 | 2.25 | 0.312 | 42000 | SMLS | 6.625 | 728 | 31.5888 | 0.099 | 0.319 | 0.478 | 4:59 | [5 empty] | AGM 5 | 3395.18 | AGM 6 | 162.89 | 5.29 | 12.49 | 19.25 | 17.51 | 17.78 | 6820 | 18.69 | 19.89 | 33.7169 | -118.0065 | 11.935
PMA 41 | Pipe Mill | Int | 19490.53 | 10.25 | 0.312 | 42000 | SMLS | 6.625 | 728 | 19.8734 | 0.062 | 0.393 | 0.591 | 6:15 | [5 empty] | AGM 5 | 3397.43 | AGM 6 | 160.64 | 7.53 | 10.25 | 19.25 | 17.51 | 17.78 | 6820 | 18.69 | 19.89 | 33.7169 | -118.0065 | 11.912
GWD 6830 | Girth Weld |  | 19500.78 | 18.69 | 0.25 | 42000 | SMLS | 6.625 | 728 | [10 empty] | AGM 5 | 3407.67 | AGM 6 | 150.4 | 17.78 | 18.69 | 17.51 | 17.78 | 18.69 | 6830 | 19.89 | 18.05 | 33.717 | -118.0065 | 11.792 | Estimated WT 0.250
GWD 6840 | Girth Weld |  | 19519.47 | 19.89 | 0.312 | 42000 | SMLS | 6.625 | 728 | [10 empty] | AGM 5 | 3426.37 | AGM 6 | 131.7 | 18.69 | 19.89 | 17.78 | 18.69 | 19.89 | 6840 | 18.05 | 19.57 | 33.717 | -118.0065 | 11.516 | Estimated WT 0.312
GWD 6850 | Girth Weld |  | 19539.36 | 18.05 | 0.25 | 42000 | SMLS | 6.625 | 728 | [10 empty] | AGM 5 | 3446.25 | AGM 6 | 111.82 | 19.89 | 18.05 | 18.69 | 19.89 | 18.05 | 6850 | 19.57 | 16.68 | 33.7171 | -118.0065 | 11.056 | Estimated WT 0.250
GWD 6860 | Girth Weld |  | 19557.41 | 19.57 | 0.312 | 42000 | SMLS | 6.625 | 728 | [10 empty] | AGM 5 | 3464.31 | AGM 6 | 93.76 | 18.05 | 19.57 | 19.89 | 18.05 | 19.57 | 6860 | 16.68 | 19.95 | 33.7171 | -118.0065 | 10.724 | Estimated WT 0.312
GWD 6870 | Girth Weld |  | 19576.98 | 16.68 | 0.312 | 42000 | SMLS | 6.625 | 728 | [10 empty] | AGM 5 | 3483.87 | AGM 6 | 74.2 | 19.57 | 16.68 | 18.05 | 19.57 | 16.68 | 6870 | 19.95 | 15.29 | 33.7172 | -118.0065 | 10.409
GWD 6880 | Girth Weld |  | 19593.65 | 19.95 | 0.312 | 42000 | SMLS | 6.625 | 728 | [10 empty] | AGM 5 | 3500.55 | AGM 6 | 57.52 | 16.68 | 19.95 | 19.57 | 16.68 | 19.95 | 6880 | 15.29 | 0.33 | 33.7172 | -118.0065 | 10.003
GWD 6890 | Girth Weld |  | 19613.6 | 15.29 | 0.203 | 42000 | SMLS | 6.625 | 728 | [10 empty] | AGM 5 | 3520.5 | AGM 6 | 37.57 | 19.95 | 15.29 | 16.68 | 19.95 | 15.29 | 6890 | 0.33 | 3.82 | 33.7173 | -118.0065 | 9.111 | Estimated WT 0.203
GWD 6900 | Girth Weld |  | 19628.89 | 0.04 | 0.203 | 42000 | SMLS | 6.625 | 728 | [10 empty] | AGM 5 | 3535.78 | AGM 6 | 22.29 | 15.29 | 0.33 | 19.95 | 15.29 | 0.33 | 6900 | 3.82 | 1.51 | 33.7173 | -118.0065 | 8.331
BND 74 | Bend |  | 19628.92 | 0.29 | 0.203 | 42000 | SMLS | 6.625 | 728 |  |  | 3.937 | [7 empty] | AGM 5 | 3535.82 | AGM 6 | 22.25 | 0.04 | 0.29 | 19.95 | 15.29 | 0.33 | 6900 | 3.82 | 1.51 | 33.7173 | -118.0065 | 8.333 | 1.5D 20.0 deg sag bend
GWD 6910 | Girth Weld |  | 19629.21 | 3.82 | 0.25 | 42000 | SMLS | 6.625 | 728 | [10 empty] | AGM 5 | 3536.11 | AGM 6 | 21.96 | 0.33 | 3.82 | 15.29 | 0.33 | 3.82 | 6910 | 1.51 | 15.85 | 33.7173 | -118.0065 | 8.378 | Estimated WT 0.250
GWD 6920 | Girth Weld |  | 19633.03 | 0.95 | 0.25 | 42000 | SMLS | 6.625 | 728 | [10 empty] | AGM 5 | 3539.93 | AGM 6 | 18.14 | 3.82 | 1.51 | 0.33 | 3.82 | 1.51 | 6920 | 15.85 | 1.18 | 33.7173 | -118.0065 | 9.294
BND 75 | Bend |  | 19633.98 | 0.56 | 0.25 | 42000 | SMLS | 6.625 | 728 |  |  | 18.15 | [7 empty] | AGM 5 | 3540.88 | AGM 6 | 17.19 | 0.95 | 0.56 | 0.33 | 3.82 | 1.51 | 6920 | 15.85 | 1.18 | 33.7173 | -118.0065 | 9.543 | 3.0D 46.6 deg right turn sag bend
GWD 6930 | Girth Weld |  | 19634.54 | 15.85 | 0.25 | 42000 | ERW | 6.625 | 728 | [10 empty] | AGM 5 | 3541.44 | AGM 6 | 16.63 | 1.51 | 15.85 | 3.82 | 1.51 | 15.85 | 6930 | 1.18 | 30.45 | 33.7173 | -118.0065 | 9.712
GWD 6940 | Girth Weld |  | 19650.39 | 0.73 | 0.25 | 42000 | ERW | 6.625 | 728 | [10 empty] | AGM 5 | 3557.29 | AGM 6 | 0.78 | 15.85 | 1.18 | 1.51 | 15.85 | 1.18 | 6940 | 30.45 | 18.44 | 33.7174 | -118.0064 | 14.939
BND 76 | Bend |  | 19651.13 | 0.05 | 0.25 | 42000 | ERW | 6.625 | 728 |  |  | 21.638 | [7 empty] | AGM 5 | 3558.02 | AGM 6 | 0.05 | 0.73 | 0.44 | 1.51 | 15.85 | 1.18 | 6940 | 30.45 | 18.44 | 33.7174 | -118.0064 | 15.163 | 3.0D 50.4 deg left turn over bend
MRK 4 | Marker |  | 19651.17 | 0.4 | 0.25 | 42000 | ERW | 6.625 | 728 |  |  |  |  | 3:26 | [5 empty] | AGM 5 | 3558.07 | AGM 7 | 2751.05 | 0.78 | 0.4 | 1.51 | 15.85 | 1.18 | 6940 | 30.45 | 18.44 | 33.7174 | -118.0064 | 15.174 | AGM 6 7' East of Goldwest St Curb - 2' U/S of Fence at Paint Mark
GWD 6950 | Girth Weld |  | 19651.57 | 0.11 | 0.25 | 42000 | SMLS | 6.625 | 728 | [10 empty] | AGM 6 | 0.4 | AGM 7 | 2750.65 | 1.18 | 30.45 | 15.85 | 1.18 | 30.45 | 6950 | 18.44 | 1.13 | 33.7174 | -118.0064 | 15.243
CSG 1 | Casing Start |  | 19651.69 | 7.61 | 0.25 | 42000 | SMLS | 6.625 | 728 |  |  | 91.291 | [7 empty] | AGM 6 | 0.51 | AGM 7 | 2750.54 | 0.11 | 30.33 | 15.85 | 1.18 | 30.45 | 6950 | 18.44 | 1.13 | 33.7174 | -118.0064 | 15.255 | Casing - Start¦With PMA
CSG 1 | Casing End |  | 19659.29 | 22.72 | 0.25 | 42000 | SMLS | 6.625 | 728 | [10 empty] | AGM 6 | 8.12 | AGM 7 | 2742.93 | 7.72 | 22.72 | 15.85 | 1.18 | 30.45 | 6950 | 18.44 | 1.13 | 33.7174 | -118.0064 | 15.722 | Casing - End¦With PMA
GWD 6960 | Girth Weld |  | 19682.02 | 7.44 | 0.25 | 42000 | SMLS | 6.625 | 728 | [10 empty] | AGM 6 | 30.84 | AGM 7 | 2720.21 | 30.45 | 18.44 | 1.18 | 30.45 | 18.44 | 6960 | 1.13 | 0.53 | 33.7174 | -118.0064 | 15.843
MOB 1 | Metal Object |  | 19689.46 | 0.32 | 0.25 | 42000 | SMLS | 6.625 | 728 |  |  | 0.961 | 11.388 | 11:33 | [5 empty] | AGM 6 | 38.29 | AGM 7 | 2712.76 | 7.44 | 11 | 1.18 | 30.45 | 18.44 | 6960 | 1.13 | 0.53 | 33.7175 | -118.0064 | 15.673 | Close Metal Object
DMA 443 | Metal Loss | Ext | 19689.79 | 8.87 | 0.25 | 42000 | SMLS | 6.625 | 728 | 15.1378 | 0.038 | 1.678 | 1.026 | 7:00 | 3757 | 0.26913 | 15 | 1.68 | 3723 | AGM 6 | 38.61 | AGM 7 | 2712.44 | 7.77 | 10.67 | 1.18 | 30.45 | 18.44 | 6960 | 1.13 | 0.53 | 33.7175 | -118.0064 | 15.665
TAP 13 | TAP |  | 19698.66 | 1.8 | 0.25 | 42000 | SMLS | 6.625 | 728 |  |  |  |  | 11:44 | [5 empty] | AGM 6 | 47.48 | AGM 7 | 2703.57 | 16.64 | 1.8 | 1.18 | 30.45 | 18.44 | 6960 | 1.13 | 0.53 | 33.7175 | -118.0064 | 15.476
GWD 6970 | Girth Weld |  | 19700.46 | 1.13 | 0.25 | 42000 | ERW | 6.625 | 728 | [10 empty] | AGM 6 | 49.29 | AGM 7 | 2701.76 | 18.44 | 1.13 | 30.45 | 18.44 | 1.13 | 6970 | 0.53 | 3.28 | 33.7175 | -118.0064 | 15.447
GWD 6980 | Girth Weld |  | 19701.59 | 0.44 | 0.25 | 42000 | ERW | 6.625 | 728 | [10 empty] | AGM 6 | 50.42 | AGM 7 | 2700.63 | 1.13 | 0.53 | 18.44 | 1.13 | 0.53 | 6980 | 3.28 | 0.59 | 33.7175 | -118.0064 | 15.409
BND 77 | Bend |  | 19702.03 | 0.09 | 0.25 | 42000 | ERW | 6.625 | 728 |  |  | 6.299 | [7 empty] | AGM 6 | 50.86 | AGM 7 | 2700.19 | 0.44 | 0.09 | 18.44 | 1.13 | 0.53 | 6980 | 3.28 | 0.59 | 33.7175 | -118.0064 | 15.401 | 3.0D 22.9 deg right turn sag bend
GWD 6990 | Girth Weld |  | 19702.12 | 3.28 | 0.25 | 42000 | ERW | 6.625 | 728 | [10 empty] | AGM 6 | 50.95 | AGM 7 | 2700.1 | 0.53 | 3.28 | 1.13 | 0.53 | 3.28 | 6990 | 0.59 | 0.51 | 33.7175 | -118.0064 | 15.402
GWD 7000 | Girth Weld |  | 19705.4 | 0.59 | 0.25 | 42000 | ERW | 6.625 | 728 | [10 empty] | AGM 6 | 54.23 | AGM 7 | 2696.82 | 3.28 | 0.59 | 0.53 | 3.28 | 0.59 | 7000 | 0.51 | 3.14 | 33.7175 | -118.0064 | 15.56
GWD 7010 | Girth Weld |  | 19705.99 | 0.26 | 0.25 | 42000 | ERW | 6.625 | 728 | [10 empty] | AGM 6 | 54.82 | AGM 7 | 2696.23 | 0.59 | 0.51 | 3.28 | 0.59 | 0.51 | 7010 | 3.14 | 18.29 | 33.7175 | -118.0064 | 15.568
RED 2 | Reducer |  | 19706.25 | 0.08 | 0.25 | 42000 | ERW | 6.625 | 728 |  |  |  |  | 9:04 | [5 empty] | AGM 6 | 55.08 | AGM 7 | 2695.97 | 0.26 | 0.25 | 3.28 | 0.59 | 0.51 | 7010 | 3.14 | 18.29 | 33.7175 | -118.0064 | 15.554 | Reducer NPS 6 x 8
BND 78 | Bend |  | 19706.33 | 0.17 | 0.25 | 42000 | ERW | 6.625 | 728 |  |  | 6.299 | [7 empty] | AGM 6 | 55.16 | AGM 7 | 2695.89 | 0.34 | 0.17 | 3.28 | 0.59 | 0.51 | 7010 | 3.14 | 18.29 | 33.7175 | -118.0064 | 15.548 | 3.0D 20.0 deg left turn over bend
GWD 7020 | Girth Weld |  | 19706.5 | 3.14 | 0.219 | 42000 | ERW | 8.625 | 728 | [10 empty] | AGM 6 | 55.33 | AGM 7 | 2695.72 | 0.51 | 3.14 | 0.59 | 0.51 | 3.14 | 7020 | 18.29 | 1.5 | 33.7175 | -118.0064 | 15.532 | Estimated WT 0.219
GWD 7030 | Girth Weld |  | 19709.64 | 5.35 | 0.28 | 42000 | SMLS | 8.625 | 728 | [10 empty] | AGM 6 | 58.47 | AGM 7 | 2692.58 | 3.14 | 18.29 | 0.51 | 3.14 | 18.29 | 7030 | 1.5 | 3.65 | 33.7175 | -118.0064 | 14.923
TAP 14 | TAP |  | 19714.99 | 5.6 | 0.28 | 42000 | SMLS | 8.625 | 728 |  |  |  |  | 11:48 | [5 empty] | AGM 6 | 63.81 | AGM 7 | 2687.24 | 5.35 | 12.94 | 0.51 | 3.14 | 18.29 | 7030 | 1.5 | 3.65 | 33.7175 | -118.0064 | 14.532
CSG 2 | Casing Start |  | 19720.59 | 7.18 | 0.28 | 42000 | SMLS | 8.625 | 728 |  |  | 86.175 | [7 empty] | AGM 6 | 69.41 | AGM 7 | 2681.64 | 10.95 | 7.34 | 0.51 | 3.14 | 18.29 | 7030 | 1.5 | 3.65 | 33.7176 | -118.0064 | 14.116 | Casing - Start
CSG 2 | Casing End |  | 19727.77 | 0.16 | 0.28 | 42000 | SMLS | 8.625 | 728 | [10 empty] | AGM 6 | 76.59 | AGM 7 | 2674.46 | 18.13 | 0.16 | 0.51 | 3.14 | 18.29 | 7030 | 1.5 | 3.65 | 33.7176 | -118.0064 | 13.63 | Casing - End
GWD 7040 | Girth Weld |  | 19727.93 | 0.7 | 0.28 | 42000 | SMLS | 8.625 | 728 | [10 empty] | AGM 6 | 76.75 | AGM 7 | 2674.3 | 18.29 | 1.5 | 3.14 | 18.29 | 1.5 | 7040 | 3.65 | 3.14 | 33.7176 | -118.0064 | 13.611
BND 79 | Bend |  | 19728.63 | 0.79 | 0.28 | 42000 | SMLS | 8.625 | 728 |  |  | 24.386 | [7 empty] | AGM 6 | 77.46 | AGM 7 | 2673.59 | 0.7 | 0.79 | 3.14 | 18.29 | 1.5 | 7040 | 3.65 | 3.14 | 33.7176 | -118.0064 | 13.416 | 3.0D 45.7 deg right turn over bend
GWD 7050 | Girth Weld |  | 19729.42 | 3.65 | 0.28 | 42000 | ERW | 8.625 | 728 | [10 empty] | AGM 6 | 78.25 | AGM 7 | 2672.8 | 1.5 | 3.65 | 18.29 | 1.5 | 3.65 | 7050 | 3.14 | 10.72 | 33.7176 | -118.0064 | 12.962
GWD 7060 | Girth Weld |  | 19733.07 | 1.87 | 0.28 | 42000 | ERW | 8.625 | 728 | [10 empty] | AGM 6 | 81.9 | AGM 7 | 2669.15 | 3.65 | 3.14 | 1.5 | 3.65 | 3.14 | 7060 | 10.72 | 3.11 | 33.7176 | -118.0064 | 10.234
BND 80 | Bend |  | 19734.95 | 1.27 | 0.28 | 42000 | ERW | 8.625 | 728 |  |  | 41.201 | [7 empty] | AGM 6 | 83.77 | AGM 7 | 2667.28 | 1.87 | 1.27 | 1.5 | 3.65 | 3.14 | 7060 | 10.72 | 3.11 | 33.7176 | -118.0064 | 8.918 | 3.0D 90.7 deg left turn sag bend
GWD 7070 | Girth Weld |  | 19736.22 | 10.72 | 0.28 | 42000 | ERW | 8.625 | 728 | [10 empty] | AGM 6 | 85.04 | AGM 7 | 2666.01 | 3.14 | 10.72 | 3.65 | 3.14 | 10.72 | 7070 | 3.11 | 42.04 | 33.7176 | -118.0064 | 8.392
GWD 7080 | Girth Weld |  | 19746.94 | 1.53 | 0.28 | 42000 | ERW | 8.625 | 728 | [10 empty] | AGM 6 | 95.76 | AGM 7 | 2655.29 | 10.72 | 3.11 | 3.14 | 10.72 | 3.11 | 7080 | 42.04 | 61.76 | 33.7176 | -118.0065 | 7.828
BND 81 | Bend |  | 19748.47 | 1.58 | 0.28 | 42000 | ERW | 8.625 | 728 |  |  | 38.1 | [7 empty] | AGM 6 | 97.29 | AGM 7 | 2653.76 | 1.53 | 1.58 | 3.14 | 10.72 | 3.11 | 7080 | 42.04 | 61.76 | 33.7176 | -118.0065 | 7.769 | 3.0D 89.7 deg right turn sag bend
GWD 7090 | Girth Weld |  | 19750.05 | 42.04 | 0.28 | 42000 | ERW | 8.625 | 728 | [10 empty] | AGM 6 | 98.87 | AGM 7 | 2652.18 | 3.11 | 42.04 | 10.72 | 3.11 | 42.04 | 7090 | 61.76 | 61.55 | 33.7176 | -118.0065 | 7.736
GWD 7100 | Girth Weld |  | 19792.09 | 61.76 | 0.28 | 42000 | ERW | 8.625 | 728 | [10 empty] | AGM 6 | 140.91 | AGM 7 | 2610.14 | 42.04 | 61.76 | 3.11 | 42.04 | 61.76 | 7100 | 61.55 | 61.83 | 33.7177 | -118.0065 | 7.737
GWD 7110 | Girth Weld |  | 19853.85 | 61.55 | 0.28 | 42000 | ERW | 8.625 | 728 | [10 empty] | AGM 6 | 202.68 | AGM 7 | 2548.37 | 61.76 | 61.55 | 42.04 | 61.76 | 61.55 | 7110 | 61.83 | 58.98 | 33.7179 | -118.0065 | 8.376
GWD 7120 | Girth Weld |  | 19915.4 | 61.83 | 0.28 | 42000 | ERW | 8.625 | 728 | [10 empty] | AGM 6 | 264.22 | AGM 7 | 2486.83 | 61.55 | 61.83 | 61.76 | 61.55 | 61.83 | 7120 | 58.98 | 61.68 | 33.718 | -118.0065 | 7.848
GWD 7130 | Girth Weld |  | 19977.23 | 58.98 | 0.28 | 42000 | ERW | 8.625 | 728 | [10 empty] | AGM 6 | 326.05 | AGM 7 | 2425 | 61.83 | 58.98 | 61.55 | 61.83 | 58.98 | 7130 | 61.68 | 61.86 | 33.7182 | -118.0065 | 8.849
GWD 7140 | Girth Weld |  | 20036.21 | 61.68 | 0.28 | 42000 | ERW | 8.625 | 728 | [10 empty] | AGM 6 | 385.04 | AGM 7 | 2366.01 | 58.98 | 61.68 | 61.83 | 58.98 | 61.68 | 7140 | 61.86 | 61.87 | 33.7184 | -118.0065 | 8.859
GWD 7150 | Girth Weld |  | 20097.9 | 61.86 | 0.28 | 42000 | ERW | 8.625 | 728 | [10 empty] | AGM 6 | 446.72 | AGM 7 | 2304.33 | 61.68 | 61.86 | 58.98 | 61.68 | 61.86 | 7150 | 61.87 | 61.84 | 33.7185 | -118.0065 | 9.345
GWD 7160 | Girth Weld |  | 20159.75 | 61.87 | 0.28 | 42000 | ERW | 8.625 | 728 | [10 empty] | AGM 6 | 508.58 | AGM 7 | 2242.47 | 61.86 | 61.87 | 61.68 | 61.86 | 61.87 | 7160 | 61.84 | 61.31 | 33.7187 | -118.0065 | 10.053
GWD 7170 | Girth Weld |  | 20221.62 | 61.84 | 0.28 | 42000 | ERW | 8.625 | 728 | [10 empty] | AGM 6 | 570.45 | AGM 7 | 2180.6 | 61.87 | 61.84 | 61.86 | 61.87 | 61.84 | 7170 | 61.31 | 61.83 | 33.7189 | -118.0065 | 10.332
GWD 7180 | Girth Weld |  | 20283.47 | 61.31 | 0.28 | 42000 | ERW | 8.625 | 728 | [10 empty] | AGM 6 | 632.29 | AGM 7 | 2118.76 | 61.84 | 61.31 | 61.87 | 61.84 | 61.31 | 7180 | 61.83 | 61.88 | 33.7191 | -118.0065 | 10.901
GWD 7190 | Girth Weld |  | 20344.77 | 61.83 | 0.28 | 42000 | ERW | 8.625 | 728 | [10 empty] | AGM 6 | 693.6 | AGM 7 | 2057.45 | 61.31 | 61.83 | 61.84 | 61.31 | 61.83 | 7190 | 61.88 | 59.98 | 33.7192 | -118.0065 | 10.119
GWD 7200 | Girth Weld |  | 20406.6 | 61.88 | 0.28 | 42000 | ERW | 8.625 | 728 | [10 empty] | AGM 6 | 755.43 | AGM 7 | 1995.62 | 61.83 | 61.88 | 61.31 | 61.83 | 61.88 | 7200 | 59.98 | 61.43 | 33.7194 | -118.0065 | 10.896
GWD 7210 | Girth Weld |  | 20468.49 | 59.98 | 0.28 | 42000 | ERW | 8.625 | 728 | [10 empty] | AGM 6 | 817.31 | AGM 7 | 1933.74 | 61.88 | 59.98 | 61.83 | 61.88 | 59.98 | 7210 | 61.43 | 61.86 | 33.7196 | -118.0065 | 11.947
GWD 7220 | Girth Weld |  | 20528.47 | 61.43 | 0.28 | 42000 | ERW | 8.625 | 728 | [10 empty] | AGM 6 | 877.29 | AGM 7 | 1873.76 | 59.98 | 61.43 | 61.88 | 59.98 | 61.43 | 7220 | 61.86 | 61.82 | 33.7197 | -118.0065 | 11.922
GWD 7230 | Girth Weld |  | 20589.89 | 61.86 | 0.28 | 42000 | ERW | 8.625 | 728 | [10 empty] | AGM 6 | 938.72 | AGM 7 | 1812.33 | 61.43 | 61.86 | 59.98 | 61.43 | 61.86 | 7230 | 61.82 | 61.71 | 33.7199 | -118.0065 | 12.725
GWD 7240 | Girth Weld |  | 20651.76 | 61.82 | 0.28 | 42000 | ERW | 8.625 | 728 | [10 empty] | AGM 6 | 1000.58 | AGM 7 | 1750.47 | 61.86 | 61.82 | 61.43 | 61.86 | 61.82 | 7240 | 61.71 | 61.53 | 33.7201 | -118.0065 | 12.285
GWD 7250 | Girth Weld |  | 20713.58 | 2.11 | 0.28 | 42000 | ERW | 8.625 | 728 | [10 empty] | AGM 6 | 1062.4 | AGM 7 | 1688.65 | 61.82 | 61.71 | 61.86 | 61.82 | 61.71 | 7250 | 61.53 | 61.79 | 33.7202 | -118.0065 | 12.148
DMA 444 | Metal Loss | Ext | 20715.69 | 59.6 | 0.28 | 42000 | ERW | 8.625 | 728 | 34.9627 | 0.098 | 1.219 | 0.739 | 3:53 | 3175 | 0.31846 | 35 | 1.22 | 3124 | AGM 6 | 1064.51 | AGM 7 | 1686.54 | 2.11 | 59.6 | 61.86 | 61.82 | 61.71 | 7250 | 61.53 | 61.79 | 33.7202 | -118.0065 | 12.128
GWD 7260 | Girth Weld |  | 20775.29 | 61.53 | 0.28 | 42000 | ERW | 8.625 | 728 | [10 empty] | AGM 6 | 1124.11 | AGM 7 | 1626.94 | 61.71 | 61.53 | 61.82 | 61.71 | 61.53 | 7260 | 61.79 | 61.65 | 33.7204 | -118.0065 | 12.132
GWD 7270 | Girth Weld |  | 20836.81 | 61.79 | 0.28 | 42000 | ERW | 8.625 | 728 | [10 empty] | AGM 6 | 1185.64 | AGM 7 | 1565.41 | 61.53 | 61.79 | 61.71 | 61.53 | 61.79 | 7270 | 61.65 | 61.61 | 33.7206 | -118.0065 | 12.625
GWD 7280 | Girth Weld |  | 20898.61 | 61.65 | 0.28 | 42000 | ERW | 8.625 | 728 | [10 empty] | AGM 6 | 1247.43 | AGM 7 | 1503.62 | 61.79 | 61.65 | 61.53 | 61.79 | 61.65 | 7280 | 61.61 | 61.78 | 33.7208 | -118.0065 | 12.877
GWD 7290 | Girth Weld |  | 20960.26 | 61.61 | 0.28 | 42000 | ERW | 8.625 | 728 | [10 empty] | AGM 6 | 1309.08 | AGM 7 | 1441.97 | 61.65 | 61.61 | 61.79 | 61.65 | 61.61 | 7290 | 61.78 | 59.4 | 33.7209 | -118.0065 | 13.502
GWD 7300 | Girth Weld |  | 21021.86 | 61.78 | 0.28 | 42000 | ERW | 8.625 | 728 | [10 empty] | AGM 6 | 1370.69 | AGM 7 | 1380.36 | 61.61 | 61.78 | 61.65 | 61.61 | 61.78 | 7300 | 59.4 | 61.74 | 33.7211 | -118.0065 | 13.822
GWD 7310 | Girth Weld |  | 21083.64 | 59.4 | 0.28 | 42000 | ERW | 8.625 | 728 | [10 empty] | AGM 6 | 1432.47 | AGM 7 | 1318.58 | 61.78 | 59.4 | 61.61 | 61.78 | 59.4 | 7310 | 61.74 | 61.6 | 33.7213 | -118.0065 | 13.048
GWD 7320 | Girth Weld |  | 21143.04 | 61.74 | 0.28 | 42000 | ERW | 8.625 | 728 | [10 empty] | AGM 6 | 1491.87 | AGM 7 | 1259.18 | 59.4 | 61.74 | 61.78 | 59.4 | 61.74 | 7320 | 61.6 | 61.71 | 33.7214 | -118.0065 | 12.595
GWD 7330 | Girth Weld |  | 21204.78 | 61.6 | 0.28 | 42000 | ERW | 8.625 | 728 | [10 empty] | AGM 6 | 1553.61 | AGM 7 | 1197.44 | 61.74 | 61.6 | 59.4 | 61.74 | 61.6 | 7330 | 61.71 | 61.73 | 33.7216 | -118.0065 | 14.616
GWD 7340 | Girth Weld |  | 21266.38 | 61.71 | 0.28 | 42000 | ERW | 8.625 | 728 | [10 empty] | AGM 6 | 1615.2 | AGM 7 | 1135.85 | 61.6 | 61.71 | 61.74 | 61.6 | 61.71 | 7340 | 61.73 | 61.54 | 33.7218 | -118.0065 | 14.645
GWD 7350 | Girth Weld |  | 21328.09 | 61.73 | 0.28 | 42000 | ERW | 8.625 | 728 | [10 empty] | AGM 6 | 1676.92 | AGM 7 | 1074.13 | 61.71 | 61.73 | 61.6 | 61.71 | 61.73 | 7350 | 61.54 | 61.34 | 33.7219 | -118.0065 | 14.628
GWD 7360 | Girth Weld |  | 21389.82 | 61.54 | 0.28 | 42000 | ERW | 8.625 | 728 | [10 empty] | AGM 6 | 1738.65 | AGM 7 | 1012.4 | 61.73 | 61.54 | 61.71 | 61.73 | 61.54 | 7360 | 61.34 | 30.34 | 33.7221 | -118.0065 | 14.484
GWD 7370 | Girth Weld |  | 21451.36 | 61.34 | 0.28 | 42000 | ERW | 8.625 | 728 | [10 empty] | AGM 6 | 1800.19 | AGM 7 | 950.86 | 61.54 | 61.34 | 61.73 | 61.54 | 61.34 | 7370 | 30.34 | 1.3 | 33.7223 | -118.0065 | 14.553
GWD 7380 | Girth Weld |  | 21512.7 | 30.34 | 0.28 | 42000 | ERW | 8.625 | 728 | [10 empty] | AGM 6 | 1861.53 | AGM 7 | 889.52 | 61.34 | 30.34 | 61.54 | 61.34 | 30.34 | 7380 | 1.3 | 1.14 | 33.7224 | -118.0065 | 15.132
GWD 7390 | Girth Weld |  | 21543.04 | 1.3 | 0.28 | 42000 | ERW | 8.625 | 728 | [10 empty] | AGM 6 | 1891.87 | AGM 7 | 859.18 | 30.34 | 1.3 | 61.34 | 30.34 | 1.3 | 7390 | 1.14 | 1.29 | 33.7225 | -118.0065 | 14.776
GWD 7400 | Girth Weld |  | 21544.34 | 0.58 | 0.28 | 42000 | ERW | 8.625 | 728 | [10 empty] | AGM 6 | 1893.17 | AGM 7 | 857.88 | 1.3 | 1.14 | 30.34 | 1.3 | 1.14 | 7400 | 1.29 | 21.57 | 33.7225 | -118.0065 | 14.747
TEE 3 | Tee |  | 21544.92 | 0.56 | 0.28 | 42000 | ERW | 8.625 | 728 |  |  | 9.303 | 9.303 | 5:38 | [5 empty] | AGM 6 | 1893.75 | AGM 7 | 857.3 | 0.58 | 0.56 | 30.34 | 1.3 | 1.14 | 7400 | 1.29 | 21.57 | 33.7225 | -118.0065 | 14.73
GWD 7410 | Girth Weld |  | 21545.48 | 1.29 | 0.28 | 42000 | ERW | 8.625 | 728 | [10 empty] | AGM 6 | 1894.3 | AGM 7 | 856.75 | 1.14 | 1.29 | 1.3 | 1.14 | 1.29 | 7410 | 21.57 | 43.88 | 33.7225 | -118.0065 | 14.721
GWD 7420 | Girth Weld |  | 21546.77 | 21.57 | 0.28 | 42000 | ERW | 8.625 | 728 | [10 empty] | AGM 6 | 1895.59 | AGM 7 | 855.46 | 1.29 | 21.57 | 1.14 | 1.29 | 21.57 | 7420 | 43.88 | 6.22 | 33.7225 | -118.0065 | 14.701
GWD 7430 | Girth Weld |  | 21568.34 | 43.88 | 0.28 | 42000 | ERW | 8.625 | 728 | [10 empty] | AGM 6 | 1917.16 | AGM 7 | 833.89 | 21.57 | 43.88 | 1.29 | 21.57 | 43.88 | 7430 | 6.22 | 11.75 | 33.7226 | -118.0066 | 14.712
GWD 7440 | Girth Weld |  | 21612.22 | 6.22 | 0.28 | 42000 | ERW | 8.625 | 728 | [10 empty] | AGM 6 | 1961.04 | AGM 7 | 790.01 | 43.88 | 6.22 | 21.57 | 43.88 | 6.22 | 7440 | 11.75 | 41.01 | 33.7227 | -118.0066 | 14.077
GWD 7450 | Girth Weld |  | 21618.43 | 11.75 | 0.28 | 42000 | ERW | 8.625 | 728 | [10 empty] | AGM 6 | 1967.26 | AGM 7 | 783.79 | 6.22 | 11.75 | 43.88 | 6.22 | 11.75 | 7450 | 41.01 | 43.35 | 33.7227 | -118.0066 | 14.183
GWD 7460 | Girth Weld |  | 21630.19 | 41.01 | 0.28 | 42000 | ERW | 8.625 | 728 | [10 empty] | AGM 6 | 1979.01 | AGM 7 | 772.04 | 11.75 | 41.01 | 6.22 | 11.75 | 41.01 | 7460 | 43.35 | 42.47 | 33.7228 | -118.0066 | 14.592
GWD 7470 | Girth Weld |  | 21671.19 | 43.35 | 0.28 | 42000 | ERW | 8.625 | 728 | [10 empty] | AGM 6 | 2020.02 | AGM 7 | 731.03 | 41.01 | 43.35 | 11.75 | 41.01 | 43.35 | 7470 | 42.47 | 41.12 | 33.7229 | -118.0066 | 15.606
GWD 7480 | Girth Weld |  | 21714.55 | 42.47 | 0.28 | 42000 | ERW | 8.625 | 728 | [10 empty] | AGM 6 | 2063.37 | AGM 7 | 687.68 | 43.35 | 42.47 | 41.01 | 43.35 | 42.47 | 7480 | 41.12 | 41.36 | 33.723 | -118.0066 | 15.367
GWD 7490 | Girth Weld |  | 21757.02 | 31.9 | 0.28 | 42000 | ERW | 8.625 | 728 | [10 empty] | AGM 6 | 2105.84 | AGM 7 | 645.21 | 42.47 | 41.12 | 43.35 | 42.47 | 41.12 | 7490 | 41.36 | 42.51 | 33.7231 | -118.0066 | 15.251
DMA 445 | Metal Loss | Ext | 21788.92 | 0.31 | 0.28 | 42000 | ERW | 8.625 | 728 | 14.7233 | 0.041 | 0.698 | 0.661 | 6:11 | 3349 | 0.30191 | 15 | 0.7 | 3343 | AGM 6 | 2137.74 | AGM 7 | 613.31 | 31.9 | 9.23 | 43.35 | 42.47 | 41.12 | 7490 | 41.36 | 42.51 | 33.7232 | -118.0066 | 15.461
DMA 446 | Metal Loss | Ext | 21789.23 | 0.7 | 0.28 | 42000 | ERW | 8.625 | 728 | 10.8227 | 0.03 | 0.719 | 0.743 | 5:07 | 3356 | 0.30128 | 11 | 0.72 | 3351 | AGM 6 | 2138.06 | AGM 7 | 612.99 | 32.21 | 8.91 | 43.35 | 42.47 | 41.12 | 7490 | 41.36 | 42.51 | 33.7232 | -118.0066 | 15.464
DMA 447 | Metal Loss | Ext | 21789.94 | 1.3 | 0.28 | 42000 | ERW | 8.625 | 728 | 17.7974 | 0.05 | 0.766 | 0.61 | 6:21 | 3336 | 0.30309 | 18 | 0.77 | 3327 | AGM 6 | 2138.76 | AGM 7 | 612.29 | 32.92 | 8.21 | 43.35 | 42.47 | 41.12 | 7490 | 41.36 | 42.51 | 33.7232 | -118.0066 | 15.473
DMA 448 | Metal Loss | Ext | 21791.24 | 6.9 | 0.28 | 42000 | ERW | 8.625 | 728 | 13.989 | 0.039 | 0.506 | 0.553 | 5:47 | 3362 | 0.30075 | 14 | 0.51 | 3359 | AGM 6 | 2140.07 | AGM 7 | 610.98 | 34.22 | 6.9 | 43.35 | 42.47 | 41.12 | 7490 | 41.36 | 42.51 | 33.7232 | -118.0066 | 15.49
GWD 7500 | Girth Weld |  | 21798.14 | 41.36 | 0.28 | 42000 | ERW | 8.625 | 728 | [10 empty] | AGM 6 | 2146.97 | AGM 7 | 604.08 | 41.12 | 41.36 | 42.47 | 41.12 | 41.36 | 7500 | 42.51 | 43.38 | 33.7232 | -118.0066 | 15.587
GWD 7510 | Girth Weld |  | 21839.5 | 42.51 | 0.28 | 42000 | ERW | 8.625 | 728 | [10 empty] | AGM 6 | 2188.33 | AGM 7 | 562.72 | 41.36 | 42.51 | 41.12 | 41.36 | 42.51 | 7510 | 43.38 | 42.61 | 33.7233 | -118.0066 | 15.385
GWD 7520 | Girth Weld |  | 21882.02 | 43.38 | 0.28 | 42000 | ERW | 8.625 | 728 | [10 empty] | AGM 6 | 2230.84 | AGM 7 | 520.21 | 42.51 | 43.38 | 41.36 | 42.51 | 43.38 | 7520 | 42.61 | 38.57 | 33.7235 | -118.0066 | 15.344
GWD 7530 | Girth Weld |  | 21925.4 | 42.61 | 0.28 | 42000 | ERW | 8.625 | 728 | [10 empty] | AGM 6 | 2274.22 | AGM 7 | 476.83 | 43.38 | 42.61 | 42.51 | 43.38 | 42.61 | 7530 | 38.57 | 42.53 | 33.7236 | -118.0066 | 15.632
GWD 7540 | Girth Weld |  | 21968 | 38.57 | 0.28 | 42000 | ERW | 8.625 | 728 | [10 empty] | AGM 6 | 2316.83 | AGM 7 | 434.22 | 42.61 | 38.57 | 43.38 | 42.61 | 38.57 | 7540 | 42.53 | 41.7 | 33.7237 | -118.0066 | 16.087
GWD 7550 | Girth Weld |  | 22006.58 | 42.53 | 0.28 | 42000 | ERW | 8.625 | 728 | [10 empty] | AGM 6 | 2355.4 | AGM 7 | 395.65 | 38.57 | 42.53 | 42.61 | 38.57 | 42.53 | 7550 | 41.7 | 41.24 | 33.7238 | -118.0066 | 16.492
GWD 7560 | Girth Weld |  | 22049.11 | 41.7 | 0.28 | 42000 | ERW | 8.625 | 728 | [10 empty] | AGM 6 | 2397.93 | AGM 7 | 353.12 | 42.53 | 41.7 | 38.57 | 42.53 | 41.7 | 7560 | 41.24 | 41.78 | 33.7239 | -118.0066 | 16.761
GWD 7570 | Girth Weld |  | 22090.81 | 41.24 | 0.28 | 42000 | ERW | 8.625 | 728 | [10 empty] | AGM 6 | 2439.64 | AGM 7 | 311.41 | 41.7 | 41.24 | 42.53 | 41.7 | 41.24 | 7570 | 41.78 | 42.94 | 33.724 | -118.0066 | 16.695
GWD 7580 | Girth Weld |  | 22132.05 | 41.78 | 0.28 | 42000 | ERW | 8.625 | 728 | [10 empty] | AGM 6 | 2480.88 | AGM 7 | 270.17 | 41.24 | 41.78 | 41.7 | 41.24 | 41.78 | 7580 | 42.94 | 40.36 | 33.7241 | -118.0066 | 17.052
GWD 7590 | Girth Weld |  | 22173.83 | 42.94 | 0.28 | 42000 | ERW | 8.625 | 728 | [10 empty] | AGM 6 | 2522.65 | AGM 7 | 228.4 | 41.78 | 42.94 | 41.24 | 41.78 | 42.94 | 7590 | 40.36 | 39.94 | 33.7243 | -118.0066 | 17.424
GWD 7600 | Girth Weld |  | 22216.77 | 40.36 | 0.28 | 42000 | ERW | 8.625 | 728 | [10 empty] | AGM 6 | 2565.59 | AGM 7 | 185.46 | 42.94 | 40.36 | 41.78 | 42.94 | 40.36 | 7600 | 39.94 | 42.97 | 33.7244 | -118.0066 | 17.364
GWD 7610 | Girth Weld |  | 22257.13 | 39.94 | 0.28 | 42000 | ERW | 8.625 | 728 | [10 empty] | AGM 6 | 2605.96 | AGM 7 | 145.09 | 40.36 | 39.94 | 42.94 | 40.36 | 39.94 | 7610 | 42.97 | 42.45 | 33.7245 | -118.0066 | 17.418
GWD 7620 | Girth Weld |  | 22297.07 | 42.97 | 0.28 | 42000 | ERW | 8.625 | 728 | [10 empty] | AGM 6 | 2645.89 | AGM 7 | 105.16 | 39.94 | 42.97 | 40.36 | 39.94 | 42.97 | 7620 | 42.45 | 42.17 | 33.7246 | -118.0066 | 17.798
GWD 7630 | Girth Weld |  | 22340.04 | 42.45 | 0.28 | 42000 | ERW | 8.625 | 728 | [10 empty] | AGM 6 | 2688.86 | AGM 7 | 62.19 | 42.97 | 42.45 | 39.94 | 42.97 | 42.45 | 7630 | 42.17 | 42.31 | 33.7247 | -118.0066 | 18.273
GWD 7640 | Girth Weld |  | 22382.49 | 19.74 | 0.28 | 42000 | ERW | 8.625 | 728 | [10 empty] | AGM 6 | 2731.31 | AGM 7 | 19.74 | 42.45 | 42.17 | 42.97 | 42.45 | 42.17 | 7640 | 42.31 | 42.54 | 33.7248 | -118.0066 | 17.995
MRK 5 | Marker |  | 22402.22 | 22.43 | 0.28 | 42000 | ERW | 8.625 | 728 |  |  |  |  | 11:28 | [5 empty] | AGM 6 | 2751.05 | AGM 8 | 2728.48 | 19.74 | 22.43 | 42.97 | 42.45 | 42.17 | 7640 | 42.31 | 42.54 | 33.7249 | -118.0066 | 17.622 | AGM 7 9' West of Curb - Located in Goldenwest St
GWD 7650 | Girth Weld |  | 22424.66 | 42.31 | 0.28 | 42000 | ERW | 8.625 | 728 | [10 empty] | AGM 7 | 22.43 | AGM 8 | 2706.05 | 42.17 | 42.31 | 42.45 | 42.17 | 42.31 | 7650 | 42.54 | 40.65 | 33.725 | -118.0066 | 17.758
GWD 7660 | Girth Weld |  | 22466.97 | 42.54 | 0.28 | 42000 | ERW | 8.625 | 728 | [10 empty] | AGM 7 | 64.74 | AGM 8 | 2663.73 | 42.31 | 42.54 | 42.17 | 42.31 | 42.54 | 7660 | 40.65 | 41.2 | 33.7251 | -118.0066 | 18.289
GWD 7670 | Girth Weld |  | 22509.51 | 40.65 | 0.28 | 42000 | ERW | 8.625 | 728 | [10 empty] | AGM 7 | 107.28 | AGM 8 | 2621.19 | 42.54 | 40.65 | 42.31 | 42.54 | 40.65 | 7670 | 41.2 | 41.82 | 33.7252 | -118.0066 | 18.541
GWD 7680 | Girth Weld |  | 22550.16 | 41.2 | 0.28 | 42000 | ERW | 8.625 | 728 | [10 empty] | AGM 7 | 147.94 | AGM 8 | 2580.54 | 40.65 | 41.2 | 42.54 | 40.65 | 41.2 | 7680 | 41.82 | 40.03 | 33.7253 | -118.0066 | 18.575
GWD 7690 | Girth Weld |  | 22591.36 | 41.82 | 0.28 | 42000 | ERW | 8.625 | 728 | [10 empty] | AGM 7 | 189.14 | AGM 8 | 2539.34 | 41.2 | 41.82 | 40.65 | 41.2 | 41.82 | 7690 | 40.03 | 40.03 | 33.7254 | -118.0066 | 18.72
GWD 7700 | Girth Weld |  | 22633.19 | 40.03 | 0.28 | 42000 | ERW | 8.625 | 728 | [10 empty] | AGM 7 | 230.96 | AGM 8 | 2497.51 | 41.82 | 40.03 | 41.2 | 41.82 | 40.03 | 7700 | 40.03 | 42.42 | 33.7255 | -118.0066 | 18.638
GWD 7710 | Girth Weld |  | 22673.22 | 40.03 | 0.28 | 42000 | ERW | 8.625 | 728 | [10 empty] | AGM 7 | 270.99 | AGM 8 | 2457.49 | 40.03 | 40.03 | 41.82 | 40.03 | 40.03 | 7710 | 42.42 | 40.33 | 33.7256 | -118.0066 | 18.907
GWD 7720 | Girth Weld |  | 22713.25 | 42.42 | 0.28 | 42000 | ERW | 8.625 | 728 | [10 empty] | AGM 7 | 311.02 | AGM 8 | 2417.45 | 40.03 | 42.42 | 40.03 | 40.03 | 42.42 | 7720 | 40.33 | 43.15 | 33.7257 | -118.0066 | 19.156
GWD 7730 | Girth Weld |  | 22755.67 | 40.33 | 0.28 | 42000 | ERW | 8.625 | 728 | [10 empty] | AGM 7 | 353.45 | AGM 8 | 2375.03 | 42.42 | 40.33 | 40.03 | 42.42 | 40.33 | 7730 | 43.15 | 42.75 | 33.7259 | -118.0066 | 19.162
GWD 7740 | Girth Weld |  | 22796 | 43.15 | 0.28 | 42000 | ERW | 8.625 | 728 | [10 empty] | AGM 7 | 393.78 | AGM 8 | 2334.7 | 40.33 | 43.15 | 42.42 | 40.33 | 43.15 | 7740 | 42.75 | 43.11 | 33.726 | -118.0066 | 19.142
GWD 7750 | Girth Weld |  | 22839.15 | 42.75 | 0.28 | 42000 | ERW | 8.625 | 728 | [10 empty] | AGM 7 | 436.92 | AGM 8 | 2291.55 | 43.15 | 42.75 | 40.33 | 43.15 | 42.75 | 7750 | 43.11 | 42.11 | 33.7261 | -118.0066 | 19.689
GWD 7760 | Girth Weld |  | 22881.9 | 43.11 | 0.28 | 42000 | ERW | 8.625 | 728 | [10 empty] | AGM 7 | 479.68 | AGM 8 | 2248.8 | 42.75 | 43.11 | 43.15 | 42.75 | 43.11 | 7760 | 42.11 | 43.17 | 33.7262 | -118.0066 | 19.318
GWD 7770 | Girth Weld |  | 22925.01 | 42.11 | 0.28 | 42000 | ERW | 8.625 | 728 | [10 empty] | AGM 7 | 522.79 | AGM 8 | 2205.69 | 43.11 | 42.11 | 42.75 | 43.11 | 42.11 | 7770 | 43.17 | 42.46 | 33.7263 | -118.0066 | 19.601
GWD 7780 | Girth Weld |  | 22967.12 | 43.17 | 0.28 | 42000 | ERW | 8.625 | 728 | [10 empty] | AGM 7 | 564.9 | AGM 8 | 2163.58 | 42.11 | 43.17 | 43.11 | 42.11 | 43.17 | 7780 | 42.46 | 38.35 | 33.7264 | -118.0066 | 19.851
GWD 7790 | Girth Weld |  | 23010.29 | 42.46 | 0.28 | 42000 | ERW | 8.625 | 728 | [10 empty] | AGM 7 | 608.06 | AGM 8 | 2120.42 | 43.17 | 42.46 | 42.11 | 43.17 | 42.46 | 7790 | 38.35 | 41.99 | 33.7266 | -118.0066 | 20.288
GWD 7800 | Girth Weld |  | 23052.75 | 38.35 | 0.28 | 42000 | ERW | 8.625 | 728 | [10 empty] | AGM 7 | 650.52 | AGM 8 | 2077.96 | 42.46 | 38.35 | 43.17 | 42.46 | 38.35 | 7800 | 41.99 | 42.54 | 33.7267 | -118.0066 | 20.452
GWD 7810 | Girth Weld |  | 23091.1 | 41.99 | 0.28 | 42000 | ERW | 8.625 | 728 | [10 empty] | AGM 7 | 688.87 | AGM 8 | 2039.61 | 38.35 | 41.99 | 42.46 | 38.35 | 41.99 | 7810 | 42.54 | 41.8 | 33.7268 | -118.0066 | 20.795
GWD 7820 | Girth Weld |  | 23133.08 | 42.54 | 0.28 | 42000 | ERW | 8.625 | 728 | [10 empty] | AGM 7 | 730.86 | AGM 8 | 1997.62 | 41.99 | 42.54 | 38.35 | 41.99 | 42.54 | 7820 | 41.8 | 42.05 | 33.7269 | -118.0066 | 21
GWD 7830 | Girth Weld |  | 23175.62 | 41.8 | 0.28 | 42000 | ERW | 8.625 | 728 | [10 empty] | AGM 7 | 773.4 | AGM 8 | 1955.08 | 42.54 | 41.8 | 41.99 | 42.54 | 41.8 | 7830 | 42.05 | 40.44 | 33.727 | -118.0066 | 20.902
GWD 7840 | Girth Weld |  | 23217.42 | 42.05 | 0.28 | 42000 | ERW | 8.625 | 728 | [10 empty] | AGM 7 | 815.2 | AGM 8 | 1913.28 | 41.8 | 42.05 | 42.54 | 41.8 | 42.05 | 7840 | 40.44 | 41.74 | 33.7271 | -118.0066 | 20.665
GWD 7850 | Girth Weld |  | 23259.48 | 40.44 | 0.28 | 42000 | ERW | 8.625 | 728 | [10 empty] | AGM 7 | 857.25 | AGM 8 | 1871.23 | 42.05 | 40.44 | 41.8 | 42.05 | 40.44 | 7850 | 41.74 | 42.01 | 33.7272 | -118.0066 | 21.199
GWD 7860 | Girth Weld |  | 23299.92 | 41.74 | 0.28 | 42000 | ERW | 8.625 | 728 | [10 empty] | AGM 7 | 897.7 | AGM 8 | 1830.78 | 40.44 | 41.74 | 42.05 | 40.44 | 41.74 | 7860 | 42.01 | 41.72 | 33.7274 | -118.0066 | 21.876
GWD 7870 | Girth Weld |  | 23341.66 | 42.01 | 0.28 | 42000 | ERW | 8.625 | 728 | [10 empty] | AGM 7 | 939.43 | AGM 8 | 1789.05 | 41.74 | 42.01 | 40.44 | 41.74 | 42.01 | 7870 | 41.72 | 42.76 | 33.7275 | -118.0066 | 21.995
GWD 7880 | Girth Weld |  | 23383.66 | 41.72 | 0.28 | 42000 | ERW | 8.625 | 728 | [10 empty] | AGM 7 | 981.44 | AGM 8 | 1747.04 | 42.01 | 41.72 | 41.74 | 42.01 | 41.72 | 7880 | 42.76 | 41.67 | 33.7276 | -118.0066 | 22.033
GWD 7890 | Girth Weld |  | 23425.38 | 42.76 | 0.28 | 42000 | ERW | 8.625 | 728 | [10 empty] | AGM 7 | 1023.16 | AGM 8 | 1705.32 | 41.72 | 42.76 | 42.01 | 41.72 | 42.76 | 7890 | 41.67 | 42.35 | 33.7277 | -118.0066 | 20.891
GWD 7900 | Girth Weld |  | 23468.15 | 41.67 | 0.28 | 42000 | ERW | 8.625 | 728 | [10 empty] | AGM 7 | 1065.92 | AGM 8 | 1662.56 | 42.76 | 41.67 | 41.72 | 42.76 | 41.67 | 7900 | 42.35 | 41.41 | 33.7278 | -118.0066 | 21.39
GWD 7910 | Girth Weld |  | 23509.82 | 42.35 | 0.28 | 42000 | ERW | 8.625 | 728 | [10 empty] | AGM 7 | 1107.59 | AGM 8 | 1620.88 | 41.67 | 42.35 | 42.76 | 41.67 | 42.35 | 7910 | 41.41 | 41.19 | 33.7279 | -118.0066 | 21.953
GWD 7920 | Girth Weld |  | 23552.17 | 41.41 | 0.28 | 42000 | ERW | 8.625 | 728 | [10 empty] | AGM 7 | 1149.95 | AGM 8 | 1578.53 | 42.35 | 41.41 | 41.67 | 42.35 | 41.41 | 7920 | 41.19 | 41.32 | 33.7281 | -118.0066 | 21.592
GWD 7930 | Girth Weld |  | 23593.58 | 41.19 | 0.28 | 42000 | ERW | 8.625 | 728 | [10 empty] | AGM 7 | 1191.36 | AGM 8 | 1537.12 | 41.41 | 41.19 | 42.35 | 41.41 | 41.19 | 7930 | 41.32 | 42 | 33.7282 | -118.0066 | 22.033
GWD 7940 | Girth Weld |  | 23634.77 | 41.32 | 0.28 | 42000 | ERW | 8.625 | 728 | [10 empty] | AGM 7 | 1232.54 | AGM 8 | 1495.93 | 41.19 | 41.32 | 41.41 | 41.19 | 41.32 | 7940 | 42 | 40.96 | 33.7283 | -118.0066 | 22.371
GWD 7950 | Girth Weld |  | 23676.09 | 42 | 0.28 | 42000 | ERW | 8.625 | 728 | [10 empty] | AGM 7 | 1273.87 | AGM 8 | 1454.61 | 41.32 | 42 | 41.19 | 41.32 | 42 | 7950 | 40.96 | 40.93 | 33.7284 | -118.0066 | 22.556
GWD 7960 | Girth Weld |  | 23718.09 | 40.96 | 0.28 | 42000 | ERW | 8.625 | 728 | [10 empty] | AGM 7 | 1315.86 | AGM 8 | 1412.61 | 42 | 40.96 | 41.32 | 42 | 40.96 | 7960 | 40.93 | 42.02 | 33.7285 | -118.0066 | 23.075
GWD 7970 | Girth Weld |  | 23759.05 | 40.93 | 0.28 | 42000 | ERW | 8.625 | 728 | [10 empty] | AGM 7 | 1356.82 | AGM 8 | 1371.66 | 40.96 | 40.93 | 42 | 40.96 | 40.93 | 7970 | 42.02 | 40.29 | 33.7286 | -118.0066 | 22.815
GWD 7980 | Girth Weld |  | 23799.98 | 42.02 | 0.28 | 42000 | ERW | 8.625 | 728 | [10 empty] | AGM 7 | 1397.75 | AGM 8 | 1330.73 | 40.93 | 42.02 | 40.96 | 40.93 | 42.02 | 7980 | 40.29 | 42.07 | 33.7287 | -118.0066 | 23.024
GWD 7990 | Girth Weld |  | 23841.99 | 40.29 | 0.28 | 42000 | ERW | 8.625 | 728 | [10 empty] | AGM 7 | 1439.77 | AGM 8 | 1288.71 | 42.02 | 40.29 | 40.93 | 42.02 | 40.29 | 7990 | 42.07 | 41.05 | 33.7289 | -118.0066 | 22.966
GWD 8000 | Girth Weld |  | 23882.29 | 42.07 | 0.28 | 42000 | ERW | 8.625 | 728 | [10 empty] | AGM 7 | 1480.06 | AGM 8 | 1248.41 | 40.29 | 42.07 | 42.02 | 40.29 | 42.07 | 8000 | 41.05 | 42.12 | 33.729 | -118.0066 | 23.326
GWD 8010 | Girth Weld |  | 23924.35 | 41.05 | 0.28 | 42000 | ERW | 8.625 | 728 | [10 empty] | AGM 7 | 1522.13 | AGM 8 | 1206.35 | 42.07 | 41.05 | 40.29 | 42.07 | 41.05 | 8010 | 42.12 | 8.02 | 33.7291 | -118.0066 | 23.273
GWD 8020 | Girth Weld |  | 23965.4 | 42.12 | 0.28 | 42000 | ERW | 8.625 | 728 | [10 empty] | AGM 7 | 1563.18 | AGM 8 | 1165.3 | 41.05 | 42.12 | 42.07 | 41.05 | 42.12 | 8020 | 8.02 | 42.37 | 33.7292 | -118.0066 | 23.192
GWD 8030 | Girth Weld |  | 24007.52 | 8.02 | 0.28 | 42000 | ERW | 8.625 | 728 | [10 empty] | AGM 7 | 1605.29 | AGM 8 | 1123.18 | 42.12 | 8.02 | 41.05 | 42.12 | 8.02 | 8030 | 42.37 | 41.03 | 33.7293 | -118.0066 | 23.391
GWD 8040 | Girth Weld |  | 24015.54 | 42.37 | 0.28 | 42000 | ERW | 8.625 | 728 | [10 empty] | AGM 7 | 1613.31 | AGM 8 | 1115.16 | 8.02 | 42.37 | 42.12 | 8.02 | 42.37 | 8040 | 41.03 | 41.17 | 33.7293 | -118.0066 | 23.552
GWD 8050 | Girth Weld |  | 24057.91 | 41.03 | 0.28 | 42000 | ERW | 8.625 | 728 | [10 empty] | AGM 7 | 1655.68 | AGM 8 | 1072.79 | 42.37 | 41.03 | 8.02 | 42.37 | 41.03 | 8050 | 41.17 | 41.43 | 33.7294 | -118.0066 | 23.16
GWD 8060 | Girth Weld |  | 24098.94 | 41.17 | 0.28 | 42000 | ERW | 8.625 | 728 | [10 empty] | AGM 7 | 1696.71 | AGM 8 | 1031.77 | 41.03 | 41.17 | 42.37 | 41.03 | 41.17 | 8060 | 41.43 | 40.65 | 33.7296 | -118.0067 | 22.776
GWD 8070 | Girth Weld |  | 24140.11 | 41.43 | 0.28 | 42000 | ERW | 8.625 | 728 | [10 empty] | AGM 7 | 1737.88 | AGM 8 | 990.59 | 41.17 | 41.43 | 41.03 | 41.17 | 41.43 | 8070 | 40.65 | 42.73 | 33.7297 | -118.0067 | 22.898
GWD 8080 | Girth Weld |  | 24181.53 | 40.65 | 0.28 | 42000 | ERW | 8.625 | 728 | [10 empty] | AGM 7 | 1779.31 | AGM 8 | 949.17 | 41.43 | 40.65 | 41.17 | 41.43 | 40.65 | 8080 | 42.73 | 41.87 | 33.7298 | -118.0067 | 22.755
GWD 8090 | Girth Weld |  | 24222.19 | 42.73 | 0.28 | 42000 | ERW | 8.625 | 728 | [10 empty] | AGM 7 | 1819.96 | AGM 8 | 908.51 | 40.65 | 42.73 | 41.43 | 40.65 | 42.73 | 8090 | 41.87 | 47.19 | 33.7299 | -118.0067 | 22.19
GWD 8100 | Girth Weld |  | 24264.92 | 41.87 | 0.28 | 42000 | ERW | 8.625 | 728 | [10 empty] | AGM 7 | 1862.7 | AGM 8 | 865.78 | 42.73 | 41.87 | 40.65 | 42.73 | 41.87 | 8100 | 47.19 | 41.28 | 33.73 | -118.0067 | 21.795
GWD 8110 | Girth Weld |  | 24306.79 | 47.19 | 0.28 | 42000 | ERW | 8.625 | 728 | [10 empty] | AGM 7 | 1904.57 | AGM 8 | 823.91 | 41.87 | 47.19 | 42.73 | 41.87 | 47.19 | 8110 | 41.28 | 40.25 | 33.7301 | -118.0067 | 22.125
GWD 8120 | Girth Weld |  | 24353.98 | 41.28 | 0.28 | 42000 | ERW | 8.625 | 728 | [10 empty] | AGM 7 | 1951.76 | AGM 8 | 776.72 | 47.19 | 41.28 | 41.87 | 47.19 | 41.28 | 8120 | 40.25 | 41.09 | 33.7303 | -118.0067 | 23.172
GWD 8130 | Girth Weld |  | 24395.26 | 40.25 | 0.28 | 42000 | ERW | 8.625 | 728 | [10 empty] | AGM 7 | 1993.04 | AGM 8 | 735.44 | 41.28 | 40.25 | 47.19 | 41.28 | 40.25 | 8130 | 41.09 | 40.57 | 33.7304 | -118.0067 | 24.102
GWD 8140 | Girth Weld |  | 24435.51 | 41.09 | 0.28 | 42000 | ERW | 8.625 | 728 | [10 empty] | AGM 7 | 2033.29 | AGM 8 | 695.19 | 40.25 | 41.09 | 41.28 | 40.25 | 41.09 | 8140 | 40.57 | 39.48 | 33.7305 | -118.0067 | 24.141
GWD 8150 | Girth Weld |  | 24476.6 | 40.57 | 0.28 | 42000 | ERW | 8.625 | 728 | [10 empty] | AGM 7 | 2074.38 | AGM 8 | 654.1 | 41.09 | 40.57 | 40.25 | 41.09 | 40.57 | 8150 | 39.48 | 41.11 | 33.7306 | -118.0067 | 24.097
GWD 8160 | Girth Weld |  | 24517.18 | 39.48 | 0.28 | 42000 | ERW | 8.625 | 728 | [10 empty] | AGM 7 | 2114.95 | AGM 8 | 613.52 | 40.57 | 39.48 | 41.09 | 40.57 | 39.48 | 8160 | 41.11 | 42.08 | 33.7307 | -118.0067 | 24.242
GWD 8170 | Girth Weld |  | 24556.65 | 41.11 | 0.28 | 42000 | ERW | 8.625 | 728 | [10 empty] | AGM 7 | 2154.43 | AGM 8 | 574.05 | 39.48 | 41.11 | 40.57 | 39.48 | 41.11 | 8170 | 42.08 | 39.69 | 33.7308 | -118.0067 | 23.981
GWD 8180 | Girth Weld |  | 24597.76 | 42.08 | 0.28 | 42000 | ERW | 8.625 | 728 | [10 empty] | AGM 7 | 2195.54 | AGM 8 | 532.94 | 41.11 | 42.08 | 39.48 | 41.11 | 42.08 | 8180 | 39.69 | 41.14 | 33.7309 | -118.0067 | 24.147
GWD 8190 | Girth Weld |  | 24639.84 | 39.69 | 0.28 | 42000 | ERW | 8.625 | 728 | [10 empty] | AGM 7 | 2237.62 | AGM 8 | 490.86 | 42.08 | 39.69 | 41.11 | 42.08 | 39.69 | 8190 | 41.14 | 42.64 | 33.731 | -118.0067 | 24.272
GWD 8200 | Girth Weld |  | 24679.54 | 41.14 | 0.28 | 42000 | ERW | 8.625 | 728 | [10 empty] | AGM 7 | 2277.31 | AGM 8 | 451.16 | 39.69 | 41.14 | 42.08 | 39.69 | 41.14 | 8200 | 42.64 | 41.11 | 33.7312 | -118.0067 | 24.3
GWD 8210 | Girth Weld |  | 24720.68 | 42.64 | 0.28 | 42000 | ERW | 8.625 | 728 | [10 empty] | AGM 7 | 2318.45 | AGM 8 | 410.02 | 41.14 | 42.64 | 39.69 | 41.14 | 42.64 | 8210 | 41.11 | 42.81 | 33.7313 | -118.0067 | 24.274
GWD 8220 | Girth Weld |  | 24763.32 | 41.11 | 0.28 | 42000 | ERW | 8.625 | 728 | [10 empty] | AGM 7 | 2361.09 | AGM 8 | 367.38 | 42.64 | 41.11 | 41.14 | 42.64 | 41.11 | 8220 | 42.81 | 39.77 | 33.7314 | -118.0067 | 24.254
GWD 8230 | Girth Weld |  | 24804.43 | 42.81 | 0.28 | 42000 | ERW | 8.625 | 728 | [10 empty] | AGM 7 | 2402.2 | AGM 8 | 326.28 | 41.11 | 42.81 | 42.64 | 41.11 | 42.81 | 8230 | 39.77 | 41.06 | 33.7315 | -118.0067 | 24.41
GWD 8240 | Girth Weld |  | 24847.23 | 39.77 | 0.28 | 42000 | ERW | 8.625 | 728 | [10 empty] | AGM 7 | 2445.01 | AGM 8 | 283.47 | 42.81 | 39.77 | 41.11 | 42.81 | 39.77 | 8240 | 41.06 | 41.56 | 33.7316 | -118.0067 | 24.815
GWD 8250 | Girth Weld |  | 24887.01 | 41.06 | 0.28 | 42000 | ERW | 8.625 | 728 | [10 empty] | AGM 7 | 2484.78 | AGM 8 | 243.7 | 39.77 | 41.06 | 42.81 | 39.77 | 41.06 | 8250 | 41.56 | 41.72 | 33.7317 | -118.0067 | 24.831
GWD 8260 | Girth Weld |  | 24928.07 | 41.56 | 0.28 | 42000 | ERW | 8.625 | 728 | [10 empty] | AGM 7 | 2525.84 | AGM 8 | 202.63 | 41.06 | 41.56 | 39.77 | 41.06 | 41.56 | 8260 | 41.72 | 42.75 | 33.7318 | -118.0067 | 24.946
GWD 8270 | Girth Weld |  | 24969.63 | 41.72 | 0.28 | 42000 | ERW | 8.625 | 728 | [10 empty] | AGM 7 | 2567.41 | AGM 8 | 161.07 | 41.56 | 41.72 | 41.06 | 41.56 | 41.72 | 8270 | 42.75 | 41.36 | 33.732 | -118.0067 | 24.909
GWD 8280 | Girth Weld |  | 25011.35 | 42.75 | 0.28 | 42000 | ERW | 8.625 | 728 | [10 empty] | AGM 7 | 2609.13 | AGM 8 | 119.35 | 41.72 | 42.75 | 41.56 | 41.72 | 42.75 | 8280 | 41.36 | 41.69 | 33.7321 | -118.0067 | 25.3
GWD 8290 | Girth Weld |  | 25054.1 | 41.36 | 0.28 | 42000 | ERW | 8.625 | 728 | [10 empty] | AGM 7 | 2651.88 | AGM 8 | 76.6 | 42.75 | 41.36 | 41.72 | 42.75 | 41.36 | 8290 | 41.69 | 41.44 | 33.7322 | -118.0067 | 25.357
GWD 8300 | Girth Weld |  | 25095.47 | 35.24 | 0.28 | 42000 | ERW | 8.625 | 728 | [10 empty] | AGM 7 | 2693.24 | AGM 8 | 35.24 | 41.36 | 41.69 | 42.75 | 41.36 | 41.69 | 8300 | 41.44 | 41.25 | 33.7323 | -118.0067 | 25.766
MRK 6 | Marker |  | 25130.7 | 6.45 | 0.28 | 42000 | ERW | 8.625 | 728 |  |  |  |  | 11:32 | [5 empty] | AGM 7 | 2728.48 | AGM 9 | 2665.42 | 35.24 | 6.45 | 42.75 | 41.36 | 41.69 | 8300 | 41.44 | 41.25 | 33.7324 | -118.0067 | 25.639 | AGM 8 8' West of Curb - Located in Goldenwest St
GWD 8310 | Girth Weld |  | 25137.15 | 41.44 | 0.28 | 42000 | ERW | 8.625 | 728 | [10 empty] | AGM 8 | 6.45 | AGM 9 | 2658.97 | 41.69 | 41.44 | 41.36 | 41.69 | 41.44 | 8310 | 41.25 | 40.43 | 33.7324 | -118.0067 | 25.599
GWD 8320 | Girth Weld |  | 25178.59 | 41.25 | 0.28 | 42000 | ERW | 8.625 | 728 | [10 empty] | AGM 8 | 47.89 | AGM 9 | 2617.53 | 41.44 | 41.25 | 41.69 | 41.44 | 41.25 | 8320 | 40.43 | 40.89 | 33.7325 | -118.0067 | 25.556
GWD 8330 | Girth Weld |  | 25219.85 | 40.43 | 0.28 | 42000 | ERW | 8.625 | 728 | [10 empty] | AGM 8 | 89.14 | AGM 9 | 2576.28 | 41.25 | 40.43 | 41.44 | 41.25 | 40.43 | 8330 | 40.89 | 40.51 | 33.7326 | -118.0067 | 25.825
GWD 8340 | Girth Weld |  | 25260.28 | 40.89 | 0.28 | 42000 | ERW | 8.625 | 728 | [10 empty] | AGM 8 | 129.58 | AGM 9 | 2535.84 | 40.43 | 40.89 | 41.25 | 40.43 | 40.89 | 8340 | 40.51 | 40.26 | 33.7327 | -118.0067 | 26.098
GWD 8350 | Girth Weld |  | 25301.17 | 40.51 | 0.28 | 42000 | ERW | 8.625 | 728 | [10 empty] | AGM 8 | 170.47 | AGM 9 | 2494.95 | 40.89 | 40.51 | 40.43 | 40.89 | 40.51 | 8350 | 40.26 | 40.11 | 33.7329 | -118.0067 | 25.881
GWD 8360 | Girth Weld |  | 25341.68 | 40.26 | 0.28 | 42000 | ERW | 8.625 | 728 | [10 empty] | AGM 8 | 210.98 | AGM 9 | 2454.44 | 40.51 | 40.26 | 40.89 | 40.51 | 40.26 | 8360 | 40.11 | 42.77 | 33.733 | -118.0067 | 25.995
GWD 8370 | Girth Weld |  | 25381.94 | 40.11 | 0.28 | 42000 | ERW | 8.625 | 728 | [10 empty] | AGM 8 | 251.24 | AGM 9 | 2414.18 | 40.26 | 40.11 | 40.51 | 40.26 | 40.11 | 8370 | 42.77 | 42.97 | 33.7331 | -118.0067 | 26.116
GWD 8380 | Girth Weld |  | 25422.05 | 42.77 | 0.28 | 42000 | ERW | 8.625 | 728 | [10 empty] | AGM 8 | 291.35 | AGM 9 | 2374.07 | 40.11 | 42.77 | 40.26 | 40.11 | 42.77 | 8380 | 42.97 | 42.59 | 33.7332 | -118.0067 | 26.11
GWD 8390 | Girth Weld |  | 25464.82 | 42.97 | 0.28 | 42000 | ERW | 8.625 | 728 | [10 empty] | AGM 8 | 334.12 | AGM 9 | 2331.3 | 42.77 | 42.97 | 40.11 | 42.77 | 42.97 | 8390 | 42.59 | 42.79 | 33.7333 | -118.0067 | 25.914
GWD 8400 | Girth Weld |  | 25507.79 | 42.59 | 0.28 | 42000 | ERW | 8.625 | 728 | [10 empty] | AGM 8 | 377.08 | AGM 9 | 2288.34 | 42.97 | 42.59 | 42.77 | 42.97 | 42.59 | 8400 | 42.79 | 42.01 | 33.7334 | -118.0067 | 26.157
GWD 8410 | Girth Weld |  | 25550.37 | 42.79 | 0.28 | 42000 | ERW | 8.625 | 728 | [10 empty] | AGM 8 | 419.67 | AGM 9 | 2245.75 | 42.59 | 42.79 | 42.97 | 42.59 | 42.79 | 8410 | 42.01 | 47.85 | 33.7335 | -118.0067 | 26.253
GWD 8420 | Girth Weld |  | 25593.17 | 42.01 | 0.28 | 42000 | ERW | 8.625 | 728 | [10 empty] | AGM 8 | 462.46 | AGM 9 | 2202.96 | 42.79 | 42.01 | 42.59 | 42.79 | 42.01 | 8420 | 47.85 | 47.4 | 33.7337 | -118.0067 | 26.628
GWD 8430 | Girth Weld |  | 25635.17 | 47.85 | 0.28 | 42000 | ERW | 8.625 | 728 | [10 empty] | AGM 8 | 504.47 | AGM 9 | 2160.95 | 42.01 | 47.85 | 42.79 | 42.01 | 47.85 | 8430 | 47.4 | 42.78 | 33.7338 | -118.0067 | 26.664
GWD 8440 | Girth Weld |  | 25683.02 | 47.4 | 0.28 | 42000 | ERW | 8.625 | 728 | [10 empty] | AGM 8 | 552.32 | AGM 9 | 2113.1 | 47.85 | 47.4 | 42.01 | 47.85 | 47.4 | 8440 | 42.78 | 46.53 | 33.7339 | -118.0067 | 26.753
GWD 8450 | Girth Weld |  | 25730.42 | 42.78 | 0.28 | 42000 | ERW | 8.625 | 728 | [10 empty] | AGM 8 | 599.72 | AGM 9 | 2065.7 | 47.4 | 42.78 | 47.85 | 47.4 | 42.78 | 8450 | 46.53 | 47.31 | 33.734 | -118.0067 | 26.641
GWD 8460 | Girth Weld |  | 25773.2 | 46.53 | 0.28 | 42000 | ERW | 8.625 | 728 | [10 empty] | AGM 8 | 642.5 | AGM 9 | 2022.92 | 42.78 | 46.53 | 47.4 | 42.78 | 46.53 | 8460 | 47.31 | 42.29 | 33.7342 | -118.0067 | 26.85
GWD 8470 | Girth Weld |  | 25819.73 | 47.31 | 0.28 | 42000 | ERW | 8.625 | 728 | [10 empty] | AGM 8 | 689.03 | AGM 9 | 1976.39 | 46.53 | 47.31 | 42.78 | 46.53 | 47.31 | 8470 | 42.29 | 45.33 | 33.7343 | -118.0067 | 26.586
GWD 8480 | Girth Weld |  | 25867.03 | 42.29 | 0.28 | 42000 | ERW | 8.625 | 728 | [10 empty] | AGM 8 | 736.33 | AGM 9 | 1929.09 | 47.31 | 42.29 | 46.53 | 47.31 | 42.29 | 8480 | 45.33 | 41.44 | 33.7344 | -118.0067 | 26.581
GWD 8490 | Girth Weld |  | 25909.33 | 45.33 | 0.28 | 42000 | ERW | 8.625 | 728 | [10 empty] | AGM 8 | 778.62 | AGM 9 | 1886.8 | 42.29 | 45.33 | 47.31 | 42.29 | 45.33 | 8490 | 41.44 | 47.69 | 33.7345 | -118.0067 | 26.478
GWD 8500 | Girth Weld |  | 25954.65 | 41.44 | 0.28 | 42000 | ERW | 8.625 | 728 | [10 empty] | AGM 8 | 823.95 | AGM 9 | 1841.47 | 45.33 | 41.44 | 42.29 | 45.33 | 41.44 | 8500 | 47.69 | 46.11 | 33.7347 | -118.0067 | 26.339
GWD 8510 | Girth Weld |  | 25996.09 | 47.69 | 0.28 | 42000 | ERW | 8.625 | 728 | [10 empty] | AGM 8 | 865.39 | AGM 9 | 1800.03 | 41.44 | 47.69 | 45.33 | 41.44 | 47.69 | 8510 | 46.11 | 40.24 | 33.7348 | -118.0067 | 26.304
GWD 8520 | Girth Weld |  | 26043.78 | 46.11 | 0.28 | 42000 | ERW | 8.625 | 728 | [10 empty] | AGM 8 | 913.08 | AGM 9 | 1752.34 | 47.69 | 46.11 | 41.44 | 47.69 | 46.11 | 8520 | 40.24 | 42.28 | 33.7349 | -118.0067 | 26.098
GWD 8530 | Girth Weld |  | 26089.89 | 40.24 | 0.28 | 42000 | ERW | 8.625 | 728 | [10 empty] | AGM 8 | 959.19 | AGM 9 | 1706.23 | 46.11 | 40.24 | 47.69 | 46.11 | 40.24 | 8530 | 42.28 | 42.04 | 33.735 | -118.0067 | 26.262
GWD 8540 | Girth Weld |  | 26130.14 | 42.28 | 0.28 | 42000 | ERW | 8.625 | 728 | [10 empty] | AGM 8 | 999.44 | AGM 9 | 1665.98 | 40.24 | 42.28 | 46.11 | 40.24 | 42.28 | 8540 | 42.04 | 46.29 | 33.7351 | -118.0067 | 26.298
GWD 8550 | Girth Weld |  | 26172.41 | 42.04 | 0.28 | 42000 | ERW | 8.625 | 728 | [10 empty] | AGM 8 | 1041.71 | AGM 9 | 1623.71 | 42.28 | 42.04 | 40.24 | 42.28 | 42.04 | 8550 | 46.29 | 47.69 | 33.7353 | -118.0067 | 26.313
GWD 8560 | Girth Weld |  | 26214.45 | 46.29 | 0.28 | 42000 | ERW | 8.625 | 728 | [10 empty] | AGM 8 | 1083.75 | AGM 9 | 1581.67 | 42.04 | 46.29 | 42.28 | 42.04 | 46.29 | 8560 | 47.69 | 48.11 | 33.7354 | -118.0067 | 26.084
GWD 8570 | Girth Weld |  | 26260.74 | 47.69 | 0.28 | 42000 | ERW | 8.625 | 728 | [10 empty] | AGM 8 | 1130.04 | AGM 9 | 1535.38 | 46.29 | 47.69 | 42.04 | 46.29 | 47.69 | 8570 | 48.11 | 37.08 | 33.7355 | -118.0067 | 26.196
GWD 8580 | Girth Weld |  | 26308.43 | 48.11 | 0.28 | 42000 | ERW | 8.625 | 728 | [10 empty] | AGM 8 | 1177.73 | AGM 9 | 1487.69 | 47.69 | 48.11 | 46.29 | 47.69 | 48.11 | 8580 | 37.08 | 41.91 | 33.7356 | -118.0067 | 26.141
GWD 8590 | Girth Weld |  | 26356.54 | 37.08 | 0.28 | 42000 | ERW | 8.625 | 728 | [10 empty] | AGM 8 | 1225.84 | AGM 9 | 1439.58 | 48.11 | 37.08 | 47.69 | 48.11 | 37.08 | 8590 | 41.91 | 41.69 | 33.7358 | -118.0067 | 25.645
GWD 8600 | Girth Weld |  | 26393.62 | 41.91 | 0.28 | 42000 | ERW | 8.625 | 728 | [10 empty] | AGM 8 | 1262.92 | AGM 9 | 1402.5 | 37.08 | 41.91 | 48.11 | 37.08 | 41.91 | 8600 | 41.69 | 47.64 | 33.7359 | -118.0067 | 25.839
GWD 8610 | Girth Weld |  | 26435.53 | 41.69 | 0.28 | 42000 | ERW | 8.625 | 728 | [10 empty] | AGM 8 | 1304.83 | AGM 9 | 1360.59 | 41.91 | 41.69 | 37.08 | 41.91 | 41.69 | 8610 | 47.64 | 41.61 | 33.736 | -118.0068 | 25.844
GWD 8620 | Girth Weld |  | 26477.23 | 47.64 | 0.28 | 42000 | ERW | 8.625 | 728 | [10 empty] | AGM 8 | 1346.52 | AGM 9 | 1318.9 | 41.69 | 47.64 | 41.91 | 41.69 | 47.64 | 8620 | 41.61 | 40.66 | 33.7361 | -118.0068 | 25.56
GWD 8630 | Girth Weld |  | 26524.87 | 41.61 | 0.28 | 42000 | ERW | 8.625 | 728 | [10 empty] | AGM 8 | 1394.16 | AGM 9 | 1271.26 | 47.64 | 41.61 | 41.69 | 47.64 | 41.61 | 8630 | 40.66 | 46.71 | 33.7362 | -118.0068 | 25.414
GWD 8640 | Girth Weld |  | 26566.48 | 40.66 | 0.28 | 42000 | ERW | 8.625 | 728 | [10 empty] | AGM 8 | 1435.77 | AGM 9 | 1229.65 | 41.61 | 40.66 | 47.64 | 41.61 | 40.66 | 8640 | 46.71 | 46.4 | 33.7363 | -118.0068 | 25.31
GWD 8650 | Girth Weld |  | 26607.13 | 46.71 | 0.28 | 42000 | ERW | 8.625 | 728 | [10 empty] | AGM 8 | 1476.43 | AGM 9 | 1188.99 | 40.66 | 46.71 | 41.61 | 40.66 | 46.71 | 8650 | 46.4 | 46.63 | 33.7364 | -118.0068 | 25.259
GWD 8660 | Girth Weld |  | 26653.84 | 46.4 | 0.28 | 42000 | ERW | 8.625 | 728 | [10 empty] | AGM 8 | 1523.14 | AGM 9 | 1142.28 | 46.71 | 46.4 | 40.66 | 46.71 | 46.4 | 8660 | 46.63 | 44.57 | 33.7366 | -118.0068 | 25.379
GWD 8670 | Girth Weld |  | 26700.24 | 46.63 | 0.28 | 42000 | ERW | 8.625 | 728 | [10 empty] | AGM 8 | 1569.54 | AGM 9 | 1095.88 | 46.4 | 46.63 | 46.71 | 46.4 | 46.63 | 8670 | 44.57 | 44.9 | 33.7367 | -118.0068 | 24.976
GWD 8680 | Girth Weld |  | 26746.88 | 44.57 | 0.28 | 42000 | ERW | 8.625 | 728 | [10 empty] | AGM 8 | 1616.17 | AGM 9 | 1049.25 | 46.63 | 44.57 | 46.4 | 46.63 | 44.57 | 8680 | 44.9 | 47.56 | 33.7368 | -118.0068 | 25.202
GWD 8690 | Girth Weld |  | 26791.45 | 44.9 | 0.28 | 42000 | ERW | 8.625 | 728 | [10 empty] | AGM 8 | 1660.75 | AGM 9 | 1004.67 | 44.57 | 44.9 | 46.63 | 44.57 | 44.9 | 8690 | 47.56 | 44.15 | 33.7369 | -118.0068 | 25.642
GWD 8700 | Girth Weld |  | 26836.35 | 47.56 | 0.28 | 42000 | ERW | 8.625 | 728 | [10 empty] | AGM 8 | 1705.65 | AGM 9 | 959.77 | 44.9 | 47.56 | 44.57 | 44.9 | 47.56 | 8700 | 44.15 | 42.09 | 33.7371 | -118.0068 | 25.811
GWD 8710 | Girth Weld |  | 26883.91 | 44.15 | 0.28 | 42000 | ERW | 8.625 | 728 | [10 empty] | AGM 8 | 1753.21 | AGM 9 | 912.21 | 47.56 | 44.15 | 44.9 | 47.56 | 44.15 | 8710 | 42.09 | 8.98 | 33.7372 | -118.0068 | 25.299
GWD 8720 | Girth Weld |  | 26928.06 | 42.09 | 0.28 | 42000 | ERW | 8.625 | 728 | [10 empty] | AGM 8 | 1797.35 | AGM 9 | 868.07 | 44.15 | 42.09 | 47.56 | 44.15 | 42.09 | 8720 | 8.98 | 40.41 | 33.7373 | -118.0068 | 25.266
GWD 8730 | Girth Weld |  | 26970.15 | 8.98 | 0.28 | 42000 | ERW | 8.625 | 728 | [10 empty] | AGM 8 | 1839.45 | AGM 9 | 825.97 | 42.09 | 8.98 | 44.15 | 42.09 | 8.98 | 8730 | 40.41 | 42.57 | 33.7374 | -118.0068 | 25.694
GWD 8740 | Girth Weld |  | 26979.13 | 40.41 | 0.28 | 42000 | ERW | 8.625 | 728 | [10 empty] | AGM 8 | 1848.43 | AGM 9 | 816.99 | 8.98 | 40.41 | 42.09 | 8.98 | 40.41 | 8740 | 42.57 | 41.15 | 33.7375 | -118.0068 | 25.889
GWD 8750 | Girth Weld |  | 27019.54 | 42.57 | 0.28 | 42000 | ERW | 8.625 | 728 | [10 empty] | AGM 8 | 1888.84 | AGM 9 | 776.58 | 40.41 | 42.57 | 8.98 | 40.41 | 42.57 | 8750 | 41.15 | 41.95 | 33.7376 | -118.0068 | 25.68
GWD 8760 | Girth Weld |  | 27062.11 | 41.15 | 0.28 | 42000 | ERW | 8.625 | 728 | [10 empty] | AGM 8 | 1931.4 | AGM 9 | 734.02 | 42.57 | 41.15 | 40.41 | 42.57 | 41.15 | 8760 | 41.95 | 38.52 | 33.7377 | -118.0068 | 25.791
GWD 8770 | Girth Weld |  | 27103.25 | 41.95 | 0.28 | 42000 | ERW | 8.625 | 728 | [10 empty] | AGM 8 | 1972.55 | AGM 9 | 692.87 | 41.15 | 41.95 | 42.57 | 41.15 | 41.95 | 8770 | 38.52 | 41.12 | 33.7378 | -118.0068 | 25.935
GWD 8780 | Girth Weld |  | 27145.2 | 38.52 | 0.28 | 42000 | ERW | 8.625 | 728 | [10 empty] | AGM 8 | 2014.5 | AGM 9 | 650.92 | 41.95 | 38.52 | 41.15 | 41.95 | 38.52 | 8780 | 41.12 | 42.81 | 33.7379 | -118.0068 | 26.226
GWD 8790 | Girth Weld |  | 27183.73 | 41.12 | 0.28 | 42000 | ERW | 8.625 | 728 | [10 empty] | AGM 8 | 2053.03 | AGM 9 | 612.39 | 38.52 | 41.12 | 41.95 | 38.52 | 41.12 | 8790 | 42.81 | 41.25 | 33.738 | -118.0068 | 25.928
GWD 8800 | Girth Weld |  | 27224.85 | 42.81 | 0.28 | 42000 | ERW | 8.625 | 728 | [10 empty] | AGM 8 | 2094.15 | AGM 9 | 571.27 | 41.12 | 42.81 | 38.52 | 41.12 | 42.81 | 8800 | 41.25 | 42.15 | 33.7381 | -118.0068 | 25.419
GWD 8810 | Girth Weld |  | 27267.67 | 41.25 | 0.28 | 42000 | ERW | 8.625 | 728 | [10 empty] | AGM 8 | 2136.96 | AGM 9 | 528.46 | 42.81 | 41.25 | 41.12 | 42.81 | 41.25 | 8810 | 42.15 | 40.61 | 33.7383 | -118.0068 | 25.933
GWD 8820 | Girth Weld |  | 27308.92 | 42.15 | 0.28 | 42000 | ERW | 8.625 | 728 | [10 empty] | AGM 8 | 2178.21 | AGM 9 | 487.21 | 41.25 | 42.15 | 42.81 | 41.25 | 42.15 | 8820 | 40.61 | 38.22 | 33.7384 | -118.0068 | 26.069
GWD 8830 | Girth Weld |  | 27351.07 | 40.61 | 0.28 | 42000 | ERW | 8.625 | 728 | [10 empty] | AGM 8 | 2220.36 | AGM 9 | 445.06 | 42.15 | 40.61 | 41.25 | 42.15 | 40.61 | 8830 | 38.22 | 42.34 | 33.7385 | -118.0068 | 26.036
GWD 8840 | Girth Weld |  | 27391.68 | 38.22 | 0.28 | 42000 | ERW | 8.625 | 728 | [10 empty] | AGM 8 | 2260.98 | AGM 9 | 404.44 | 40.61 | 38.22 | 42.15 | 40.61 | 38.22 | 8840 | 42.34 | 38.69 | 33.7386 | -118.0068 | 26.186
GWD 8850 | Girth Weld |  | 27429.9 | 42.34 | 0.28 | 42000 | ERW | 8.625 | 728 | [10 empty] | AGM 8 | 2299.2 | AGM 9 | 366.22 | 38.22 | 42.34 | 40.61 | 38.22 | 42.34 | 8850 | 38.69 | 42.71 | 33.7387 | -118.0068 | 26.734
GWD 8860 | Girth Weld |  | 27472.24 | 38.69 | 0.28 | 42000 | ERW | 8.625 | 728 | [10 empty] | AGM 8 | 2341.54 | AGM 9 | 323.88 | 42.34 | 38.69 | 38.22 | 42.34 | 38.69 | 8860 | 42.71 | 42.37 | 33.7388 | -118.0068 | 26.542
GWD 8870 | Girth Weld |  | 27510.93 | 42.71 | 0.28 | 42000 | ERW | 8.625 | 728 | [10 empty] | AGM 8 | 2380.23 | AGM 9 | 285.19 | 38.69 | 42.71 | 42.34 | 38.69 | 42.71 | 8870 | 42.37 | 37.04 | 33.7389 | -118.0068 | 26.766
GWD 8880 | Girth Weld |  | 27553.64 | 42.37 | 0.28 | 42000 | ERW | 8.625 | 728 | [10 empty] | AGM 8 | 2422.94 | AGM 9 | 242.48 | 42.71 | 42.37 | 38.69 | 42.71 | 42.37 | 8880 | 37.04 | 41.89 | 33.739 | -118.0068 | 27.099
GWD 8890 | Girth Weld |  | 27596.01 | 37.04 | 0.28 | 42000 | ERW | 8.625 | 728 | [10 empty] | AGM 8 | 2465.31 | AGM 9 | 200.11 | 42.37 | 37.04 | 42.71 | 42.37 | 37.04 | 8890 | 41.89 | 42.37 | 33.7392 | -118.0068 | 26.778
GWD 8900 | Girth Weld |  | 27633.05 | 41.89 | 0.28 | 42000 | ERW | 8.625 | 728 | [10 empty] | AGM 8 | 2502.35 | AGM 9 | 163.07 | 37.04 | 41.89 | 42.37 | 37.04 | 41.89 | 8900 | 42.37 | 41.06 | 33.7393 | -118.0068 | 27.086
GWD 8910 | Girth Weld |  | 27674.94 | 42.37 | 0.28 | 42000 | ERW | 8.625 | 728 | [10 empty] | AGM 8 | 2544.24 | AGM 9 | 121.18 | 41.89 | 42.37 | 37.04 | 41.89 | 42.37 | 8910 | 41.06 | 39.18 | 33.7394 | -118.0068 | 26.903
GWD 8920 | Girth Weld |  | 27717.32 | 41.06 | 0.28 | 42000 | ERW | 8.625 | 728 | [10 empty] | AGM 8 | 2586.61 | AGM 9 | 78.81 | 42.37 | 41.06 | 41.89 | 42.37 | 41.06 | 8920 | 39.18 | 41.28 | 33.7395 | -118.0068 | 27.411
GWD 8930 | Girth Weld |  | 27758.37 | 37.75 | 0.28 | 42000 | ERW | 8.625 | 728 | [10 empty] | AGM 8 | 2627.67 | AGM 9 | 37.75 | 41.06 | 39.18 | 42.37 | 41.06 | 39.18 | 8930 | 41.28 | 42.56 | 33.7396 | -118.0068 | 27.841
MRK 7 | Marker |  | 27796.12 | 1.43 | 0.28 | 42000 | ERW | 8.625 | 728 |  |  |  |  | 11:39 | [5 empty] | AGM 8 | 2665.42 | AGM 10 | 3205.09 | 37.75 | 1.43 | 42.37 | 41.06 | 39.18 | 8930 | 41.28 | 42.56 | 33.7397 | -118.0068 | 27.689 | AGM 9 7' West of Curb - Located in Goldenwest St
GWD 8940 | Girth Weld |  | 27797.55 | 41.28 | 0.28 | 42000 | ERW | 8.625 | 728 | [10 empty] | AGM 9 | 1.43 | AGM 10 | 3203.66 | 39.18 | 41.28 | 41.06 | 39.18 | 41.28 | 8940 | 42.56 | 42.36 | 33.7397 | -118.0068 | 27.675
GWD 8950 | Girth Weld |  | 27838.83 | 42.56 | 0.28 | 42000 | ERW | 8.625 | 728 | [10 empty] | AGM 9 | 42.71 | AGM 10 | 3162.37 | 41.28 | 42.56 | 39.18 | 41.28 | 42.56 | 8950 | 42.36 | 38.06 | 33.7398 | -118.0068 | 27.872
GWD 8960 | Girth Weld |  | 27881.39 | 42.36 | 0.28 | 42000 | ERW | 8.625 | 728 | [10 empty] | AGM 9 | 85.27 | AGM 10 | 3119.81 | 42.56 | 42.36 | 41.28 | 42.56 | 42.36 | 8960 | 38.06 | 42.94 | 33.7399 | -118.0068 | 27.969
GWD 8970 | Girth Weld |  | 27923.76 | 38.06 | 0.28 | 42000 | ERW | 8.625 | 728 | [10 empty] | AGM 9 | 127.63 | AGM 10 | 3077.45 | 42.36 | 38.06 | 42.56 | 42.36 | 38.06 | 8970 | 42.94 | 42.24 | 33.7401 | -118.0068 | 27.991
GWD 8980 | Girth Weld |  | 27961.82 | 42.94 | 0.28 | 42000 | ERW | 8.625 | 728 | [10 empty] | AGM 9 | 165.7 | AGM 10 | 3039.39 | 38.06 | 42.94 | 42.36 | 38.06 | 42.94 | 8980 | 42.24 | 40.49 | 33.7402 | -118.0068 | 27.34
GWD 8990 | Girth Weld |  | 28004.76 | 42.24 | 0.28 | 42000 | ERW | 8.625 | 728 | [10 empty] | AGM 9 | 208.64 | AGM 10 | 2996.45 | 42.94 | 42.24 | 38.06 | 42.94 | 42.24 | 8990 | 40.49 | 40.02 | 33.7403 | -118.0068 | 27.57
GWD 9000 | Girth Weld |  | 28047 | 40.49 | 0.28 | 42000 | ERW | 8.625 | 728 | [10 empty] | AGM 9 | 250.87 | AGM 10 | 2954.21 | 42.24 | 40.49 | 42.94 | 42.24 | 40.49 | 9000 | 40.02 | 41.24 | 33.7404 | -118.0068 | 27.74
GWD 9010 | Girth Weld |  | 28087.48 | 40.02 | 0.28 | 42000 | ERW | 8.625 | 728 | [10 empty] | AGM 9 | 291.36 | AGM 10 | 2913.72 | 40.49 | 40.02 | 42.24 | 40.49 | 40.02 | 9010 | 41.24 | 42.06 | 33.7405 | -118.0068 | 27.764
GWD 9020 | Girth Weld |  | 28127.5 | 41.24 | 0.28 | 42000 | ERW | 8.625 | 728 | [10 empty] | AGM 9 | 331.38 | AGM 10 | 2873.71 | 40.02 | 41.24 | 40.49 | 40.02 | 41.24 | 9020 | 42.06 | 42.76 | 33.7406 | -118.0068 | 27.584
GWD 9030 | Girth Weld |  | 28168.74 | 42.06 | 0.28 | 42000 | ERW | 8.625 | 728 | [10 empty] | AGM 9 | 372.62 | AGM 10 | 2832.46 | 41.24 | 42.06 | 40.02 | 41.24 | 42.06 | 9030 | 42.76 | 42.17 | 33.7407 | -118.0068 | 27.59
GWD 9040 | Girth Weld |  | 28210.8 | 42.76 | 0.28 | 42000 | ERW | 8.625 | 728 | [10 empty] | AGM 9 | 414.68 | AGM 10 | 2790.41 | 42.06 | 42.76 | 41.24 | 42.06 | 42.76 | 9040 | 42.17 | 40.23 | 33.7408 | -118.0068 | 27.659
GWD 9050 | Girth Weld |  | 28253.56 | 42.17 | 0.28 | 42000 | ERW | 8.625 | 728 | [10 empty] | AGM 9 | 457.44 | AGM 10 | 2747.65 | 42.76 | 42.17 | 42.06 | 42.76 | 42.17 | 9050 | 40.23 | 41.51 | 33.741 | -118.0068 | 28.172
GWD 9060 | Girth Weld |  | 28295.73 | 40.23 | 0.28 | 42000 | ERW | 8.625 | 728 | [10 empty] | AGM 9 | 499.61 | AGM 10 | 2705.48 | 42.17 | 40.23 | 42.76 | 42.17 | 40.23 | 9060 | 41.51 | 40.67 | 33.7411 | -118.0068 | 28.552
GWD 9070 | Girth Weld |  | 28335.96 | 41.51 | 0.28 | 42000 | ERW | 8.625 | 728 | [10 empty] | AGM 9 | 539.84 | AGM 10 | 2665.24 | 40.23 | 41.51 | 42.17 | 40.23 | 41.51 | 9070 | 40.67 | 38.92 | 33.7412 | -118.0068 | 28.21
GWD 9080 | Girth Weld |  | 28377.47 | 40.67 | 0.28 | 42000 | ERW | 8.625 | 728 | [10 empty] | AGM 9 | 581.35 | AGM 10 | 2623.73 | 41.51 | 40.67 | 40.23 | 41.51 | 40.67 | 9080 | 38.92 | 38.37 | 33.7413 | -118.0068 | 27.285
GWD 9090 | Girth Weld |  | 28418.15 | 38.92 | 0.28 | 42000 | ERW | 8.625 | 728 | [10 empty] | AGM 9 | 622.03 | AGM 10 | 2583.06 | 40.67 | 38.92 | 41.51 | 40.67 | 38.92 | 9090 | 38.37 | 40.16 | 33.7414 | -118.0068 | 26.506
GWD 9100 | Girth Weld |  | 28457.06 | 38.37 | 0.28 | 42000 | ERW | 8.625 | 728 | [10 empty] | AGM 9 | 660.94 | AGM 10 | 2544.14 | 38.92 | 38.37 | 40.67 | 38.92 | 38.37 | 9100 | 40.16 | 40.48 | 33.7415 | -118.0068 | 26.11
GWD 9110 | Girth Weld |  | 28495.43 | 40.16 | 0.28 | 42000 | ERW | 8.625 | 728 | [10 empty] | AGM 9 | 699.31 | AGM 10 | 2505.78 | 38.37 | 40.16 | 38.92 | 38.37 | 40.16 | 9110 | 40.48 | 29.35 | 33.7416 | -118.0068 | 26.086
GWD 9120 | Girth Weld |  | 28535.59 | 40.48 | 0.28 | 42000 | ERW | 8.625 | 728 | [10 empty] | AGM 9 | 739.47 | AGM 10 | 2465.61 | 40.16 | 40.48 | 38.37 | 40.16 | 40.48 | 9120 | 29.35 | 39.66 | 33.7417 | -118.0068 | 25.611
GWD 9130 | Girth Weld |  | 28576.07 | 29.35 | 0.28 | 42000 | ERW | 8.625 | 728 | [10 empty] | AGM 9 | 779.95 | AGM 10 | 2425.14 | 40.48 | 29.35 | 40.16 | 40.48 | 29.35 | 9130 | 39.66 | 28.15 | 33.7419 | -118.0068 | 25.876
GWD 9140 | Girth Weld |  | 28605.42 | 39.66 | 0.28 | 42000 | ERW | 8.625 | 728 | [10 empty] | AGM 9 | 809.3 | AGM 10 | 2395.78 | 29.35 | 39.66 | 40.48 | 29.35 | 39.66 | 9140 | 28.15 | 41.69 | 33.7419 | -118.0068 | 26.151
GWD 9150 | Girth Weld |  | 28645.09 | 28.15 | 0.28 | 42000 | ERW | 8.625 | 728 | [10 empty] | AGM 9 | 848.96 | AGM 10 | 2356.12 | 39.66 | 28.15 | 29.35 | 39.66 | 28.15 | 9150 | 41.69 | 40.53 | 33.742 | -118.0068 | 26.843
GWD 9160 | Girth Weld |  | 28673.24 | 41.69 | 0.28 | 42000 | ERW | 8.625 | 728 | [10 empty] | AGM 9 | 877.11 | AGM 10 | 2327.97 | 28.15 | 41.69 | 39.66 | 28.15 | 41.69 | 9160 | 40.53 | 33.03 | 33.7421 | -118.0068 | 27.23
GWD 9170 | Girth Weld |  | 28714.93 | 40.53 | 0.28 | 42000 | ERW | 8.625 | 728 | [10 empty] | AGM 9 | 918.8 | AGM 10 | 2286.28 | 41.69 | 40.53 | 28.15 | 41.69 | 40.53 | 9170 | 33.03 | 41.78 | 33.7422 | -118.0068 | 27.577
GWD 9180 | Girth Weld |  | 28755.46 | 33.03 | 0.28 | 42000 | ERW | 8.625 | 728 | [10 empty] | AGM 9 | 959.34 | AGM 10 | 2245.75 | 40.53 | 33.03 | 41.69 | 40.53 | 33.03 | 9180 | 41.78 | 42.49 | 33.7423 | -118.0068 | 28.016
GWD 9190 | Girth Weld |  | 28788.49 | 41.78 | 0.28 | 42000 | ERW | 8.625 | 728 | [10 empty] | AGM 9 | 992.37 | AGM 10 | 2212.72 | 33.03 | 41.78 | 40.53 | 33.03 | 41.78 | 9190 | 42.49 | 41.46 | 33.7424 | -118.0068 | 28.155
GWD 9200 | Girth Weld |  | 28830.27 | 42.49 | 0.28 | 42000 | ERW | 8.625 | 728 | [10 empty] | AGM 9 | 1034.14 | AGM 10 | 2170.94 | 41.78 | 42.49 | 33.03 | 41.78 | 42.49 | 9200 | 41.46 | 41.17 | 33.7426 | -118.0068 | 27.904
GWD 9210 | Girth Weld |  | 28872.76 | 41.46 | 0.28 | 42000 | ERW | 8.625 | 728 | [10 empty] | AGM 9 | 1076.64 | AGM 10 | 2128.45 | 42.49 | 41.46 | 41.78 | 42.49 | 41.46 | 9210 | 41.17 | 40.45 | 33.7427 | -118.0068 | 27.856
GWD 9220 | Girth Weld |  | 28914.22 | 41.17 | 0.28 | 42000 | ERW | 8.625 | 728 | [10 empty] | AGM 9 | 1118.1 | AGM 10 | 2086.98 | 41.46 | 41.17 | 42.49 | 41.46 | 41.17 | 9220 | 40.45 | 41.37 | 33.7428 | -118.0068 | 27.73
GWD 9230 | Girth Weld |  | 28955.4 | 40.45 | 0.28 | 42000 | ERW | 8.625 | 728 | [10 empty] | AGM 9 | 1159.28 | AGM 10 | 2045.81 | 41.17 | 40.45 | 41.46 | 41.17 | 40.45 | 9230 | 41.37 | 41.49 | 33.7429 | -118.0068 | 27.683
GWD 9240 | Girth Weld |  | 28995.84 | 41.37 | 0.28 | 42000 | ERW | 8.625 | 728 | [10 empty] | AGM 9 | 1199.72 | AGM 10 | 2005.36 | 40.45 | 41.37 | 41.17 | 40.45 | 41.37 | 9240 | 41.49 | 43.06 | 33.743 | -118.0068 | 27.787
GWD 9250 | Girth Weld |  | 29037.22 | 41.49 | 0.28 | 42000 | ERW | 8.625 | 728 | [10 empty] | AGM 9 | 1241.1 | AGM 10 | 1963.99 | 41.37 | 41.49 | 40.45 | 41.37 | 41.49 | 9250 | 43.06 | 42.45 | 33.7431 | -118.0068 | 27.955
GWD 9260 | Girth Weld |  | 29078.7 | 43.06 | 0.28 | 42000 | ERW | 8.625 | 728 | [10 empty] | AGM 9 | 1282.58 | AGM 10 | 1922.5 | 41.49 | 43.06 | 41.37 | 41.49 | 43.06 | 9260 | 42.45 | 38.37 | 33.7432 | -118.0068 | 28.361
GWD 9270 | Girth Weld |  | 29121.77 | 42.45 | 0.28 | 42000 | ERW | 8.625 | 728 | [10 empty] | AGM 9 | 1325.65 | AGM 10 | 1879.44 | 43.06 | 42.45 | 41.49 | 43.06 | 42.45 | 9270 | 38.37 | 37.75 | 33.7434 | -118.0068 | 28.649
GWD 9280 | Girth Weld |  | 29164.22 | 38.37 | 0.28 | 42000 | ERW | 8.625 | 728 | [10 empty] | AGM 9 | 1368.1 | AGM 10 | 1836.99 | 42.45 | 38.37 | 43.06 | 42.45 | 38.37 | 9280 | 37.75 | 40.57 | 33.7435 | -118.0068 | 28.559
GWD 9290 | Girth Weld |  | 29202.59 | 37.75 | 0.28 | 42000 | ERW | 8.625 | 728 | [10 empty] | AGM 9 | 1406.46 | AGM 10 | 1798.62 | 38.37 | 37.75 | 42.45 | 38.37 | 37.75 | 9290 | 40.57 | 40.93 | 33.7436 | -118.0069 | 28.156
GWD 9300 | Girth Weld |  | 29240.33 | 40.57 | 0.28 | 42000 | ERW | 8.625 | 728 | [10 empty] | AGM 9 | 1444.21 | AGM 10 | 1760.87 | 37.75 | 40.57 | 38.37 | 37.75 | 40.57 | 9300 | 40.93 | 37.55 | 33.7437 | -118.0069 | 28.636
GWD 9310 | Girth Weld |  | 29280.91 | 40.93 | 0.28 | 42000 | ERW | 8.625 | 728 | [10 empty] | AGM 9 | 1484.79 | AGM 10 | 1720.3 | 40.57 | 40.93 | 37.75 | 40.57 | 40.93 | 9310 | 37.55 | 41.5 | 33.7438 | -118.0069 | 28.579
GWD 9320 | Girth Weld |  | 29321.84 | 37.55 | 0.28 | 42000 | ERW | 8.625 | 728 | [10 empty] | AGM 9 | 1525.72 | AGM 10 | 1679.37 | 40.93 | 37.55 | 40.57 | 40.93 | 37.55 | 9320 | 41.5 | 9.18 | 33.7439 | -118.0069 | 28.981
GWD 9330 | Girth Weld |  | 29359.39 | 41.5 | 0.28 | 42000 | ERW | 8.625 | 728 | [10 empty] | AGM 9 | 1563.26 | AGM 10 | 1641.82 | 37.55 | 41.5 | 40.93 | 37.55 | 41.5 | 9330 | 9.18 | 39.85 | 33.744 | -118.0069 | 28.924
GWD 9340 | Girth Weld |  | 29400.88 | 9.18 | 0.28 | 42000 | ERW | 8.625 | 728 | [10 empty] | AGM 9 | 1604.76 | AGM 10 | 1600.33 | 41.5 | 9.18 | 37.55 | 41.5 | 9.18 | 9340 | 39.85 | 2.99 | 33.7441 | -118.0069 | 28.606
GWD 9350 | Girth Weld |  | 29410.07 | 39.85 | 0.28 | 42000 | ERW | 8.625 | 728 | [10 empty] | AGM 9 | 1613.94 | AGM 10 | 1591.14 | 9.18 | 39.85 | 41.5 | 9.18 | 39.85 | 9350 | 2.99 | 36.61 | 33.7441 | -118.0069 | 28.679
GWD 9360 | Girth Weld |  | 29449.92 | 2.99 | 0.28 | 42000 | ERW | 8.625 | 728 | [10 empty] | AGM 9 | 1653.79 | AGM 10 | 1551.29 | 39.85 | 2.99 | 9.18 | 39.85 | 2.99 | 9360 | 36.61 | 31.58 | 33.7443 | -118.0069 | 29.294
GWD 9370 | Girth Weld |  | 29452.91 | 36.61 | 0.28 | 42000 | ERW | 8.625 | 728 | [10 empty] | AGM 9 | 1656.78 | AGM 10 | 1548.3 | 2.99 | 36.61 | 39.85 | 2.99 | 36.61 | 9370 | 31.58 | 42.62 | 33.7443 | -118.0069 | 29.32
GWD 9380 | Girth Weld |  | 29489.52 | 31.58 | 0.28 | 42000 | ERW | 8.625 | 728 | [10 empty] | AGM 9 | 1693.4 | AGM 10 | 1511.69 | 36.61 | 31.58 | 2.99 | 36.61 | 31.58 | 9380 | 42.62 | 42.33 | 33.7444 | -118.0069 | 29.894
GWD 9390 | Girth Weld |  | 29521.1 | 42.62 | 0.28 | 42000 | ERW | 8.625 | 728 | [10 empty] | AGM 9 | 1724.98 | AGM 10 | 1480.11 | 31.58 | 42.62 | 36.61 | 31.58 | 42.62 | 9390 | 42.33 | 42.77 | 33.7445 | -118.0069 | 30.504
GWD 9400 | Girth Weld |  | 29563.72 | 42.33 | 0.28 | 42000 | ERW | 8.625 | 728 | [10 empty] | AGM 9 | 1767.59 | AGM 10 | 1437.49 | 42.62 | 42.33 | 31.58 | 42.62 | 42.33 | 9400 | 42.77 | 30.03 | 33.7446 | -118.0069 | 30.592
GWD 9410 | Girth Weld |  | 29606.05 | 42.77 | 0.28 | 42000 | ERW | 8.625 | 728 | [10 empty] | AGM 9 | 1809.93 | AGM 10 | 1395.16 | 42.33 | 42.77 | 42.62 | 42.33 | 42.77 | 9410 | 30.03 | 42.5 | 33.7447 | -118.0069 | 31.369
GWD 9420 | Girth Weld |  | 29648.83 | 30.03 | 0.28 | 42000 | ERW | 8.625 | 728 | [10 empty] | AGM 9 | 1852.7 | AGM 10 | 1352.38 | 42.77 | 30.03 | 42.33 | 42.77 | 30.03 | 9420 | 42.5 | 41.22 | 33.7448 | -118.0069 | 32.599
GWD 9430 | Girth Weld |  | 29678.86 | 42.5 | 0.28 | 42000 | ERW | 8.625 | 728 | [10 empty] | AGM 9 | 1882.74 | AGM 10 | 1322.35 | 30.03 | 42.5 | 42.77 | 30.03 | 42.5 | 9430 | 41.22 | 43.07 | 33.7449 | -118.0069 | 33.7
GWD 9440 | Girth Weld |  | 29721.36 | 41.22 | 0.28 | 42000 | ERW | 8.625 | 728 | [10 empty] | AGM 9 | 1925.24 | AGM 10 | 1279.85 | 42.5 | 41.22 | 30.03 | 42.5 | 41.22 | 9440 | 43.07 | 43.18 | 33.745 | -118.0069 | 35.325
GWD 9450 | Girth Weld |  | 29762.58 | 43.07 | 0.28 | 42000 | ERW | 8.625 | 728 | [10 empty] | AGM 9 | 1966.46 | AGM 10 | 1238.63 | 41.22 | 43.07 | 42.5 | 41.22 | 43.07 | 9450 | 43.18 | 42.51 | 33.7451 | -118.0069 | 37.689
GWD 9460 | Girth Weld |  | 29805.65 | 43.18 | 0.28 | 42000 | ERW | 8.625 | 728 | [10 empty] | AGM 9 | 2009.53 | AGM 10 | 1195.56 | 43.07 | 43.18 | 41.22 | 43.07 | 43.18 | 9460 | 42.51 | 43.62 | 33.7452 | -118.0069 | 39.672
GWD 9470 | Girth Weld |  | 29848.83 | 42.51 | 0.28 | 42000 | ERW | 8.625 | 728 | [10 empty] | AGM 9 | 2052.71 | AGM 10 | 1152.38 | 43.18 | 42.51 | 43.07 | 43.18 | 42.51 | 9470 | 43.62 | 24.01 | 33.7454 | -118.0069 | 41.449
GWD 9480 | Girth Weld |  | 29891.34 | 43.62 | 0.28 | 42000 | ERW | 8.625 | 728 | [10 empty] | AGM 9 | 2095.22 | AGM 10 | 1109.87 | 42.51 | 43.62 | 43.18 | 42.51 | 43.62 | 9480 | 24.01 | 43.01 | 33.7455 | -118.0069 | 43.179
GWD 9490 | Girth Weld |  | 29934.96 | 24.01 | 0.28 | 42000 | ERW | 8.625 | 728 | [10 empty] | AGM 9 | 2138.83 | AGM 10 | 1066.25 | 43.62 | 24.01 | 42.51 | 43.62 | 24.01 | 9490 | 43.01 | 42.15 | 33.7456 | -118.0069 | 45.396
GWD 9500 | Girth Weld |  | 29958.97 | 43.01 | 0.28 | 42000 | ERW | 8.625 | 728 | [10 empty] | AGM 9 | 2162.85 | AGM 10 | 1042.24 | 24.01 | 43.01 | 43.62 | 24.01 | 43.01 | 9500 | 42.15 | 42.87 | 33.7457 | -118.0069 | 47.211
GWD 9510 | Girth Weld |  | 30001.98 | 7.12 | 0.28 | 42000 | ERW | 8.625 | 728 | [10 empty] | AGM 9 | 2205.86 | AGM 10 | 999.23 | 43.01 | 42.15 | 24.01 | 43.01 | 42.15 | 9510 | 42.87 | 44.1 | 33.7458 | -118.0069 | 50.35
CSG 3 | Casing Start |  | 30009.1 | 35.02 | 0.28 | 42000 | ERW | 8.625 | 728 |  |  | 5195.338 | [7 empty] | AGM 9 | 2212.98 | AGM 10 | 992.1 | 7.12 | 35.02 | 24.01 | 43.01 | 42.15 | 9510 | 42.87 | 44.1 | 33.7458 | -118.0069 | 50.735 | Casing - Start
GWD 9520 | Girth Weld |  | 30044.13 | 42.87 | 0.28 | 42000 | ERW | 8.625 | 728 | [10 empty] | AGM 9 | 2248.01 | AGM 10 | 957.08 | 42.15 | 42.87 | 43.01 | 42.15 | 42.87 | 9520 | 44.1 | 43.59 | 33.7459 | -118.0069 | 52.23
GWD 9530 | Girth Weld |  | 30087 | 44.1 | 0.28 | 42000 | ERW | 8.625 | 728 | [10 empty] | AGM 9 | 2290.88 | AGM 10 | 914.21 | 42.87 | 44.1 | 42.15 | 42.87 | 44.1 | 9530 | 43.59 | 43.07 | 33.746 | -118.0069 | 53.894
GWD 9540 | Girth Weld |  | 30131.1 | 43.59 | 0.28 | 42000 | ERW | 8.625 | 728 | [10 empty] | AGM 9 | 2334.98 | AGM 10 | 870.11 | 44.1 | 43.59 | 42.87 | 44.1 | 43.59 | 9540 | 43.07 | 42.96 | 33.7461 | -118.0069 | 55.57
GWD 9550 | Girth Weld |  | 30174.69 | 43.07 | 0.28 | 42000 | ERW | 8.625 | 728 | [10 empty] | AGM 9 | 2378.57 | AGM 10 | 826.52 | 43.59 | 43.07 | 44.1 | 43.59 | 43.07 | 9550 | 42.96 | 43.47 | 33.7463 | -118.0069 | 56.552
GWD 9560 | Girth Weld |  | 30217.76 | 42.96 | 0.28 | 42000 | ERW | 8.625 | 728 | [10 empty] | AGM 9 | 2421.64 | AGM 10 | 783.45 | 43.07 | 42.96 | 43.59 | 43.07 | 42.96 | 9560 | 43.47 | 42.71 | 33.7464 | -118.0069 | 57.344
GWD 9570 | Girth Weld |  | 30260.72 | 43.47 | 0.28 | 42000 | ERW | 8.625 | 728 | [10 empty] | AGM 9 | 2464.6 | AGM 10 | 740.49 | 42.96 | 43.47 | 43.07 | 42.96 | 43.47 | 9570 | 42.71 | 43.1 | 33.7465 | -118.0069 | 57.792
GWD 9580 | Girth Weld |  | 30304.19 | 42.71 | 0.28 | 42000 | ERW | 8.625 | 728 | [10 empty] | AGM 9 | 2508.07 | AGM 10 | 697.01 | 43.47 | 42.71 | 42.96 | 43.47 | 42.71 | 9580 | 43.1 | 41.56 | 33.7466 | -118.0069 | 57.839
GWD 9590 | Girth Weld |  | 30346.91 | 43.1 | 0.28 | 42000 | ERW | 8.625 | 728 | [10 empty] | AGM 9 | 2550.78 | AGM 10 | 654.3 | 42.71 | 43.1 | 43.47 | 42.71 | 43.1 | 9590 | 41.56 | 31.42 | 33.7467 | -118.0069 | 57.643
GWD 9600 | Girth Weld |  | 30390.01 | 41.56 | 0.28 | 42000 | ERW | 8.625 | 728 | [10 empty] | AGM 9 | 2593.88 | AGM 10 | 611.2 | 43.1 | 41.56 | 42.71 | 43.1 | 41.56 | 9600 | 31.42 | 40.02 | 33.7468 | -118.0069 | 57.289
GWD 9610 | Girth Weld |  | 30431.57 | 10.48 | 0.28 | 42000 | ERW | 8.625 | 728 | [10 empty] | AGM 9 | 2635.44 | AGM 10 | 569.64 | 41.56 | 31.42 | 43.1 | 41.56 | 31.42 | 9610 | 40.02 | 10.37 | 33.747 | -118.0069 | 56.237
CSG 3 | Casing End |  | 30442.05 | 20.94 | 0.28 | 42000 | ERW | 8.625 | 728 | [10 empty] | AGM 9 | 2645.93 | AGM 10 | 559.16 | 10.48 | 20.94 | 43.1 | 41.56 | 31.42 | 9610 | 40.02 | 10.37 | 33.747 | -118.0069 | 56.029 | Casing - End
GWD 9620 | Girth Weld |  | 30462.99 | 40.02 | 0.28 | 42000 | ERW | 8.625 | 728 | [10 empty] | AGM 9 | 2666.87 | AGM 10 | 538.22 | 31.42 | 40.02 | 41.56 | 31.42 | 40.02 | 9620 | 10.37 | 43.6 | 33.747 | -118.0069 | 55.801
GWD 9630 | Girth Weld |  | 30503.01 | 10.37 | 0.28 | 42000 | ERW | 8.625 | 728 | [10 empty] | AGM 9 | 2706.89 | AGM 10 | 498.2 | 40.02 | 10.37 | 31.42 | 40.02 | 10.37 | 9630 | 43.6 | 43.39 | 33.7472 | -118.0069 | 54.992
GWD 9640 | Girth Weld |  | 30513.38 | 43.6 | 0.28 | 42000 | ERW | 8.625 | 728 | [10 empty] | AGM 9 | 2717.26 | AGM 10 | 487.82 | 10.37 | 43.6 | 40.02 | 10.37 | 43.6 | 9640 | 43.39 | 33.51 | 33.7472 | -118.0069 | 54.753
GWD 9650 | Girth Weld |  | 30556.98 | 43.39 | 0.28 | 42000 | ERW | 8.625 | 728 | [10 empty] | AGM 9 | 2760.86 | AGM 10 | 444.22 | 43.6 | 43.39 | 10.37 | 43.6 | 43.39 | 9650 | 33.51 | 42.88 | 33.7473 | -118.0069 | 53
GWD 9660 | Girth Weld |  | 30600.38 | 33.51 | 0.28 | 42000 | ERW | 8.625 | 728 | [10 empty] | AGM 9 | 2804.25 | AGM 10 | 400.83 | 43.39 | 33.51 | 43.6 | 43.39 | 33.51 | 9660 | 42.88 | 43.83 | 33.7474 | -118.0069 | 50.491
GWD 9670 | Girth Weld |  | 30633.88 | 42.88 | 0.28 | 42000 | ERW | 8.625 | 728 | [10 empty] | AGM 9 | 2837.76 | AGM 10 | 367.33 | 33.51 | 42.88 | 43.39 | 33.51 | 42.88 | 9670 | 43.83 | 43.96 | 33.7475 | -118.0069 | 48.896
GWD 9680 | Girth Weld |  | 30676.76 | 43.83 | 0.28 | 42000 | ERW | 8.625 | 728 | [10 empty] | AGM 9 | 2880.64 | AGM 10 | 324.44 | 42.88 | 43.83 | 33.51 | 42.88 | 43.83 | 9680 | 43.96 | 43.06 | 33.7476 | -118.0069 | 45.742
GWD 9690 | Girth Weld |  | 30720.59 | 43.96 | 0.28 | 42000 | ERW | 8.625 | 728 | [10 empty] | AGM 9 | 2924.47 | AGM 10 | 280.62 | 43.83 | 43.96 | 42.88 | 43.83 | 43.96 | 9690 | 43.06 | 42.95 | 33.7478 | -118.0069 | 43.08
GWD 9700 | Girth Weld |  | 30764.55 | 43.06 | 0.28 | 42000 | ERW | 8.625 | 728 | [10 empty] | AGM 9 | 2968.43 | AGM 10 | 236.65 | 43.96 | 43.06 | 43.83 | 43.96 | 43.06 | 9700 | 42.95 | 43.3 | 33.7479 | -118.0069 | 39.984
GWD 9710 | Girth Weld |  | 30807.61 | 42.95 | 0.28 | 42000 | ERW | 8.625 | 728 | [10 empty] | AGM 9 | 3011.49 | AGM 10 | 193.59 | 43.06 | 42.95 | 43.96 | 43.06 | 42.95 | 9710 | 43.3 | 5.07 | 33.748 | -118.0069 | 37.602
GWD 9720 | Girth Weld |  | 30850.56 | 42.7 | 0.28 | 42000 | ERW | 8.625 | 728 | [10 empty] | AGM 9 | 3054.44 | AGM 10 | 150.64 | 42.95 | 43.3 | 43.06 | 42.95 | 43.3 | 9720 | 5.07 | 37.93 | 33.7481 | -118.0069 | 35.229
MOB 2 | Metal Object |  | 30893.26 | 0.6 | 0.28 | 42000 | ERW | 8.625 | 728 |  |  | 3.581 | 2.029 | 6:09 | [5 empty] | AGM 9 | 3097.14 | AGM 10 | 107.94 | 42.7 | 0.6 | 43.06 | 42.95 | 43.3 | 9720 | 5.07 | 37.93 | 33.7482 | -118.0069 | 33.001 | Touching Metal Object
GWD 9730 | Girth Weld |  | 30893.87 | 5.07 | 0.28 | 42000 | ERW | 8.625 | 728 | [10 empty] | AGM 9 | 3097.75 | AGM 10 | 107.34 | 43.3 | 5.07 | 42.95 | 43.3 | 5.07 | 9730 | 37.93 | 40.59 | 33.7482 | -118.0069 | 32.98
GWD 9740 | Girth Weld |  | 30898.93 | 37.93 | 0.28 | 42000 | ERW | 8.625 | 728 | [10 empty] | AGM 9 | 3102.81 | AGM 10 | 102.27 | 5.07 | 37.93 | 43.3 | 5.07 | 37.93 | 9740 | 40.59 | 35.42 | 33.7482 | -118.0069 | 32.779
GWD 9750 | Girth Weld |  | 30936.86 | 40.59 | 0.28 | 42000 | ERW | 8.625 | 728 | [10 empty] | AGM 9 | 3140.74 | AGM 10 | 64.35 | 37.93 | 40.59 | 5.07 | 37.93 | 40.59 | 9750 | 35.42 | 31.89 | 33.7484 | -118.0069 | 32.618
GWD 9760 | Girth Weld |  | 30977.45 | 23.75 | 0.28 | 42000 | ERW | 8.625 | 728 | [10 empty] | AGM 9 | 3181.33 | AGM 10 | 23.75 | 40.59 | 35.42 | 37.93 | 40.59 | 35.42 | 9760 | 31.89 | 38.81 | 33.7485 | -118.0069 | 31.934
MRK 8 | Marker |  | 31001.21 | 11.67 | 0.28 | 42000 | ERW | 8.625 | 728 |  |  |  |  | 11:36 | [5 empty] | AGM 9 | 3205.09 | AGM 11 | 2677.69 | 23.75 | 11.67 | 37.93 | 40.59 | 35.42 | 9760 | 31.89 | 38.81 | 33.7485 | -118.0069 | 31.3 | AGM 10 7' West of Curb - Located in Goldenwest St
GWD 9770 | Girth Weld |  | 31012.88 | 31.89 | 0.28 | 42000 | ERW | 8.625 | 728 | [10 empty] | AGM 10 | 11.67 | AGM 11 | 2666.02 | 35.42 | 31.89 | 40.59 | 35.42 | 31.89 | 9770 | 38.81 | 38.26 | 33.7486 | -118.0069 | 31.142
GWD 9780 | Girth Weld |  | 31044.76 | 38.81 | 0.28 | 42000 | ERW | 8.625 | 728 | [10 empty] | AGM 10 | 43.56 | AGM 11 | 2634.14 | 31.89 | 38.81 | 35.42 | 31.89 | 38.81 | 9780 | 38.26 | 35.28 | 33.7486 | -118.0069 | 31.531
GWD 9790 | Girth Weld |  | 31083.57 | 38.26 | 0.28 | 42000 | ERW | 8.625 | 728 | [10 empty] | AGM 10 | 82.37 | AGM 11 | 2595.32 | 38.81 | 38.26 | 31.89 | 38.81 | 38.26 | 9790 | 35.28 | 37 | 33.7488 | -118.0069 | 31.759
GWD 9800 | Girth Weld |  | 31121.83 | 35.28 | 0.28 | 42000 | ERW | 8.625 | 728 | [10 empty] | AGM 10 | 120.62 | AGM 11 | 2557.07 | 38.26 | 35.28 | 38.81 | 38.26 | 35.28 | 9800 | 37 | 26.49 | 33.7489 | -118.0069 | 31.855
GWD 9810 | Girth Weld |  | 31157.11 | 37 | 0.28 | 42000 | ERW | 8.625 | 728 | [10 empty] | AGM 10 | 155.91 | AGM 11 | 2521.78 | 35.28 | 37 | 38.26 | 35.28 | 37 | 9810 | 26.49 | 1.76 | 33.749 | -118.0069 | 31.715
GWD 9820 | Girth Weld |  | 31194.11 | 20.55 | 0.28 | 42000 | ERW | 8.625 | 728 | [10 empty] | AGM 10 | 192.9 | AGM 11 | 2484.79 | 37 | 26.49 | 35.28 | 37 | 26.49 | 9820 | 1.76 | 19.83 | 33.7491 | -118.0069 | 32.202
MOB 3 | Metal Object |  | 31214.66 | 5.94 | 0.28 | 42000 | ERW | 8.625 | 728 |  |  | 3.764 | 2.239 | 11:47 | [5 empty] | AGM 10 | 213.45 | AGM 11 | 2464.24 | 20.55 | 5.94 | 35.28 | 37 | 26.49 | 9820 | 1.76 | 19.83 | 33.7491 | -118.0069 | 32.389 | Touching Metal Object
GWD 9830 | Girth Weld |  | 31220.59 | 1.76 | 0.28 | 42000 | ERW | 8.625 | 728 | [10 empty] | AGM 10 | 219.39 | AGM 11 | 2458.3 | 26.49 | 1.76 | 37 | 26.49 | 1.76 | 9830 | 19.83 | 45.72 | 33.7491 | -118.0069 | 32.295
GWD 9840 | Girth Weld |  | 31222.35 | 14.51 | 0.28 | 42000 | ERW | 8.625 | 728 | [10 empty] | AGM 10 | 221.15 | AGM 11 | 2456.54 | 1.76 | 19.83 | 26.49 | 1.76 | 19.83 | 9840 | 45.72 | 45.35 | 33.7491 | -118.0069 | 32.246
MOB 4 | Metal Object |  | 31236.86 | 5.32 | 0.28 | 42000 | ERW | 8.625 | 728 |  |  | 2.272 | 3.02 | 12:09 | [5 empty] | AGM 10 | 235.66 | AGM 11 | 2442.03 | 14.51 | 5.32 | 26.49 | 1.76 | 19.83 | 9840 | 45.72 | 45.35 | 33.7492 | -118.0069 | 31.707 | Touching Metal Object
GWD 9850 | Girth Weld |  | 31242.18 | 45.72 | 0.28 | 42000 | ERW | 8.625 | 728 | [10 empty] | AGM 10 | 240.97 | AGM 11 | 2436.72 | 19.83 | 45.72 | 1.76 | 19.83 | 45.72 | 9850 | 45.35 | 51.88 | 33.7492 | -118.0069 | 31.546
GWD 9860 | Girth Weld |  | 31287.9 | 45.35 | 0.28 | 42000 | ERW | 8.625 | 728 | [10 empty] | AGM 10 | 286.7 | AGM 11 | 2390.99 | 45.72 | 45.35 | 19.83 | 45.72 | 45.35 | 9860 | 51.88 | 50.4 | 33.7493 | -118.0069 | 31.416
GWD 9870 | Girth Weld |  | 31333.26 | 51.88 | 0.28 | 42000 | ERW | 8.625 | 728 | [10 empty] | AGM 10 | 332.05 | AGM 11 | 2345.64 | 45.35 | 51.88 | 45.72 | 45.35 | 51.88 | 9870 | 50.4 | 25.69 | 33.7494 | -118.0069 | 31.753
GWD 9880 | Girth Weld |  | 31385.13 | 50.4 | 0.28 | 42000 | ERW | 8.625 | 728 | [10 empty] | AGM 10 | 383.93 | AGM 11 | 2293.76 | 51.88 | 50.4 | 45.35 | 51.88 | 50.4 | 9880 | 25.69 | 19.16 | 33.7496 | -118.0069 | 31.997
GWD 9890 | Girth Weld |  | 31435.54 | 25.69 | 0.28 | 42000 | ERW | 8.625 | 728 | [10 empty] | AGM 10 | 434.33 | AGM 11 | 2243.36 | 50.4 | 25.69 | 51.88 | 50.4 | 25.69 | 9890 | 19.16 | 41.51 | 33.7497 | -118.0069 | 32.681
GWD 9900 | Girth Weld |  | 31461.23 | 19.16 | 0.28 | 42000 | ERW | 8.625 | 728 | [10 empty] | AGM 10 | 460.02 | AGM 11 | 2217.67 | 25.69 | 19.16 | 50.4 | 25.69 | 19.16 | 9900 | 41.51 | 39.81 | 33.7498 | -118.0069 | 32.94
GWD 9910 | Girth Weld |  | 31480.4 | 41.51 | 0.28 | 42000 | ERW | 8.625 | 728 | [10 empty] | AGM 10 | 479.19 | AGM 11 | 2198.5 | 19.16 | 41.51 | 25.69 | 19.16 | 41.51 | 9910 | 39.81 | 41.65 | 33.7498 | -118.0069 | 32.844
GWD 9920 | Girth Weld |  | 31521.9 | 39.81 | 0.28 | 42000 | ERW | 8.625 | 728 | [10 empty] | AGM 10 | 520.7 | AGM 11 | 2156.99 | 41.51 | 39.81 | 19.16 | 41.51 | 39.81 | 9920 | 41.65 | 53.94 | 33.75 | -118.0069 | 32.752
GWD 9930 | Girth Weld |  | 31561.71 | 41.65 | 0.28 | 42000 | ERW | 8.625 | 728 | [10 empty] | AGM 10 | 560.51 | AGM 11 | 2117.18 | 39.81 | 41.65 | 41.51 | 39.81 | 41.65 | 9930 | 53.94 | 41.77 | 33.7501 | -118.0069 | 33.383
GWD 9940 | Girth Weld |  | 31603.37 | 53.94 | 0.28 | 42000 | ERW | 8.625 | 728 | [10 empty] | AGM 10 | 602.16 | AGM 11 | 2075.53 | 41.65 | 53.94 | 39.81 | 41.65 | 53.94 | 9940 | 41.77 | 54.3 | 33.7502 | -118.0069 | 33.774
GWD 9950 | Girth Weld |  | 31657.31 | 41.77 | 0.28 | 42000 | ERW | 8.625 | 728 | [10 empty] | AGM 10 | 656.1 | AGM 11 | 2021.59 | 53.94 | 41.77 | 41.65 | 53.94 | 41.77 | 9950 | 54.3 | 52.49 | 33.7503 | -118.0069 | 35.061
GWD 9960 | Girth Weld |  | 31699.08 | 54.3 | 0.28 | 42000 | ERW | 8.625 | 728 | [10 empty] | AGM 10 | 697.87 | AGM 11 | 1979.82 | 41.77 | 54.3 | 53.94 | 41.77 | 54.3 | 9960 | 52.49 | 54 | 33.7504 | -118.0069 | 35.566
GWD 9970 | Girth Weld |  | 31753.38 | 52.49 | 0.28 | 42000 | ERW | 8.625 | 728 | [10 empty] | AGM 10 | 752.17 | AGM 11 | 1925.52 | 54.3 | 52.49 | 41.77 | 54.3 | 52.49 | 9970 | 54 | 22.44 | 33.7506 | -118.0069 | 36.324
GWD 9980 | Girth Weld |  | 31805.86 | 54 | 0.28 | 42000 | ERW | 8.625 | 728 | [10 empty] | AGM 10 | 804.66 | AGM 11 | 1873.03 | 52.49 | 54 | 54.3 | 52.49 | 54 | 9980 | 22.44 | 1.63 | 33.7507 | -118.0069 | 35.938
GWD 9990 | Girth Weld |  | 31859.87 | 22.44 | 0.28 | 42000 | ERW | 8.625 | 728 | [10 empty] | AGM 10 | 858.66 | AGM 11 | 1819.03 | 54 | 22.44 | 52.49 | 54 | 22.44 | 9990 | 1.63 | 6.98 | 33.7509 | -118.0069 | 35.837
GWD 10000 | Girth Weld |  | 31882.3 | 0.85 | 0.28 | 42000 | ERW | 8.625 | 728 | [10 empty] | AGM 10 | 881.1 | AGM 11 | 1796.59 | 22.44 | 1.63 | 54 | 22.44 | 1.63 | 10000 | 6.98 | 1.68 | 33.7509 | -118.0069 | 35.733
BND 82 | Bend |  | 31883.15 | 0.78 | 0.28 | 42000 | ERW | 8.625 | 728 |  |  | 24.996 | [7 empty] | AGM 10 | 881.94 | AGM 11 | 1795.75 | 0.85 | 0.78 | 54 | 22.44 | 1.63 | 10000 | 6.98 | 1.68 | 33.751 | -118.0069 | 35.796 | 3.0D 47.6 deg right turn sag bend
GWD 10010 | Girth Weld |  | 31883.93 | 6.98 | 0.28 | 42000 | ERW | 8.625 | 728 | [10 empty] | AGM 10 | 882.72 | AGM 11 | 1794.97 | 1.63 | 6.98 | 22.44 | 1.63 | 6.98 | 10010 | 1.68 | 8.3 | 33.751 | -118.0069 | 35.966
GWD 10020 | Girth Weld |  | 31890.91 | 0.89 | 0.28 | 42000 | ERW | 8.625 | 728 | [10 empty] | AGM 10 | 889.7 | AGM 11 | 1787.99 | 6.98 | 1.68 | 1.63 | 6.98 | 1.68 | 10020 | 8.3 | 22.94 | 33.751 | -118.0069 | 38.16
BND 83 | Bend |  | 31891.8 | 0.79 | 0.28 | 42000 | ERW | 8.625 | 728 |  |  | 24.667 | [7 empty] | AGM 10 | 890.6 | AGM 11 | 1787.09 | 0.89 | 0.79 | 1.63 | 6.98 | 1.68 | 10020 | 8.3 | 22.94 | 33.751 | -118.0069 | 38.385 | 3.0D 48.7 deg left turn over bend
GWD 10030 | Girth Weld |  | 31892.59 | 1.98 | 0.28 | 42000 | ERW | 8.625 | 728 | [10 empty] | AGM 10 | 891.39 | AGM 11 | 1786.3 | 1.68 | 8.3 | 6.98 | 1.68 | 8.3 | 10030 | 22.94 | 22 | 33.751 | -118.0069 | 38.472
CSG 4 | Casing Start |  | 31894.57 | 6.32 | 0.28 | 42000 | ERW | 8.625 | 728 |  |  | 595.295 | [7 empty] | AGM 10 | 893.37 | AGM 11 | 1784.32 | 1.98 | 6.32 | 6.98 | 1.68 | 8.3 | 10030 | 22.94 | 22 | 33.751 | -118.0069 | 38.489 | Casing - Start
GWD 10040 | Girth Weld |  | 31900.9 | 22.94 | 0.28 | 42000 | ERW | 8.625 | 728 | [10 empty] | AGM 10 | 899.69 | AGM 11 | 1778 | 8.3 | 22.94 | 1.68 | 8.3 | 22.94 | 10040 | 22 | 1.5 | 33.751 | -118.0069 | 38.488
GWD 10050 | Girth Weld |  | 31923.83 | 20.35 | 0.28 | 42000 | ERW | 8.625 | 728 | [10 empty] | AGM 10 | 922.63 | AGM 11 | 1755.06 | 22.94 | 22 | 8.3 | 22.94 | 22 | 10050 | 1.5 | 5.05 | 33.7511 | -118.0069 | 38.547
CSG 4 | Casing End |  | 31944.18 | 1.65 | 0.28 | 42000 | ERW | 8.625 | 728 | [10 empty] | AGM 10 | 942.97 | AGM 11 | 1734.72 | 20.35 | 1.65 | 8.3 | 22.94 | 22 | 10050 | 1.5 | 5.05 | 33.7511 | -118.0069 | 38.549 | Casing - End
GWD 10060 | Girth Weld |  | 31945.83 | 0.69 | 0.28 | 42000 | ERW | 8.625 | 728 | [10 empty] | AGM 10 | 944.63 | AGM 11 | 1733.06 | 22 | 1.5 | 22.94 | 22 | 1.5 | 10060 | 5.05 | 1.53 | 33.7511 | -118.0069 | 38.553
BND 84 | Bend |  | 31946.53 | 0.81 | 0.28 | 42000 | ERW | 8.625 | 728 |  |  | 24.755 | [7 empty] | AGM 10 | 945.32 | AGM 11 | 1732.37 | 0.69 | 0.81 | 22.94 | 22 | 1.5 | 10060 | 5.05 | 1.53 | 33.7511 | -118.0069 | 38.486 | 3.0D 48.7 deg left turn over bend
GWD 10070 | Girth Weld |  | 31947.33 | 5.05 | 0.28 | 42000 | ERW | 8.625 | 728 | [10 empty] | AGM 10 | 946.13 | AGM 11 | 1731.57 | 1.5 | 5.05 | 22 | 1.5 | 5.05 | 10070 | 1.53 | 44.12 | 33.7511 | -118.0069 | 38.333
GWD 10080 | Girth Weld |  | 31952.38 | 0.84 | 0.28 | 42000 | ERW | 8.625 | 728 | [10 empty] | AGM 10 | 951.17 | AGM 11 | 1726.52 | 5.05 | 1.53 | 1.5 | 5.05 | 1.53 | 10080 | 44.12 | 26.13 | 33.7511 | -118.0069 | 37.084
BND 85 | Bend |  | 31953.22 | 0.69 | 0.28 | 42000 | ERW | 8.625 | 728 |  |  | 25.946 | [7 empty] | AGM 10 | 952.02 | AGM 11 | 1725.68 | 0.84 | 0.69 | 1.5 | 5.05 | 1.53 | 10080 | 44.12 | 26.13 | 33.7511 | -118.0069 | 36.921 | 3.0D 47.8 deg right turn sag bend
GWD 10090 | Girth Weld |  | 31953.91 | 44.12 | 0.28 | 42000 | ERW | 8.625 | 728 | [10 empty] | AGM 10 | 952.71 | AGM 11 | 1724.98 | 1.53 | 44.12 | 5.05 | 1.53 | 44.12 | 10090 | 26.13 | 35.37 | 33.7511 | -118.0069 | 36.854
GWD 10100 | Girth Weld |  | 31998.03 | 26.13 | 0.28 | 42000 | ERW | 8.625 | 728 | [10 empty] | AGM 10 | 996.82 | AGM 11 | 1680.87 | 44.12 | 26.13 | 1.53 | 44.12 | 26.13 | 10100 | 35.37 | 42.67 | 33.7513 | -118.0069 | 36.872
GWD 10110 | Girth Weld |  | 32024.16 | 35.37 | 0.28 | 42000 | ERW | 8.625 | 728 | [10 empty] | AGM 10 | 1022.96 | AGM 11 | 1654.73 | 26.13 | 35.37 | 44.12 | 26.13 | 35.37 | 10110 | 42.67 | 38.43 | 33.7513 | -118.0069 | 36.39
GWD 10120 | Girth Weld |  | 32059.53 | 42.67 | 0.28 | 42000 | ERW | 8.625 | 728 | [10 empty] | AGM 10 | 1058.32 | AGM 11 | 1619.37 | 35.37 | 42.67 | 26.13 | 35.37 | 42.67 | 10120 | 38.43 | 42.31 | 33.7514 | -118.0069 | 36.778
GWD 10130 | Girth Weld |  | 32102.2 | 38.43 | 0.28 | 42000 | ERW | 8.625 | 728 | [10 empty] | AGM 10 | 1100.99 | AGM 11 | 1576.7 | 42.67 | 38.43 | 35.37 | 42.67 | 38.43 | 10130 | 42.31 | 10.04 | 33.7515 | -118.0069 | 37.698
GWD 10140 | Girth Weld |  | 32140.63 | 42.31 | 0.28 | 42000 | ERW | 8.625 | 728 | [10 empty] | AGM 10 | 1139.42 | AGM 11 | 1538.27 | 38.43 | 42.31 | 42.67 | 38.43 | 42.31 | 10140 | 10.04 | 36 | 33.7516 | -118.0069 | 37.652
GWD 10150 | Girth Weld |  | 32182.94 | 10.04 | 0.28 | 42000 | ERW | 8.625 | 728 | [10 empty] | AGM 10 | 1181.74 | AGM 11 | 1495.95 | 42.31 | 10.04 | 38.43 | 42.31 | 10.04 | 10150 | 36 | 46.16 | 33.7518 | -118.0069 | 37.627
GWD 10160 | Girth Weld |  | 32192.98 | 36 | 0.28 | 42000 | ERW | 8.625 | 728 | [10 empty] | AGM 10 | 1191.78 | AGM 11 | 1485.91 | 10.04 | 36 | 42.31 | 10.04 | 36 | 10160 | 46.16 | 46.89 | 33.7518 | -118.0069 | 37.633
GWD 10170 | Girth Weld |  | 32228.99 | 46.16 | 0.28 | 42000 | ERW | 8.625 | 728 | [10 empty] | AGM 10 | 1227.78 | AGM 11 | 1449.91 | 36 | 46.16 | 10.04 | 36 | 46.16 | 10170 | 46.89 | 0.94 | 33.7519 | -118.0069 | 37.648
GWD 10180 | Girth Weld |  | 32275.15 | 46.89 | 0.28 | 42000 | ERW | 8.625 | 728 | [10 empty] | AGM 10 | 1273.94 | AGM 11 | 1403.75 | 46.16 | 46.89 | 36 | 46.16 | 46.89 | 10180 | 0.94 | 24.54 | 33.752 | -118.0069 | 37.948
GWD 10190 | Girth Weld |  | 32322.04 | 0.37 | 0.28 | 42000 | ERW | 8.625 | 728 | [10 empty] | AGM 10 | 1320.83 | AGM 11 | 1356.86 | 46.89 | 0.94 | 46.16 | 46.89 | 0.94 | 10190 | 24.54 | 7.42 | 33.7521 | -118.0069 | 38.352
BND 86 | Bend |  | 32322.41 | 0.57 | 0.28 | 42000 | ERW | 8.625 | 728 |  |  | 11.299 | [7 empty] | AGM 10 | 1321.2 | AGM 11 | 1356.49 | 0.37 | 0.57 | 46.16 | 46.89 | 0.94 | 10190 | 24.54 | 7.42 | 33.7521 | -118.0069 | 38.349 | 3.0D 28.7 deg left turn over bend
GWD 10200 | Girth Weld |  | 32322.98 | 24.54 | 0.28 | 42000 | ERW | 8.625 | 728 | [10 empty] | AGM 10 | 1321.77 | AGM 11 | 1355.92 | 0.94 | 24.54 | 46.89 | 0.94 | 24.54 | 10200 | 7.42 | 7.34 | 33.7521 | -118.0069 | 38.342
GWD 10210 | Girth Weld |  | 32347.52 | 7.42 | 0.28 | 42000 | ERW | 8.625 | 728 | [10 empty] | AGM 10 | 1346.31 | AGM 11 | 1331.38 | 24.54 | 7.42 | 0.94 | 24.54 | 7.42 | 10210 | 7.34 | 48.03 | 33.7522 | -118.007 | 38.092
GWD 10220 | Girth Weld |  | 32354.95 | 7.34 | 0.28 | 42000 | ERW | 8.625 | 728 | [10 empty] | AGM 10 | 1353.74 | AGM 11 | 1323.95 | 7.42 | 7.34 | 24.54 | 7.42 | 7.34 | 10220 | 48.03 | 43.69 | 33.7522 | -118.007 | 38.108
GWD 10230 | Girth Weld |  | 32362.29 | 28.9 | 0.28 | 42000 | ERW | 8.625 | 728 | [10 empty] | AGM 10 | 1361.08 | AGM 11 | 1316.61 | 7.34 | 48.03 | 7.42 | 7.34 | 48.03 | 10230 | 43.69 | 10.33 | 33.7522 | -118.007 | 38.145
CSG 5 | Casing Start |  | 32391.19 | 19.12 | 0.28 | 42000 | ERW | 8.625 | 728 |  |  | 838.273 | [7 empty] | AGM 10 | 1389.98 | AGM 11 | 1287.71 | 28.9 | 19.12 | 7.42 | 7.34 | 48.03 | 10230 | 43.69 | 10.33 | 33.7523 | -118.007 | 37.329 | Casing - Start
GWD 10240 | Girth Weld |  | 32410.31 | 43.69 | 0.28 | 42000 | ERW | 8.625 | 728 | [10 empty] | AGM 10 | 1409.11 | AGM 11 | 1268.58 | 48.03 | 43.69 | 7.34 | 48.03 | 43.69 | 10240 | 10.33 | 23.92 | 33.7524 | -118.0071 | 37.822
GWD 10250 | Girth Weld |  | 32454 | 7.04 | 0.28 | 42000 | ERW | 8.625 | 728 | [10 empty] | AGM 10 | 1452.8 | AGM 11 | 1224.89 | 43.69 | 10.33 | 48.03 | 43.69 | 10.33 | 10250 | 23.92 | 34.2 | 33.7525 | -118.0071 | 38.485
CSG 5 | Casing End |  | 32461.05 | 3.28 | 0.28 | 42000 | ERW | 8.625 | 728 | [10 empty] | AGM 10 | 1459.84 | AGM 11 | 1217.85 | 7.04 | 3.28 | 48.03 | 43.69 | 10.33 | 10250 | 23.92 | 34.2 | 33.7525 | -118.0071 | 38.541 | Casing - End
GWD 10260 | Girth Weld |  | 32464.33 | 11.68 | 0.28 | 42000 | ERW | 8.625 | 728 | [10 empty] | AGM 10 | 1463.12 | AGM 11 | 1214.57 | 10.33 | 23.92 | 43.69 | 10.33 | 23.92 | 10260 | 34.2 | 47.73 | 33.7525 | -118.0071 | 38.569
BND 87 | Bend |  | 32476.01 | 12.25 | 0.28 | 42000 | ERW | 8.625 | 728 |  |  | 57.008 | [7 empty] | AGM 10 | 1474.8 | AGM 11 | 1202.89 | 11.68 | 12.25 | 43.69 | 10.33 | 23.92 | 10260 | 34.2 | 47.73 | 33.7525 | -118.0072 | 38.76 | 13.3D 24.8 deg right turn bend
GWD 10270 | Girth Weld |  | 32488.25 | 34.2 | 0.28 | 42000 | ERW | 8.625 | 728 | [10 empty] | AGM 10 | 1487.05 | AGM 11 | 1190.64 | 23.92 | 34.2 | 10.33 | 23.92 | 34.2 | 10270 | 47.73 | 47.79 | 33.7526 | -118.0072 | 38.765
GWD 10280 | Girth Weld |  | 32522.46 | 47.73 | 0.28 | 42000 | ERW | 8.625 | 728 | [10 empty] | AGM 10 | 1521.25 | AGM 11 | 1156.44 | 34.2 | 47.73 | 23.92 | 34.2 | 47.73 | 10280 | 47.79 | 47.01 | 33.7526 | -118.0072 | 38.54
GWD 10290 | Girth Weld |  | 32570.19 | 47.79 | 0.28 | 42000 | ERW | 8.625 | 728 | [10 empty] | AGM 10 | 1568.99 | AGM 11 | 1108.7 | 47.73 | 47.79 | 34.2 | 47.73 | 47.79 | 10290 | 47.01 | 39.15 | 33.7528 | -118.0072 | 38.946
GWD 10300 | Girth Weld |  | 32617.99 | 47.01 | 0.28 | 42000 | ERW | 8.625 | 728 | [10 empty] | AGM 10 | 1616.78 | AGM 11 | 1060.91 | 47.79 | 47.01 | 47.73 | 47.79 | 47.01 | 10300 | 39.15 | 46.06 | 33.7529 | -118.0072 | 39.033
GWD 10310 | Girth Weld |  | 32665 | 39.15 | 0.28 | 42000 | ERW | 8.625 | 728 | [10 empty] | AGM 10 | 1663.79 | AGM 11 | 1013.9 | 47.01 | 39.15 | 47.79 | 47.01 | 39.15 | 10310 | 46.06 | 47.88 | 33.753 | -118.0072 | 39.382
GWD 10320 | Girth Weld |  | 32704.14 | 46.06 | 0.28 | 42000 | ERW | 8.625 | 728 | [10 empty] | AGM 10 | 1702.94 | AGM 11 | 974.75 | 39.15 | 46.06 | 47.01 | 39.15 | 46.06 | 10320 | 47.88 | 48.65 | 33.7531 | -118.0072 | 39.571
GWD 10330 | Girth Weld |  | 32750.21 | 47.88 | 0.28 | 42000 | ERW | 8.625 | 728 | [10 empty] | AGM 10 | 1749 | AGM 11 | 928.69 | 46.06 | 47.88 | 39.15 | 46.06 | 47.88 | 10330 | 48.65 | 48.18 | 33.7533 | -118.0072 | 39.304
GWD 10340 | Girth Weld |  | 32798.09 | 48.65 | 0.28 | 42000 | ERW | 8.625 | 728 | [10 empty] | AGM 10 | 1796.88 | AGM 11 | 880.81 | 47.88 | 48.65 | 46.06 | 47.88 | 48.65 | 10340 | 48.18 | 46.83 | 33.7534 | -118.0072 | 39.282
GWD 10350 | Girth Weld |  | 32846.73 | 48.18 | 0.28 | 42000 | ERW | 8.625 | 728 | [10 empty] | AGM 10 | 1845.53 | AGM 11 | 832.16 | 48.65 | 48.18 | 47.88 | 48.65 | 48.18 | 10350 | 46.83 | 47.96 | 33.7535 | -118.0072 | 39.204
GWD 10360 | Girth Weld |  | 32894.92 | 46.83 | 0.28 | 42000 | ERW | 8.625 | 728 | [10 empty] | AGM 10 | 1893.71 | AGM 11 | 783.98 | 48.18 | 46.83 | 48.65 | 48.18 | 46.83 | 10360 | 47.96 | 47.81 | 33.7537 | -118.0072 | 39.52
GWD 10370 | Girth Weld |  | 32941.75 | 47.96 | 0.28 | 42000 | ERW | 8.625 | 728 | [10 empty] | AGM 10 | 1940.54 | AGM 11 | 737.15 | 46.83 | 47.96 | 48.18 | 46.83 | 47.96 | 10370 | 47.81 | 46.14 | 33.7538 | -118.0072 | 39.003
GWD 10380 | Girth Weld |  | 32989.7 | 47.81 | 0.28 | 42000 | ERW | 8.625 | 728 | [10 empty] | AGM 10 | 1988.5 | AGM 11 | 689.19 | 47.96 | 47.81 | 46.83 | 47.96 | 47.81 | 10380 | 46.14 | 48.4 | 33.7539 | -118.0072 | 39.058
GWD 10390 | Girth Weld |  | 33037.51 | 46.14 | 0.28 | 42000 | ERW | 8.625 | 728 | [10 empty] | AGM 10 | 2036.31 | AGM 11 | 641.38 | 47.81 | 46.14 | 47.96 | 47.81 | 46.14 | 10390 | 48.4 | 48.46 | 33.7541 | -118.0072 | 38.987
GWD 10400 | Girth Weld |  | 33083.65 | 48.4 | 0.28 | 42000 | ERW | 8.625 | 728 | [10 empty] | AGM 10 | 2082.44 | AGM 11 | 595.25 | 46.14 | 48.4 | 47.81 | 46.14 | 48.4 | 10400 | 48.46 | 48.49 | 33.7542 | -118.0072 | 38.788
GWD 10410 | Girth Weld |  | 33132.05 | 48.46 | 0.28 | 42000 | ERW | 8.625 | 728 | [10 empty] | AGM 10 | 2130.84 | AGM 11 | 546.85 | 48.4 | 48.46 | 46.14 | 48.4 | 48.46 | 10410 | 48.49 | 46.25 | 33.7543 | -118.0072 | 38.941
GWD 10420 | Girth Weld |  | 33180.51 | 48.49 | 0.28 | 42000 | ERW | 8.625 | 728 | [10 empty] | AGM 10 | 2179.3 | AGM 11 | 498.39 | 48.46 | 48.49 | 48.4 | 48.46 | 48.49 | 10420 | 46.25 | 37.61 | 33.7545 | -118.0072 | 38.583
GWD 10430 | Girth Weld |  | 33229 | 46.25 | 0.28 | 42000 | ERW | 8.625 | 728 | [10 empty] | AGM 10 | 2227.79 | AGM 11 | 449.9 | 48.49 | 46.25 | 48.46 | 48.49 | 46.25 | 10430 | 37.61 | 49.25 | 33.7546 | -118.0072 | 38.896
GWD 10440 | Girth Weld |  | 33275.25 | 37.61 | 0.28 | 42000 | ERW | 8.625 | 728 | [10 empty] | AGM 10 | 2274.04 | AGM 11 | 403.65 | 46.25 | 37.61 | 48.49 | 46.25 | 37.61 | 10440 | 49.25 | 48.42 | 33.7547 | -118.0072 | 39.018
GWD 10450 | Girth Weld |  | 33312.86 | 49.25 | 0.28 | 42000 | ERW | 8.625 | 728 | [10 empty] | AGM 10 | 2311.65 | AGM 11 | 366.04 | 37.61 | 49.25 | 46.25 | 37.61 | 49.25 | 10450 | 48.42 | 48.48 | 33.7548 | -118.0072 | 39.031
GWD 10460 | Girth Weld |  | 33362.11 | 48.42 | 0.28 | 42000 | ERW | 8.625 | 728 | [10 empty] | AGM 10 | 2360.9 | AGM 11 | 316.79 | 49.25 | 48.42 | 37.61 | 49.25 | 48.42 | 10460 | 48.48 | 48.02 | 33.755 | -118.0072 | 39.441
GWD 10470 | Girth Weld |  | 33410.53 | 48.48 | 0.28 | 42000 | ERW | 8.625 | 728 | [10 empty] | AGM 10 | 2409.32 | AGM 11 | 268.37 | 48.42 | 48.48 | 49.25 | 48.42 | 48.48 | 10470 | 48.02 | 47.36 | 33.7551 | -118.0072 | 39.7
GWD 10480 | Girth Weld |  | 33459.01 | 48.02 | 0.28 | 42000 | ERW | 8.625 | 728 | [10 empty] | AGM 10 | 2457.8 | AGM 11 | 219.89 | 48.48 | 48.02 | 48.42 | 48.48 | 48.02 | 10480 | 47.36 | 14.92 | 33.7552 | -118.0072 | 40.006
GWD 10490 | Girth Weld |  | 33507.02 | 47.36 | 0.28 | 42000 | ERW | 8.625 | 728 | [10 empty] | AGM 10 | 2505.82 | AGM 11 | 171.87 | 48.02 | 47.36 | 48.48 | 48.02 | 47.36 | 10490 | 14.92 | 42.1 | 33.7554 | -118.0072 | 39.397
GWD 10500 | Girth Weld |  | 33554.38 | 14.92 | 0.28 | 42000 | ERW | 8.625 | 728 | [10 empty] | AGM 10 | 2553.18 | AGM 11 | 124.51 | 47.36 | 14.92 | 48.02 | 47.36 | 14.92 | 10500 | 42.1 | 43.97 | 33.7555 | -118.0072 | 39.382
GWD 10510 | Girth Weld |  | 33569.31 | 42.1 | 0.28 | 42000 | ERW | 8.625 | 728 | [10 empty] | AGM 10 | 2568.1 | AGM 11 | 109.59 | 14.92 | 42.1 | 47.36 | 14.92 | 42.1 | 10510 | 43.97 | 1.23 | 33.7555 | -118.0072 | 39.151
GWD 10520 | Girth Weld |  | 33611.4 | 43.97 | 0.28 | 42000 | ERW | 8.625 | 728 | [10 empty] | AGM 10 | 2610.2 | AGM 11 | 67.49 | 42.1 | 43.97 | 14.92 | 42.1 | 43.97 | 10520 | 1.23 | 7.73 | 33.7556 | -118.0072 | 38.396
GWD 10530 | Girth Weld |  | 33655.38 | 1.23 | 0.28 | 42000 | ERW | 8.625 | 728 | [10 empty] | AGM 10 | 2654.17 | AGM 11 | 23.52 | 43.97 | 1.23 | 42.1 | 43.97 | 1.23 | 10530 | 7.73 | 12.3 | 33.7558 | -118.0072 | 37.818
GWD 10540 | Girth Weld |  | 33656.6 | 7.73 | 0.28 | 42000 | ERW | 8.625 | 728 | [10 empty] | AGM 10 | 2655.4 | AGM 11 | 22.29 | 1.23 | 7.73 | 43.97 | 1.23 | 7.73 | 10540 | 12.3 | 8.93 | 33.7558 | -118.0072 | 37.842
GWD 10550 | Girth Weld |  | 33664.33 | 12.3 | 0.28 | 42000 | ERW | 8.625 | 728 | [10 empty] | AGM 10 | 2663.12 | AGM 11 | 14.57 | 7.73 | 12.3 | 1.23 | 7.73 | 12.3 | 10550 | 8.93 | 40.45 | 33.7558 | -118.0072 | 37.905
GWD 10560 | Girth Weld |  | 33676.63 | 2.27 | 0.28 | 42000 | ERW | 8.625 | 728 | [10 empty] | AGM 10 | 2675.42 | AGM 11 | 2.27 | 12.3 | 8.93 | 7.73 | 12.3 | 8.93 | 10560 | 40.45 | 42.94 | 33.7558 | -118.0072 | 37.978
MRK 9 | Marker |  | 33678.9 | 6.66 | 0.28 | 42000 | ERW | 8.625 | 728 |  |  |  |  | 11:37 | [5 empty] | AGM 10 | 2677.69 | AGM 12 | 3094.16 | 2.27 | 6.66 | 7.73 | 12.3 | 8.93 | 10560 | 40.45 | 42.94 | 33.7558 | -118.0072 | 37.973 | AGM 11 6' East of Curb - Located in Goldenwest St
GWD 10570 | Girth Weld |  | 33685.56 | 40.45 | 0.28 | 42000 | ERW | 8.625 | 728 | [10 empty] | AGM 11 | 6.66 | AGM 12 | 3087.5 | 8.93 | 40.45 | 12.3 | 8.93 | 40.45 | 10570 | 42.94 | 41.9 | 33.7558 | -118.0072 | 37.961
GWD 10580 | Girth Weld |  | 33726.01 | 42.94 | 0.28 | 42000 | ERW | 8.625 | 728 | [10 empty] | AGM 11 | 47.11 | AGM 12 | 3047.05 | 40.45 | 42.94 | 8.93 | 40.45 | 42.94 | 10580 | 41.9 | 42.39 | 33.756 | -118.0072 | 38.072
GWD 10590 | Girth Weld |  | 33768.95 | 41.9 | 0.28 | 42000 | ERW | 8.625 | 728 | [10 empty] | AGM 11 | 90.05 | AGM 12 | 3004.11 | 42.94 | 41.9 | 40.45 | 42.94 | 41.9 | 10590 | 42.39 | 29.43 | 33.7561 | -118.0072 | 38.538
GWD 10600 | Girth Weld |  | 33810.85 | 42.39 | 0.28 | 42000 | ERW | 8.625 | 728 | [10 empty] | AGM 11 | 131.95 | AGM 12 | 2962.21 | 41.9 | 42.39 | 42.94 | 41.9 | 42.39 | 10600 | 29.43 | 23.98 | 33.7562 | -118.0072 | 38.374
GWD 10610 | Girth Weld |  | 33853.24 | 29.43 | 0.28 | 42000 | ERW | 8.625 | 728 | [10 empty] | AGM 11 | 174.34 | AGM 12 | 2919.82 | 42.39 | 29.43 | 41.9 | 42.39 | 29.43 | 10610 | 23.98 | 43 | 33.7563 | -118.0072 | 38.786
GWD 10620 | Girth Weld |  | 33882.67 | 23.98 | 0.28 | 42000 | ERW | 8.625 | 728 | [10 empty] | AGM 11 | 203.77 | AGM 12 | 2890.39 | 29.43 | 23.98 | 42.39 | 29.43 | 23.98 | 10620 | 43 | 42.84 | 33.7564 | -118.0072 | 38.78
GWD 10630 | Girth Weld |  | 33906.66 | 43 | 0.28 | 42000 | ERW | 8.625 | 728 | [10 empty] | AGM 11 | 227.76 | AGM 12 | 2866.4 | 23.98 | 43 | 29.43 | 23.98 | 43 | 10630 | 42.84 | 42.93 | 33.7564 | -118.0072 | 38.891
GWD 10640 | Girth Weld |  | 33949.65 | 42.84 | 0.28 | 42000 | ERW | 8.625 | 728 | [10 empty] | AGM 11 | 270.76 | AGM 12 | 2823.4 | 43 | 42.84 | 23.98 | 43 | 42.84 | 10640 | 42.93 | 42.47 | 33.7566 | -118.0072 | 38.775
GWD 10650 | Girth Weld |  | 33992.49 | 42.93 | 0.28 | 42000 | ERW | 8.625 | 728 | [10 empty] | AGM 11 | 313.59 | AGM 12 | 2780.57 | 42.84 | 42.93 | 43 | 42.84 | 42.93 | 10650 | 42.47 | 41.87 | 33.7567 | -118.0072 | 38.906
GWD 10660 | Girth Weld |  | 34035.42 | 42.47 | 0.28 | 42000 | ERW | 8.625 | 728 | [10 empty] | AGM 11 | 356.53 | AGM 12 | 2737.63 | 42.93 | 42.47 | 42.84 | 42.93 | 42.47 | 10660 | 41.87 | 41.74 | 33.7568 | -118.0072 | 38.851
GWD 10670 | Girth Weld |  | 34077.9 | 41.87 | 0.28 | 42000 | ERW | 8.625 | 728 | [10 empty] | AGM 11 | 399 | AGM 12 | 2695.16 | 42.47 | 41.87 | 42.93 | 42.47 | 41.87 | 10670 | 41.74 | 43.3 | 33.7569 | -118.0072 | 38.914
GWD 10680 | Girth Weld |  | 34119.76 | 41.74 | 0.28 | 42000 | ERW | 8.625 | 728 | [10 empty] | AGM 11 | 440.87 | AGM 12 | 2653.29 | 41.87 | 41.74 | 42.47 | 41.87 | 41.74 | 10680 | 43.3 | 12.35 | 33.757 | -118.0072 | 38.919
GWD 10690 | Girth Weld |  | 34161.5 | 43.3 | 0.28 | 42000 | ERW | 8.625 | 728 | [10 empty] | AGM 11 | 482.6 | AGM 12 | 2611.56 | 41.74 | 43.3 | 41.87 | 41.74 | 43.3 | 10690 | 12.35 | 5.16 | 33.7571 | -118.0072 | 39.186
GWD 10700 | Girth Weld |  | 34204.8 | 12.35 | 0.28 | 42000 | ERW | 8.625 | 728 | [10 empty] | AGM 11 | 525.91 | AGM 12 | 2568.25 | 43.3 | 12.35 | 41.74 | 43.3 | 12.35 | 10700 | 5.16 | 30.66 | 33.7573 | -118.0072 | 39.153
GWD 10710 | Girth Weld |  | 34217.15 | 5.16 | 0.28 | 42000 | ERW | 8.625 | 728 | [10 empty] | AGM 11 | 538.26 | AGM 12 | 2555.9 | 12.35 | 5.16 | 43.3 | 12.35 | 5.16 | 10710 | 30.66 | 35.94 | 33.7573 | -118.0072 | 38.74
GWD 10720 | Girth Weld |  | 34222.32 | 30.66 | 0.28 | 42000 | ERW | 8.625 | 728 | [10 empty] | AGM 11 | 543.42 | AGM 12 | 2550.74 | 5.16 | 30.66 | 12.35 | 5.16 | 30.66 | 10720 | 35.94 | 46.46 | 33.7573 | -118.0072 | 38.476
GWD 10730 | Girth Weld |  | 34252.98 | 35.94 | 0.28 | 42000 | ERW | 8.625 | 728 | [10 empty] | AGM 11 | 574.08 | AGM 12 | 2520.08 | 30.66 | 35.94 | 5.16 | 30.66 | 35.94 | 10730 | 46.46 | 33.45 | 33.7574 | -118.0072 | 37.251
GWD 10740 | Girth Weld |  | 34288.92 | 46.46 | 0.28 | 42000 | ERW | 8.625 | 728 | [10 empty] | AGM 11 | 610.02 | AGM 12 | 2484.14 | 35.94 | 46.46 | 30.66 | 35.94 | 46.46 | 10740 | 33.45 | 45.63 | 33.7575 | -118.0072 | 37.11
GWD 10750 | Girth Weld |  | 34335.37 | 33.45 | 0.28 | 42000 | ERW | 8.625 | 728 | [10 empty] | AGM 11 | 656.48 | AGM 12 | 2437.69 | 46.46 | 33.45 | 35.94 | 46.46 | 33.45 | 10750 | 45.63 | 25.27 | 33.7576 | -118.0072 | 37.438
GWD 10760 | Girth Weld |  | 34368.82 | 45.63 | 0.28 | 42000 | ERW | 8.625 | 728 | [10 empty] | AGM 11 | 689.93 | AGM 12 | 2404.23 | 33.45 | 45.63 | 46.46 | 33.45 | 45.63 | 10760 | 25.27 | 44.84 | 33.7577 | -118.0072 | 37.993
GWD 10770 | Girth Weld |  | 34414.46 | 25.27 | 0.28 | 42000 | ERW | 8.625 | 728 | [10 empty] | AGM 11 | 735.56 | AGM 12 | 2358.6 | 45.63 | 25.27 | 33.45 | 45.63 | 25.27 | 10770 | 44.84 | 46.27 | 33.7578 | -118.0072 | 38.403
GWD 10780 | Girth Weld |  | 34439.73 | 44.84 | 0.28 | 42000 | ERW | 8.625 | 728 | [10 empty] | AGM 11 | 760.83 | AGM 12 | 2333.33 | 25.27 | 44.84 | 45.63 | 25.27 | 44.84 | 10780 | 46.27 | 44.21 | 33.7579 | -118.0072 | 37.967
GWD 10790 | Girth Weld |  | 34484.56 | 46.27 | 0.28 | 42000 | ERW | 8.625 | 728 | [10 empty] | AGM 11 | 805.66 | AGM 12 | 2288.5 | 44.84 | 46.27 | 25.27 | 44.84 | 46.27 | 10790 | 44.21 | 43.21 | 33.758 | -118.0072 | 38.26
GWD 10800 | Girth Weld |  | 34530.83 | 44.21 | 0.28 | 42000 | ERW | 8.625 | 728 | [10 empty] | AGM 11 | 851.93 | AGM 12 | 2242.23 | 46.27 | 44.21 | 44.84 | 46.27 | 44.21 | 10800 | 43.21 | 44.53 | 33.7582 | -118.0072 | 38.161
GWD 10810 | Girth Weld |  | 34575.04 | 43.21 | 0.28 | 42000 | ERW | 8.625 | 728 | [10 empty] | AGM 11 | 896.14 | AGM 12 | 2198.02 | 44.21 | 43.21 | 46.27 | 44.21 | 43.21 | 10810 | 44.53 | 43.05 | 33.7583 | -118.0072 | 38.048
GWD 10820 | Girth Weld |  | 34618.25 | 44.53 | 0.28 | 42000 | ERW | 8.625 | 728 | [10 empty] | AGM 11 | 939.35 | AGM 12 | 2154.81 | 43.21 | 44.53 | 44.21 | 43.21 | 44.53 | 10820 | 43.05 | 23.07 | 33.7584 | -118.0072 | 38.122
GWD 10830 | Girth Weld |  | 34662.78 | 43.05 | 0.28 | 42000 | ERW | 8.625 | 728 | [10 empty] | AGM 11 | 983.88 | AGM 12 | 2110.28 | 44.53 | 43.05 | 43.21 | 44.53 | 43.05 | 10830 | 23.07 | 36.88 | 33.7585 | -118.0072 | 39.271
GWD 10840 | Girth Weld |  | 34705.83 | 23.07 | 0.28 | 42000 | ERW | 8.625 | 728 | [10 empty] | AGM 11 | 1026.93 | AGM 12 | 2067.23 | 43.05 | 23.07 | 44.53 | 43.05 | 23.07 | 10840 | 36.88 | 37.55 | 33.7586 | -118.0072 | 39.99
GWD 10850 | Girth Weld |  | 34728.9 | 36.88 | 0.28 | 42000 | ERW | 8.625 | 728 | [10 empty] | AGM 11 | 1050 | AGM 12 | 2044.16 | 23.07 | 36.88 | 43.05 | 23.07 | 36.88 | 10850 | 37.55 | 37.41 | 33.7587 | -118.0072 | 39.911
GWD 10860 | Girth Weld |  | 34765.77 | 37.55 | 0.28 | 42000 | ERW | 8.625 | 728 | [10 empty] | AGM 11 | 1086.88 | AGM 12 | 2007.28 | 36.88 | 37.55 | 23.07 | 36.88 | 37.55 | 10860 | 37.41 | 38.34 | 33.7588 | -118.0072 | 39.771
GWD 10870 | Girth Weld |  | 34803.33 | 37.41 | 0.28 | 42000 | ERW | 8.625 | 728 | [10 empty] | AGM 11 | 1124.43 | AGM 12 | 1969.73 | 37.55 | 37.41 | 36.88 | 37.55 | 37.41 | 10870 | 38.34 | 43.21 | 33.7589 | -118.0072 | 39.265
GWD 10880 | Girth Weld |  | 34840.74 | 3.55 | 0.28 | 42000 | ERW | 8.625 | 728 | [10 empty] | AGM 11 | 1161.84 | AGM 12 | 1932.32 | 37.41 | 38.34 | 37.55 | 37.41 | 38.34 | 10880 | 43.21 | 43.47 | 33.759 | -118.0073 | 39.372
CSG 6 | Casing Start |  | 34844.29 | 34.78 | 0.28 | 42000 | ERW | 8.625 | 728 |  |  | 751.429 | [7 empty] | AGM 11 | 1165.39 | AGM 12 | 1928.77 | 3.55 | 34.78 | 37.55 | 37.41 | 38.34 | 10880 | 43.21 | 43.47 | 33.759 | -118.0073 | 39.404 | Casing - Start
GWD 10890 | Girth Weld |  | 34879.08 | 27.83 | 0.28 | 42000 | ERW | 8.625 | 728 | [10 empty] | AGM 11 | 1200.18 | AGM 12 | 1893.98 | 38.34 | 43.21 | 37.41 | 38.34 | 43.21 | 10890 | 43.47 | 42.85 | 33.7591 | -118.0073 | 39.971
CSG 6 | Casing End |  | 34906.91 | 15.37 | 0.28 | 42000 | ERW | 8.625 | 728 | [10 empty] | AGM 11 | 1228.01 | AGM 12 | 1866.15 | 27.83 | 15.37 | 37.41 | 38.34 | 43.21 | 10890 | 43.47 | 42.85 | 33.7592 | -118.0073 | 39.808 | Casing - End
GWD 10900 | Girth Weld |  | 34922.28 | 43.47 | 0.28 | 42000 | ERW | 8.625 | 728 | [10 empty] | AGM 11 | 1243.39 | AGM 12 | 1850.77 | 43.21 | 43.47 | 38.34 | 43.21 | 43.47 | 10900 | 42.85 | 42.49 | 33.7592 | -118.0073 | 39.74
GWD 10910 | Girth Weld |  | 34965.76 | 42.85 | 0.28 | 42000 | ERW | 8.625 | 728 | [10 empty] | AGM 11 | 1286.86 | AGM 12 | 1807.3 | 43.47 | 42.85 | 43.21 | 43.47 | 42.85 | 10910 | 42.49 | 42.76 | 33.7594 | -118.0073 | 40.228
GWD 10920 | Girth Weld |  | 35008.61 | 42.49 | 0.28 | 42000 | ERW | 8.625 | 728 | [10 empty] | AGM 11 | 1329.71 | AGM 12 | 1764.45 | 42.85 | 42.49 | 43.47 | 42.85 | 42.49 | 10920 | 42.76 | 9.91 | 33.7595 | -118.0073 | 40.546
GWD 10930 | Girth Weld |  | 35051.1 | 42.76 | 0.28 | 42000 | ERW | 8.625 | 728 | [10 empty] | AGM 11 | 1372.2 | AGM 12 | 1721.96 | 42.49 | 42.76 | 42.85 | 42.49 | 42.76 | 10930 | 9.91 | 34.69 | 33.7596 | -118.0073 | 40.527
GWD 10940 | Girth Weld |  | 35093.86 | 9.91 | 0.28 | 42000 | ERW | 8.625 | 728 | [10 empty] | AGM 11 | 1414.96 | AGM 12 | 1679.2 | 42.76 | 9.91 | 42.49 | 42.76 | 9.91 | 10940 | 34.69 | 35 | 33.7597 | -118.0073 | 40.547
GWD 10950 | Girth Weld |  | 35103.77 | 34.69 | 0.28 | 42000 | ERW | 8.625 | 728 | [10 empty] | AGM 11 | 1424.87 | AGM 12 | 1669.29 | 9.91 | 34.69 | 42.76 | 9.91 | 34.69 | 10950 | 35 | 20.76 | 33.7597 | -118.0073 | 40.453
GWD 10960 | Girth Weld |  | 35138.46 | 35 | 0.28 | 42000 | ERW | 8.625 | 728 | [10 empty] | AGM 11 | 1459.57 | AGM 12 | 1634.59 | 34.69 | 35 | 9.91 | 34.69 | 35 | 10960 | 20.76 | 36.14 | 33.7598 | -118.0073 | 40.313
GWD 10970 | Girth Weld |  | 35173.46 | 20.76 | 0.28 | 42000 | ERW | 8.625 | 728 | [10 empty] | AGM 11 | 1494.57 | AGM 12 | 1599.59 | 35 | 20.76 | 34.69 | 35 | 20.76 | 10970 | 36.14 | 36.96 | 33.7599 | -118.0073 | 40.594
GWD 10980 | Girth Weld |  | 35194.23 | 36.14 | 0.28 | 42000 | ERW | 8.625 | 728 | [10 empty] | AGM 11 | 1515.33 | AGM 12 | 1578.83 | 20.76 | 36.14 | 35 | 20.76 | 36.14 | 10980 | 36.96 | 36.56 | 33.76 | -118.0073 | 40.567
GWD 10990 | Girth Weld |  | 35230.37 | 36.96 | 0.28 | 42000 | ERW | 8.625 | 728 | [10 empty] | AGM 11 | 1551.47 | AGM 12 | 1542.69 | 36.14 | 36.96 | 20.76 | 36.14 | 36.96 | 10990 | 36.56 | 37.34 | 33.7601 | -118.0073 | 40.57
GWD 11000 | Girth Weld |  | 35267.33 | 36.56 | 0.28 | 42000 | ERW | 8.625 | 728 | [10 empty] | AGM 11 | 1588.43 | AGM 12 | 1505.73 | 36.96 | 36.56 | 36.14 | 36.96 | 36.56 | 11000 | 37.34 | 37.52 | 33.7602 | -118.0073 | 40.741
GWD 11010 | Girth Weld |  | 35303.89 | 37.34 | 0.28 | 42000 | ERW | 8.625 | 728 | [10 empty] | AGM 11 | 1624.99 | AGM 12 | 1469.17 | 36.56 | 37.34 | 36.96 | 36.56 | 37.34 | 11010 | 37.52 | 37.85 | 33.7603 | -118.0073 | 40.648
GWD 11020 | Girth Weld |  | 35341.23 | 37.52 | 0.28 | 42000 | ERW | 8.625 | 728 | [10 empty] | AGM 11 | 1662.33 | AGM 12 | 1431.83 | 37.34 | 37.52 | 36.56 | 37.34 | 37.52 | 11020 | 37.85 | 36.84 | 33.7604 | -118.0073 | 40.573
GWD 11030 | Girth Weld |  | 35378.75 | 37.85 | 0.28 | 42000 | ERW | 8.625 | 728 | [10 empty] | AGM 11 | 1699.85 | AGM 12 | 1394.31 | 37.52 | 37.85 | 37.34 | 37.52 | 37.85 | 11030 | 36.84 | 34.76 | 33.7605 | -118.0073 | 40.61
GWD 11040 | Girth Weld |  | 35416.59 | 36.84 | 0.28 | 42000 | ERW | 8.625 | 728 | [10 empty] | AGM 11 | 1737.7 | AGM 12 | 1356.46 | 37.85 | 36.84 | 37.52 | 37.85 | 36.84 | 11040 | 34.76 | 37.84 | 33.7606 | -118.0073 | 40.513
GWD 11050 | Girth Weld |  | 35453.44 | 34.76 | 0.28 | 42000 | ERW | 8.625 | 728 | [10 empty] | AGM 11 | 1774.54 | AGM 12 | 1319.62 | 36.84 | 34.76 | 37.85 | 36.84 | 34.76 | 11050 | 37.84 | 36.87 | 33.7607 | -118.0073 | 40.627
GWD 11060 | Girth Weld |  | 35488.2 | 37.84 | 0.28 | 42000 | ERW | 8.625 | 728 | [10 empty] | AGM 11 | 1809.3 | AGM 12 | 1284.86 | 34.76 | 37.84 | 36.84 | 34.76 | 37.84 | 11060 | 36.87 | 38.94 | 33.7608 | -118.0073 | 40.795
GWD 11070 | Girth Weld |  | 35526.04 | 36.87 | 0.28 | 42000 | ERW | 8.625 | 728 | [10 empty] | AGM 11 | 1847.14 | AGM 12 | 1247.02 | 37.84 | 36.87 | 34.76 | 37.84 | 36.87 | 11070 | 38.94 | 36.14 | 33.7609 | -118.0073 | 40.862
GWD 11080 | Girth Weld |  | 35562.91 | 38.94 | 0.28 | 42000 | ERW | 8.625 | 728 | [10 empty] | AGM 11 | 1884.01 | AGM 12 | 1210.15 | 36.87 | 38.94 | 37.84 | 36.87 | 38.94 | 11080 | 36.14 | 35.96 | 33.761 | -118.0073 | 40.719
GWD 11090 | Girth Weld |  | 35601.85 | 36.14 | 0.28 | 42000 | ERW | 8.625 | 728 | [10 empty] | AGM 11 | 1922.95 | AGM 12 | 1171.21 | 38.94 | 36.14 | 36.87 | 38.94 | 36.14 | 11090 | 35.96 | 24.84 | 33.7611 | -118.0073 | 41.113
GWD 11100 | Girth Weld |  | 35637.99 | 35.96 | 0.28 | 42000 | ERW | 8.625 | 728 | [10 empty] | AGM 11 | 1959.09 | AGM 12 | 1135.07 | 36.14 | 35.96 | 38.94 | 36.14 | 35.96 | 11100 | 24.84 | 36.16 | 33.7612 | -118.0073 | 41.528
GWD 11110 | Girth Weld |  | 35673.95 | 24.84 | 0.28 | 42000 | ERW | 8.625 | 728 | [10 empty] | AGM 11 | 1995.05 | AGM 12 | 1099.11 | 35.96 | 24.84 | 36.14 | 35.96 | 24.84 | 11110 | 36.16 | 38.51 | 33.7613 | -118.0073 | 41.516
GWD 11120 | Girth Weld |  | 35698.8 | 36.16 | 0.28 | 42000 | ERW | 8.625 | 728 | [10 empty] | AGM 11 | 2019.9 | AGM 12 | 1074.26 | 24.84 | 36.16 | 35.96 | 24.84 | 36.16 | 11120 | 38.51 | 37.48 | 33.7614 | -118.0073 | 41.563
GWD 11130 | Girth Weld |  | 35734.95 | 38.51 | 0.28 | 42000 | ERW | 8.625 | 728 | [10 empty] | AGM 11 | 2056.06 | AGM 12 | 1038.11 | 36.16 | 38.51 | 24.84 | 36.16 | 38.51 | 11130 | 37.48 | 37.58 | 33.7615 | -118.0073 | 41.392
GWD 11140 | Girth Weld |  | 35773.47 | 37.48 | 0.28 | 42000 | ERW | 8.625 | 728 | [10 empty] | AGM 11 | 2094.57 | AGM 12 | 999.59 | 38.51 | 37.48 | 36.16 | 38.51 | 37.48 | 11140 | 37.58 | 37.16 | 33.7616 | -118.0073 | 41.282
GWD 11150 | Girth Weld |  | 35810.95 | 37.58 | 0.28 | 42000 | ERW | 8.625 | 728 | [10 empty] | AGM 11 | 2132.05 | AGM 12 | 962.11 | 37.48 | 37.58 | 38.51 | 37.48 | 37.58 | 11150 | 37.16 | 23.44 | 33.7617 | -118.0073 | 41.192
GWD 11160 | Girth Weld |  | 35848.53 | 37.16 | 0.28 | 42000 | ERW | 8.625 | 728 | [10 empty] | AGM 11 | 2169.64 | AGM 12 | 924.52 | 37.58 | 37.16 | 37.48 | 37.58 | 37.16 | 11160 | 23.44 | 4.68 | 33.7618 | -118.0073 | 41.209
GWD 11170 | Girth Weld |  | 35885.69 | 23.44 | 0.28 | 42000 | ERW | 8.625 | 728 | [10 empty] | AGM 11 | 2206.79 | AGM 12 | 887.37 | 37.16 | 23.44 | 37.58 | 37.16 | 23.44 | 11170 | 4.68 | 5.39 | 33.7619 | -118.0073 | 41.426
GWD 11180 | Girth Weld |  | 35909.13 | 4.68 | 0.28 | 42000 | ERW | 8.625 | 728 | [10 empty] | AGM 11 | 2230.23 | AGM 12 | 863.93 | 23.44 | 4.68 | 37.16 | 23.44 | 4.68 | 11180 | 5.39 | 4.44 | 33.762 | -118.0073 | 41.378
GWD 11190 | Girth Weld |  | 35913.81 | 5.39 | 0.28 | 42000 | ERW | 8.625 | 728 | [10 empty] | AGM 11 | 2234.91 | AGM 12 | 859.25 | 4.68 | 5.39 | 23.44 | 4.68 | 5.39 | 11190 | 4.44 | 43.22 | 33.762 | -118.0073 | 41.325
GWD 11200 | Girth Weld |  | 35919.2 | 4.44 | 0.28 | 42000 | ERW | 8.625 | 728 | [10 empty] | AGM 11 | 2240.3 | AGM 12 | 853.86 | 5.39 | 4.44 | 4.68 | 5.39 | 4.44 | 11200 | 43.22 | 43.1 | 33.762 | -118.0073 | 41.258
GWD 11210 | Girth Weld |  | 35923.64 | 43.22 | 0.28 | 42000 | ERW | 8.625 | 728 | [10 empty] | AGM 11 | 2244.74 | AGM 12 | 849.42 | 4.44 | 43.22 | 5.39 | 4.44 | 43.22 | 11210 | 43.1 | 43.28 | 33.762 | -118.0073 | 41.195
GWD 11220 | Girth Weld |  | 35966.85 | 43.1 | 0.28 | 42000 | ERW | 8.625 | 728 | [10 empty] | AGM 11 | 2287.95 | AGM 12 | 806.21 | 43.22 | 43.1 | 4.44 | 43.22 | 43.1 | 11220 | 43.28 | 43.78 | 33.7621 | -118.0073 | 42.003
GWD 11230 | Girth Weld |  | 36009.95 | 43.28 | 0.28 | 42000 | ERW | 8.625 | 728 | [10 empty] | AGM 11 | 2331.05 | AGM 12 | 763.11 | 43.1 | 43.28 | 43.22 | 43.1 | 43.28 | 11230 | 43.78 | 3 | 33.7622 | -118.0073 | 42.216
GWD 11240 | Girth Weld |  | 36053.23 | 43.78 | 0.28 | 42000 | ERW | 8.625 | 728 | [10 empty] | AGM 11 | 2374.33 | AGM 12 | 719.83 | 43.28 | 43.78 | 43.1 | 43.28 | 43.78 | 11240 | 3 | 0.86 | 33.7623 | -118.0073 | 42.045
GWD 11250 | Girth Weld |  | 36097.01 | 3 | 0.28 | 42000 | ERW | 8.625 | 728 | [10 empty] | AGM 11 | 2418.12 | AGM 12 | 676.04 | 43.78 | 3 | 43.28 | 43.78 | 3 | 11250 | 0.86 | 18.24 | 33.7625 | -118.0073 | 41.768
GWD 11260 | Girth Weld |  | 36100.02 | 0.3 | 0.28 | 42000 | ERW | 8.625 | 728 | [10 empty] | AGM 11 | 2421.12 | AGM 12 | 673.04 | 3 | 0.86 | 43.78 | 3 | 0.86 | 11260 | 18.24 | 0.32 | 33.7625 | -118.0073 | 41.758
BND 88 | Bend |  | 36100.32 | 0.56 | 0.28 | 42000 | ERW | 8.625 | 728 |  |  | 10.394 | [7 empty] | AGM 11 | 2421.42 | AGM 12 | 672.74 | 0.3 | 0.56 | 43.78 | 3 | 0.86 | 11260 | 18.24 | 0.32 | 33.7625 | -118.0073 | 41.763 | 3.0D 26.1 deg right turn sag bend
GWD 11270 | Girth Weld |  | 36100.88 | 18.24 | 0.28 | 42000 | ERW | 8.625 | 728 | [10 empty] | AGM 11 | 2421.98 | AGM 12 | 672.18 | 0.86 | 18.24 | 3 | 0.86 | 18.24 | 11270 | 0.32 | 4.73 | 33.7625 | -118.0073 | 41.785
GWD 11280 | Girth Weld |  | 36119.12 | 0.32 | 0.28 | 42000 | ERW | 8.625 | 728 | [10 empty] | AGM 11 | 2440.22 | AGM 12 | 653.94 | 18.24 | 0.32 | 0.86 | 18.24 | 0.32 | 11280 | 4.73 | 0.36 | 33.7625 | -118.0073 | 42.825
GWD 11290 | Girth Weld |  | 36119.44 | 0.49 | 0.28 | 42000 | ERW | 8.625 | 728 | [10 empty] | AGM 11 | 2440.55 | AGM 12 | 653.62 | 0.32 | 4.73 | 18.24 | 0.32 | 4.73 | 11290 | 0.36 | 42.59 | 33.7625 | -118.0073 | 42.857
MOB 5 | Metal Object |  | 36119.93 | 4.24 | 0.28 | 42000 | ERW | 8.625 | 728 |  |  | 6.054 | 5.048 | 2:56 | [5 empty] | AGM 11 | 2441.03 | AGM 12 | 653.13 | 0.49 | 4.24 | 18.24 | 0.32 | 4.73 | 11290 | 0.36 | 42.59 | 33.7625 | -118.0073 | 42.911 | Close Metal Object
GWD 11300 | Girth Weld |  | 36124.17 | 0.28 | 0.28 | 42000 | ERW | 8.625 | 728 | [10 empty] | AGM 11 | 2445.27 | AGM 12 | 648.89 | 4.73 | 0.36 | 0.32 | 4.73 | 0.36 | 11300 | 42.59 | 42.26 | 33.7625 | -118.0073 | 43.414
BND 89 | Bend |  | 36124.45 | 0.08 | 0.28 | 42000 | ERW | 8.625 | 728 |  |  | 23.708 | [7 empty] | AGM 11 | 2445.55 | AGM 12 | 648.61 | 0.28 | 0.08 | 0.32 | 4.73 | 0.36 | 11300 | 42.59 | 42.26 | 33.7625 | -118.0073 | 43.437 | 18.6D 8.2 deg right turn over bend
GWD 11310 | Girth Weld |  | 36124.53 | 20.7 | 0.28 | 42000 | ERW | 8.625 | 728 | [10 empty] | AGM 11 | 2445.63 | AGM 12 | 648.53 | 0.36 | 42.59 | 4.73 | 0.36 | 42.59 | 11310 | 42.26 | 43.02 | 33.7625 | -118.0073 | 43.44
CSG 7 | Casing Start |  | 36145.23 | 21.89 | 0.28 | 42000 | ERW | 8.625 | 728 |  |  | 978.03 | [7 empty] | AGM 11 | 2466.33 | AGM 12 | 627.83 | 20.7 | 21.89 | 4.73 | 0.36 | 42.59 | 11310 | 42.26 | 43.02 | 33.7626 | -118.0072 | 43.177 | Casing - Start
GWD 11320 | Girth Weld |  | 36167.12 | 42.26 | 0.28 | 42000 | ERW | 8.625 | 728 | [10 empty] | AGM 11 | 2488.22 | AGM 12 | 605.94 | 42.59 | 42.26 | 0.36 | 42.59 | 42.26 | 11320 | 43.02 | 4.26 | 33.7626 | -118.0072 | 41.434
GWD 11330 | Girth Weld |  | 36209.38 | 17.35 | 0.28 | 42000 | ERW | 8.625 | 728 | [10 empty] | AGM 11 | 2530.49 | AGM 12 | 563.67 | 42.26 | 43.02 | 42.59 | 42.26 | 43.02 | 11330 | 4.26 | 0.84 | 33.7627 | -118.0071 | 42.537
CSG 7 | Casing End |  | 36226.73 | 25.67 | 0.28 | 42000 | ERW | 8.625 | 728 | [10 empty] | AGM 11 | 2547.83 | AGM 12 | 546.33 | 17.35 | 25.67 | 42.59 | 42.26 | 43.02 | 11330 | 4.26 | 0.84 | 33.7628 | -118.0071 | 42.812 | Casing - End
GWD 11340 | Girth Weld |  | 36252.4 | 4.26 | 0.28 | 42000 | ERW | 8.625 | 728 | [10 empty] | AGM 11 | 2573.51 | AGM 12 | 520.65 | 43.02 | 4.26 | 42.26 | 43.02 | 4.26 | 11340 | 0.84 | 28.65 | 33.7629 | -118.0071 | 42.694
GWD 11350 | Girth Weld |  | 36256.67 | 0.29 | 0.28 | 42000 | ERW | 8.625 | 728 | [10 empty] | AGM 11 | 2577.77 | AGM 12 | 516.39 | 4.26 | 0.84 | 43.02 | 4.26 | 0.84 | 11350 | 28.65 | 42.12 | 33.7629 | -118.0071 | 42.674
BND 90 | Bend |  | 36256.96 | 0.55 | 0.28 | 42000 | ERW | 8.625 | 728 |  |  | 10.079 | [7 empty] | AGM 11 | 2578.06 | AGM 12 | 516.1 | 0.29 | 0.55 | 43.02 | 4.26 | 0.84 | 11350 | 28.65 | 42.12 | 33.7629 | -118.0071 | 42.671 | 5.0D 28.8 deg left turn bend
GWD 11360 | Girth Weld |  | 36257.51 | 28.65 | 0.28 | 42000 | ERW | 8.625 | 728 | [10 empty] | AGM 11 | 2578.61 | AGM 12 | 515.55 | 0.84 | 28.65 | 4.26 | 0.84 | 28.65 | 11360 | 42.12 | 41.31 | 33.7629 | -118.0071 | 42.671
GWD 11370 | Girth Weld |  | 36286.16 | 42.12 | 0.28 | 42000 | ERW | 8.625 | 728 | [10 empty] | AGM 11 | 2607.26 | AGM 12 | 486.9 | 28.65 | 42.12 | 0.84 | 28.65 | 42.12 | 11370 | 41.31 | 42.93 | 33.7629 | -118.0071 | 43.043
GWD 11380 | Girth Weld |  | 36328.28 | 41.31 | 0.28 | 42000 | ERW | 8.625 | 728 | [10 empty] | AGM 11 | 2649.38 | AGM 12 | 444.78 | 42.12 | 41.31 | 28.65 | 42.12 | 41.31 | 11380 | 42.93 | 42.38 | 33.7631 | -118.0071 | 42.979
GWD 11390 | Girth Weld |  | 36369.59 | 42.93 | 0.28 | 42000 | ERW | 8.625 | 728 | [10 empty] | AGM 11 | 2690.69 | AGM 12 | 403.47 | 41.31 | 42.93 | 42.12 | 41.31 | 42.93 | 11390 | 42.38 | 42.43 | 33.7632 | -118.0071 | 42.96
GWD 11400 | Girth Weld |  | 36412.52 | 42.38 | 0.28 | 42000 | ERW | 8.625 | 728 | [10 empty] | AGM 11 | 2733.62 | AGM 12 | 360.54 | 42.93 | 42.38 | 41.31 | 42.93 | 42.38 | 11400 | 42.43 | 42.86 | 33.7633 | -118.0071 | 42.532
GWD 11410 | Girth Weld |  | 36454.9 | 42.43 | 0.28 | 42000 | ERW | 8.625 | 728 | [10 empty] | AGM 11 | 2776 | AGM 12 | 318.16 | 42.38 | 42.43 | 42.93 | 42.38 | 42.43 | 11410 | 42.86 | 4.53 | 33.7634 | -118.0071 | 42.298
GWD 11420 | Girth Weld |  | 36497.33 | 42.86 | 0.28 | 42000 | ERW | 8.625 | 728 | [10 empty] | AGM 11 | 2818.43 | AGM 12 | 275.73 | 42.43 | 42.86 | 42.38 | 42.43 | 42.86 | 11420 | 4.53 | 42.74 | 33.7635 | -118.0071 | 42.312
GWD 11430 | Girth Weld |  | 36540.19 | 4.53 | 0.28 | 42000 | ERW | 8.625 | 728 | [10 empty] | AGM 11 | 2861.3 | AGM 12 | 232.86 | 42.86 | 4.53 | 42.43 | 42.86 | 4.53 | 11430 | 42.74 | 41.74 | 33.7636 | -118.0071 | 42.056
GWD 11440 | Girth Weld |  | 36544.72 | 42.74 | 0.28 | 42000 | ERW | 8.625 | 728 | [10 empty] | AGM 11 | 2865.82 | AGM 12 | 228.34 | 4.53 | 42.74 | 42.86 | 4.53 | 42.74 | 11440 | 41.74 | 42.6 | 33.7637 | -118.0071 | 41.915
GWD 11450 | Girth Weld |  | 36587.46 | 41.74 | 0.28 | 42000 | ERW | 8.625 | 728 | [10 empty] | AGM 11 | 2908.57 | AGM 12 | 185.6 | 42.74 | 41.74 | 4.53 | 42.74 | 41.74 | 11450 | 42.6 | 37.36 | 33.7638 | -118.0071 | 42.023
GWD 11460 | Girth Weld |  | 36629.2 | 42.6 | 0.28 | 42000 | ERW | 8.625 | 728 | [10 empty] | AGM 11 | 2950.3 | AGM 12 | 143.86 | 41.74 | 42.6 | 42.74 | 41.74 | 42.6 | 11460 | 37.36 | 41.43 | 33.7639 | -118.0071 | 42.15
GWD 11470 | Girth Weld |  | 36671.8 | 37.36 | 0.28 | 42000 | ERW | 8.625 | 728 | [10 empty] | AGM 11 | 2992.9 | AGM 12 | 101.26 | 42.6 | 37.36 | 41.74 | 42.6 | 37.36 | 11470 | 41.43 | 41.87 | 33.764 | -118.0071 | 42.041
GWD 11480 | Girth Weld |  | 36709.16 | 41.43 | 0.28 | 42000 | ERW | 8.625 | 728 | [10 empty] | AGM 11 | 3030.27 | AGM 12 | 63.89 | 37.36 | 41.43 | 42.6 | 37.36 | 41.43 | 11480 | 41.87 | 40.1 | 33.7641 | -118.0071 | 42.042
GWD 11490 | Girth Weld |  | 36750.6 | 22.46 | 0.28 | 42000 | ERW | 8.625 | 728 | [10 empty] | AGM 11 | 3071.7 | AGM 12 | 22.46 | 41.43 | 41.87 | 37.36 | 41.43 | 41.87 | 11490 | 40.1 | 39.58 | 33.7642 | -118.0071 | 41.581
MRK 10 | Marker |  | 36773.06 | 19.41 | 0.28 | 42000 | ERW | 8.625 | 728 |  |  |  |  | 11:32 | [5 empty] | AGM 11 | 3094.16 | AGM 13 | 2977.03 | 22.46 | 19.41 | 37.36 | 41.43 | 41.87 | 11490 | 40.1 | 39.58 | 33.7643 | -118.0071 | 41.414 | AGM 12 7' West of Curb - Located in Goldenwest St
GWD 11500 | Girth Weld |  | 36792.46 | 40.1 | 0.28 | 42000 | ERW | 8.625 | 728 | [10 empty] | AGM 12 | 19.41 | AGM 13 | 2957.63 | 41.87 | 40.1 | 41.43 | 41.87 | 40.1 | 11500 | 39.58 | 1.75 | 33.7643 | -118.0071 | 41.421
GWD 11510 | Girth Weld |  | 36832.56 | 39.58 | 0.28 | 42000 | ERW | 8.625 | 728 | [10 empty] | AGM 12 | 59.5 | AGM 13 | 2917.53 | 40.1 | 39.58 | 41.87 | 40.1 | 39.58 | 11510 | 1.75 | 36.8 | 33.7644 | -118.0071 | 42.264
GWD 11520 | Girth Weld |  | 36872.14 | 1.75 | 0.28 | 42000 | ERW | 8.625 | 728 | [10 empty] | AGM 12 | 99.09 | AGM 13 | 2877.95 | 39.58 | 1.75 | 40.1 | 39.58 | 1.75 | 11520 | 36.8 | 20.73 | 33.7646 | -118.0071 | 42.98
GWD 11530 | Girth Weld |  | 36873.89 | 36.8 | 0.28 | 42000 | ERW | 8.625 | 728 | [10 empty] | AGM 12 | 100.83 | AGM 13 | 2876.2 | 1.75 | 36.8 | 39.58 | 1.75 | 36.8 | 11530 | 20.73 | 20.55 | 33.7646 | -118.0071 | 43.035
GWD 11540 | Girth Weld |  | 36910.69 | 20.73 | 0.25 | 42000 | SMLS | 8.625 | 728 | [10 empty] | AGM 12 | 137.63 | AGM 13 | 2839.41 | 36.8 | 20.73 | 1.75 | 36.8 | 20.73 | 11540 | 20.55 | 38.22 | 33.7647 | -118.0071 | 43.482 | Estimated WT 0.250
GWD 11550 | Girth Weld |  | 36931.42 | 20.55 | 0.25 | 42000 | SMLS | 8.625 | 728 | [10 empty] | AGM 12 | 158.36 | AGM 13 | 2818.67 | 20.73 | 20.55 | 36.8 | 20.73 | 20.55 | 11550 | 38.22 | 31.2 | 33.7647 | -118.0071 | 43.652
GWD 11560 | Girth Weld |  | 36951.97 | 38.22 | 0.28 | 42000 | ERW | 8.625 | 728 | [10 empty] | AGM 12 | 178.91 | AGM 13 | 2798.12 | 20.55 | 38.22 | 20.73 | 20.55 | 38.22 | 11560 | 31.2 | 37.89 | 33.7648 | -118.0071 | 43.802
GWD 11570 | Girth Weld |  | 36990.19 | 31.2 | 0.28 | 42000 | ERW | 8.625 | 728 | [10 empty] | AGM 12 | 217.13 | AGM 13 | 2759.91 | 38.22 | 31.2 | 20.55 | 38.22 | 31.2 | 11570 | 37.89 | 37.12 | 33.7649 | -118.0071 | 43.663
GWD 11580 | Girth Weld |  | 37021.39 | 37.89 | 0.28 | 42000 | ERW | 8.625 | 728 | [10 empty] | AGM 12 | 248.33 | AGM 13 | 2728.7 | 31.2 | 37.89 | 38.22 | 31.2 | 37.89 | 11580 | 37.12 | 38.64 | 33.765 | -118.0071 | 43.981
GWD 11590 | Girth Weld |  | 37059.28 | 37.12 | 0.28 | 42000 | ERW | 8.625 | 728 | [10 empty] | AGM 12 | 286.22 | AGM 13 | 2690.82 | 37.89 | 37.12 | 31.2 | 37.89 | 37.12 | 11590 | 38.64 | 37.74 | 33.7651 | -118.0071 | 43.947
GWD 11600 | Girth Weld |  | 37096.4 | 38.64 | 0.28 | 42000 | ERW | 8.625 | 728 | [10 empty] | AGM 12 | 323.34 | AGM 13 | 2653.7 | 37.12 | 38.64 | 37.89 | 37.12 | 38.64 | 11600 | 37.74 | 39.07 | 33.7652 | -118.0071 | 44.077
GWD 11610 | Girth Weld |  | 37135.04 | 37.74 | 0.28 | 42000 | ERW | 8.625 | 728 | [10 empty] | AGM 12 | 361.98 | AGM 13 | 2615.06 | 38.64 | 37.74 | 37.12 | 38.64 | 37.74 | 11610 | 39.07 | 38.44 | 33.7653 | -118.0071 | 44.062
GWD 11620 | Girth Weld |  | 37172.77 | 39.07 | 0.28 | 42000 | ERW | 8.625 | 728 | [10 empty] | AGM 12 | 399.72 | AGM 13 | 2577.32 | 37.74 | 39.07 | 38.64 | 37.74 | 39.07 | 11620 | 38.44 | 37.9 | 33.7654 | -118.0071 | 44.251
GWD 11630 | Girth Weld |  | 37211.85 | 38.44 | 0.28 | 42000 | ERW | 8.625 | 728 | [10 empty] | AGM 12 | 438.79 | AGM 13 | 2538.25 | 39.07 | 38.44 | 37.74 | 39.07 | 38.44 | 11630 | 37.9 | 34.19 | 33.7655 | -118.0071 | 44.324
GWD 11640 | Girth Weld |  | 37250.28 | 37.9 | 0.28 | 42000 | ERW | 8.625 | 728 | [10 empty] | AGM 12 | 477.22 | AGM 13 | 2499.81 | 38.44 | 37.9 | 39.07 | 38.44 | 37.9 | 11640 | 34.19 | 38.62 | 33.7656 | -118.0071 | 44.204
GWD 11650 | Girth Weld |  | 37288.18 | 34.19 | 0.28 | 42000 | ERW | 8.625 | 728 | [10 empty] | AGM 12 | 515.12 | AGM 13 | 2461.91 | 37.9 | 34.19 | 38.44 | 37.9 | 34.19 | 11650 | 38.62 | 34.87 | 33.7657 | -118.0071 | 44.335
GWD 11660 | Girth Weld |  | 37322.37 | 38.62 | 0.28 | 42000 | ERW | 8.625 | 728 | [10 empty] | AGM 12 | 549.31 | AGM 13 | 2427.72 | 34.19 | 38.62 | 37.9 | 34.19 | 38.62 | 11660 | 34.87 | 56.02 | 33.7658 | -118.0071 | 44.226
GWD 11670 | Girth Weld |  | 37360.99 | 34.87 | 0.28 | 42000 | ERW | 8.625 | 728 | [10 empty] | AGM 12 | 587.94 | AGM 13 | 2389.1 | 38.62 | 34.87 | 34.19 | 38.62 | 34.87 | 11670 | 56.02 | 61.18 | 33.7659 | -118.0071 | 44.092
GWD 11680 | Girth Weld |  | 37395.87 | 56.02 | 0.28 | 42000 | ERW | 8.625 | 728 | [10 empty] | AGM 12 | 622.81 | AGM 13 | 2354.23 | 34.87 | 56.02 | 38.62 | 34.87 | 56.02 | 11680 | 61.18 | 61.76 | 33.766 | -118.0071 | 44.357
GWD 11690 | Girth Weld |  | 37451.88 | 61.18 | 0.28 | 42000 | ERW | 8.625 | 728 | [10 empty] | AGM 12 | 678.82 | AGM 13 | 2298.21 | 56.02 | 61.18 | 34.87 | 56.02 | 61.18 | 11690 | 61.76 | 9.2 | 33.7661 | -118.0071 | 44.57
GWD 11700 | Girth Weld |  | 37513.06 | 61.76 | 0.28 | 42000 | ERW | 8.625 | 728 | [10 empty] | AGM 12 | 740 | AGM 13 | 2237.03 | 61.18 | 61.76 | 56.02 | 61.18 | 61.76 | 11700 | 9.2 | 53.49 | 33.7663 | -118.0071 | 43.983
GWD 11710 | Girth Weld |  | 37574.82 | 9.2 | 0.28 | 42000 | ERW | 8.625 | 728 | [10 empty] | AGM 12 | 801.76 | AGM 13 | 2175.27 | 61.76 | 9.2 | 61.18 | 61.76 | 9.2 | 11710 | 53.49 | 9.8 | 33.7665 | -118.0071 | 43.184
GWD 11720 | Girth Weld |  | 37584.02 | 53.49 | 0.28 | 42000 | ERW | 8.625 | 728 | [10 empty] | AGM 12 | 810.96 | AGM 13 | 2166.07 | 9.2 | 53.49 | 61.76 | 9.2 | 53.49 | 11720 | 9.8 | 0.99 | 33.7665 | -118.0071 | 43.309
GWD 11730 | Girth Weld |  | 37637.51 | 9.8 | 0.28 | 42000 | ERW | 8.625 | 728 | [10 empty] | AGM 12 | 864.45 | AGM 13 | 2112.58 | 53.49 | 9.8 | 9.2 | 53.49 | 9.8 | 11730 | 0.99 | 1.03 | 33.7667 | -118.0072 | 43.7
GWD 11740 | Girth Weld |  | 37647.31 | 0.99 | 0.28 | 42000 | ERW | 8.625 | 728 | [10 empty] | AGM 12 | 874.25 | AGM 13 | 2102.78 | 9.8 | 0.99 | 53.49 | 9.8 | 0.99 | 11740 | 1.03 | 45.33 | 33.7667 | -118.0072 | 43.702
GWD 11750 | Girth Weld |  | 37648.29 | 1.03 | 0.219 | 42000 | ERW | 8.625 | 728 | [10 empty] | AGM 12 | 875.24 | AGM 13 | 2101.8 | 0.99 | 1.03 | 9.8 | 0.99 | 1.03 | 11750 | 45.33 | 47.78 | 33.7667 | -118.0072 | 43.714
GWD 11760 | Girth Weld |  | 37649.32 | 45.33 | 0.219 | 42000 | ERW | 8.625 | 728 | [10 empty] | AGM 12 | 876.27 | AGM 13 | 2100.77 | 1.03 | 45.33 | 0.99 | 1.03 | 45.33 | 11760 | 47.78 | 47.82 | 33.7667 | -118.0072 | 43.722
GWD 11770 | Girth Weld |  | 37694.65 | 47.78 | 0.219 | 42000 | ERW | 8.625 | 728 | [10 empty] | AGM 12 | 921.6 | AGM 13 | 2055.44 | 45.33 | 47.78 | 1.03 | 45.33 | 47.78 | 11770 | 47.82 | 47.7 | 33.7668 | -118.0072 | 43.901
GWD 11780 | Girth Weld |  | 37742.43 | 47.82 | 0.219 | 42000 | ERW | 8.625 | 728 | [10 empty] | AGM 12 | 969.37 | AGM 13 | 2007.66 | 47.78 | 47.82 | 45.33 | 47.78 | 47.82 | 11780 | 47.7 | 47.74 | 33.7669 | -118.0072 | 43.589
GWD 11790 | Girth Weld |  | 37790.25 | 47.7 | 0.219 | 42000 | ERW | 8.625 | 728 | [10 empty] | AGM 12 | 1017.2 | AGM 13 | 1959.84 | 47.82 | 47.7 | 47.78 | 47.82 | 47.7 | 11790 | 47.74 | 47.92 | 33.7671 | -118.0072 | 43.255
GWD 11800 | Girth Weld |  | 37837.95 | 47.74 | 0.219 | 42000 | ERW | 8.625 | 728 | [10 empty] | AGM 12 | 1064.9 | AGM 13 | 1912.14 | 47.7 | 47.74 | 47.82 | 47.7 | 47.74 | 11800 | 47.92 | 47.7 | 33.7672 | -118.0072 | 43.388
GWD 11810 | Girth Weld |  | 37885.7 | 47.92 | 0.219 | 42000 | ERW | 8.625 | 728 | [10 empty] | AGM 12 | 1112.64 | AGM 13 | 1864.39 | 47.74 | 47.92 | 47.7 | 47.74 | 47.92 | 11810 | 47.7 | 21.64 | 33.7673 | -118.0072 | 43.323
GWD 11820 | Girth Weld |  | 37933.62 | 47.7 | 0.219 | 42000 | ERW | 8.625 | 728 | [10 empty] | AGM 12 | 1160.56 | AGM 13 | 1816.47 | 47.92 | 47.7 | 47.74 | 47.92 | 47.7 | 11820 | 21.64 | 1.03 | 33.7675 | -118.0072 | 43.594
GWD 11830 | Girth Weld |  | 37981.32 | 21.64 | 0.219 | 42000 | ERW | 8.625 | 728 | [10 empty] | AGM 12 | 1208.26 | AGM 13 | 1768.77 | 47.7 | 21.64 | 47.92 | 47.7 | 21.64 | 11830 | 1.03 | 1.52 | 33.7676 | -118.0072 | 44.082
GWD 11840 | Girth Weld |  | 38002.96 | 1.03 | 0.219 | 42000 | ERW | 8.625 | 728 | [10 empty] | AGM 12 | 1229.9 | AGM 13 | 1747.13 | 21.64 | 1.03 | 47.7 | 21.64 | 1.03 | 11840 | 1.52 | 11.06 | 33.7677 | -118.0072 | 44.444
GWD 11850 | Girth Weld |  | 38003.99 | 0.73 | 0.219 | 42000 | ERW | 8.625 | 728 | [10 empty] | AGM 12 | 1230.93 | AGM 13 | 1746.1 | 1.03 | 1.52 | 21.64 | 1.03 | 1.52 | 11850 | 11.06 | 1.5 | 33.7677 | -118.0072 | 44.45
BND 91 | Bend |  | 38004.72 | 0.8 | 0.219 | 42000 | ERW | 8.625 | 728 |  |  | 24.78 | [7 empty] | AGM 12 | 1231.66 | AGM 13 | 1745.38 | 0.73 | 0.8 | 21.64 | 1.03 | 1.52 | 11850 | 11.06 | 1.5 | 33.7677 | -118.0072 | 44.447 | 3.0D 47.4 deg right turn bend
GWD 11860 | Girth Weld |  | 38005.51 | 11.06 | 0.219 | 42000 | ERW | 8.625 | 728 | [10 empty] | AGM 12 | 1232.45 | AGM 13 | 1744.58 | 1.52 | 11.06 | 1.03 | 1.52 | 11.06 | 11860 | 1.5 | 1.06 | 33.7677 | -118.0072 | 44.447
GWD 11870 | Girth Weld |  | 38016.57 | 0.72 | 0.219 | 42000 | ERW | 8.625 | 728 | [10 empty] | AGM 12 | 1243.52 | AGM 13 | 1733.52 | 11.06 | 1.5 | 1.52 | 11.06 | 1.5 | 11870 | 1.06 | 1.01 | 33.7677 | -118.0072 | 44.464
BND 92 | Bend |  | 38017.3 | 0.78 | 0.219 | 42000 | ERW | 8.625 | 728 |  |  | 24.682 | [7 empty] | AGM 12 | 1244.24 | AGM 13 | 1732.8 | 0.72 | 0.78 | 1.52 | 11.06 | 1.5 | 11870 | 1.06 | 1.01 | 33.7677 | -118.0072 | 44.48 | 3.0D 46.6 deg left turn bend
GWD 11880 | Girth Weld |  | 38018.08 | 1.06 | 0.219 | 42000 | ERW | 8.625 | 728 | [10 empty] | AGM 12 | 1245.02 | AGM 13 | 1732.02 | 1.5 | 1.06 | 11.06 | 1.5 | 1.06 | 11880 | 1.01 | 40.37 | 33.7677 | -118.0072 | 44.487
GWD 11890 | Girth Weld |  | 38019.14 | 1.01 | 0.312 | 42000 | ERW | 8.625 | 728 | [10 empty] | AGM 12 | 1246.08 | AGM 13 | 1730.96 | 1.06 | 1.01 | 1.5 | 1.06 | 1.01 | 11890 | 40.37 | 41.44 | 33.7677 | -118.0072 | 44.501 | Estimated WT 0.312
GWD 11900 | Girth Weld |  | 38020.15 | 40.37 | 0.312 | 42000 | ERW | 8.625 | 728 | [10 empty] | AGM 12 | 1247.09 | AGM 13 | 1729.94 | 1.01 | 40.37 | 1.06 | 1.01 | 40.37 | 11900 | 41.44 | 41.01 | 33.7677 | -118.0072 | 44.519
GWD 11910 | Girth Weld |  | 38060.52 | 41.44 | 0.312 | 42000 | ERW | 8.625 | 728 | [10 empty] | AGM 12 | 1287.46 | AGM 13 | 1689.57 | 40.37 | 41.44 | 1.01 | 40.37 | 41.44 | 11910 | 41.01 | 40.09 | 33.7678 | -118.0072 | 44.529
GWD 11920 | Girth Weld |  | 38101.96 | 41.01 | 0.312 | 42000 | ERW | 8.625 | 728 | [10 empty] | AGM 12 | 1328.9 | AGM 13 | 1648.13 | 41.44 | 41.01 | 40.37 | 41.44 | 41.01 | 11920 | 40.09 | 21.04 | 33.7679 | -118.0072 | 44.553
GWD 11930 | Girth Weld |  | 38142.97 | 40.09 | 0.312 | 42000 | ERW | 8.625 | 728 | [10 empty] | AGM 12 | 1369.91 | AGM 13 | 1607.13 | 41.01 | 40.09 | 41.44 | 41.01 | 40.09 | 11930 | 21.04 | 37.98 | 33.768 | -118.0072 | 44.512
GWD 11940 | Girth Weld |  | 38183.05 | 21.04 | 0.312 | 42000 | ERW | 8.625 | 728 | [10 empty] | AGM 12 | 1409.99 | AGM 13 | 1567.04 | 40.09 | 21.04 | 41.01 | 40.09 | 21.04 | 11940 | 37.98 | 40.55 | 33.7681 | -118.0072 | 44.09
GWD 11950 | Girth Weld |  | 38204.09 | 37.98 | 0.312 | 42000 | ERW | 8.625 | 728 | [10 empty] | AGM 12 | 1431.03 | AGM 13 | 1546 | 21.04 | 37.98 | 40.09 | 21.04 | 37.98 | 11950 | 40.55 | 41.75 | 33.7682 | -118.0072 | 44.228
GWD 11960 | Girth Weld |  | 38242.06 | 40.55 | 0.312 | 42000 | ERW | 8.625 | 728 | [10 empty] | AGM 12 | 1469.01 | AGM 13 | 1508.03 | 37.98 | 40.55 | 21.04 | 37.98 | 40.55 | 11960 | 41.75 | 41.98 | 33.7683 | -118.0072 | 44.47
GWD 11970 | Girth Weld |  | 38282.62 | 41.75 | 0.312 | 42000 | ERW | 8.625 | 728 | [10 empty] | AGM 12 | 1509.56 | AGM 13 | 1467.47 | 40.55 | 41.75 | 37.98 | 40.55 | 41.75 | 11970 | 41.98 | 38.87 | 33.7684 | -118.0072 | 44.667
GWD 11980 | Girth Weld |  | 38324.37 | 41.98 | 0.312 | 42000 | ERW | 8.625 | 728 | [10 empty] | AGM 12 | 1551.32 | AGM 13 | 1425.72 | 41.75 | 41.98 | 40.55 | 41.75 | 41.98 | 11980 | 38.87 | 41.68 | 33.7685 | -118.0072 | 44.957
GWD 11990 | Girth Weld |  | 38366.35 | 38.87 | 0.312 | 42000 | ERW | 8.625 | 728 | [10 empty] | AGM 12 | 1593.29 | AGM 13 | 1383.74 | 41.98 | 38.87 | 41.75 | 41.98 | 38.87 | 11990 | 41.68 | 37.78 | 33.7686 | -118.0072 | 45.231
GWD 12000 | Girth Weld |  | 38405.22 | 41.68 | 0.312 | 42000 | ERW | 8.625 | 728 | [10 empty] | AGM 12 | 1632.16 | AGM 13 | 1344.87 | 38.87 | 41.68 | 41.98 | 38.87 | 41.68 | 12000 | 37.78 | 1.55 | 33.7688 | -118.0072 | 45.424
GWD 12010 | Girth Weld |  | 38446.9 | 37.78 | 0.312 | 42000 | ERW | 8.625 | 728 | [10 empty] | AGM 12 | 1673.84 | AGM 13 | 1303.19 | 41.68 | 37.78 | 38.87 | 41.68 | 37.78 | 12010 | 1.55 | 10.91 | 33.7689 | -118.0072 | 45.582
GWD 12020 | Girth Weld |  | 38484.67 | 0.83 | 0.312 | 42000 | ERW | 8.625 | 728 | [10 empty] | AGM 12 | 1711.62 | AGM 13 | 1265.42 | 37.78 | 1.55 | 41.68 | 37.78 | 1.55 | 12020 | 10.91 | 1.51 | 33.769 | -118.0072 | 45.941
BND 93 | Bend |  | 38485.5 | 0.72 | 0.312 | 42000 | ERW | 8.625 | 728 |  |  | 24.56 | [7 empty] | AGM 12 | 1712.44 | AGM 13 | 1264.59 | 0.83 | 0.72 | 41.68 | 37.78 | 1.55 | 12020 | 10.91 | 1.51 | 33.769 | -118.0072 | 45.918 | 3.0D 46.9 deg left turn over bend
GWD 12030 | Girth Weld |  | 38486.22 | 10.91 | 0.219 | 42000 | ERW | 8.625 | 728 | [10 empty] | AGM 12 | 1713.17 | AGM 13 | 1263.87 | 1.55 | 10.91 | 37.78 | 1.55 | 10.91 | 12030 | 1.51 | 0.96 | 33.769 | -118.0072 | 45.848
GWD 12040 | Girth Weld |  | 38497.13 | 0.61 | 0.219 | 42000 | ERW | 8.625 | 728 | [10 empty] | AGM 12 | 1724.08 | AGM 13 | 1252.96 | 10.91 | 1.51 | 1.55 | 10.91 | 1.51 | 12040 | 0.96 | 44.68 | 33.769 | -118.0072 | 44.276
BND 94 | Bend |  | 38497.74 | 0.9 | 0.219 | 42000 | ERW | 8.625 | 728 |  |  | 25.107 | [7 empty] | AGM 12 | 1724.68 | AGM 13 | 1252.35 | 0.61 | 0.9 | 1.55 | 10.91 | 1.51 | 12040 | 0.96 | 44.68 | 33.769 | -118.0072 | 44.221 | 3.0D 47.2 deg right turn sag bend
GWD 12050 | Girth Weld |  | 38498.64 | 0.96 | 0.312 | 42000 | ERW | 8.625 | 728 | [10 empty] | AGM 12 | 1725.59 | AGM 13 | 1251.45 | 1.51 | 0.96 | 10.91 | 1.51 | 0.96 | 12050 | 44.68 | 47.75 | 33.769 | -118.0072 | 44.195 | Estimated WT 0.312
GWD 12060 | Girth Weld |  | 38499.61 | 44.68 | 0.219 | 42000 | ERW | 8.625 | 728 | [10 empty] | AGM 12 | 1726.55 | AGM 13 | 1250.48 | 0.96 | 44.68 | 1.51 | 0.96 | 44.68 | 12060 | 47.75 | 47.71 | 33.769 | -118.0072 | 44.211
GWD 12070 | Girth Weld |  | 38544.29 | 47.75 | 0.219 | 42000 | ERW | 8.625 | 728 | [10 empty] | AGM 12 | 1771.23 | AGM 13 | 1205.81 | 44.68 | 47.75 | 0.96 | 44.68 | 47.75 | 12070 | 47.71 | 47.62 | 33.7691 | -118.0072 | 44.101
GWD 12080 | Girth Weld |  | 38592.04 | 47.71 | 0.219 | 42000 | ERW | 8.625 | 728 | [10 empty] | AGM 12 | 1818.98 | AGM 13 | 1158.05 | 47.75 | 47.71 | 44.68 | 47.75 | 47.71 | 12080 | 47.62 | 12.22 | 33.7693 | -118.0072 | 44.046
GWD 12090 | Girth Weld |  | 38639.75 | 47.62 | 0.219 | 42000 | ERW | 8.625 | 728 | [10 empty] | AGM 12 | 1866.69 | AGM 13 | 1110.34 | 47.71 | 47.62 | 47.75 | 47.71 | 47.62 | 12090 | 12.22 | 31.29 | 33.7694 | -118.0072 | 43.795
GWD 12100 | Girth Weld |  | 38687.37 | 12.22 | 0.219 | 42000 | ERW | 8.625 | 728 | [10 empty] | AGM 12 | 1914.31 | AGM 13 | 1062.73 | 47.62 | 12.22 | 47.71 | 47.62 | 12.22 | 12100 | 31.29 | 43.59 | 33.7695 | -118.0072 | 43.563
GWD 12110 | Girth Weld |  | 38699.59 | 31.29 | 0.203 | 42000 | ERW | 8.625 | 728 | [10 empty] | AGM 12 | 1926.53 | AGM 13 | 1050.51 | 12.22 | 31.29 | 47.62 | 12.22 | 31.29 | 12110 | 43.59 | 42.45 | 33.7696 | -118.0072 | 43.661 | Estimated WT 0.203
GWD 12120 | Girth Weld |  | 38730.87 | 43.59 | 0.203 | 42000 | ERW | 8.625 | 728 | [10 empty] | AGM 12 | 1957.82 | AGM 13 | 1019.22 | 31.29 | 43.59 | 12.22 | 31.29 | 43.59 | 12120 | 42.45 | 39.91 | 33.7696 | -118.0072 | 43.56
GWD 12130 | Girth Weld |  | 38774.46 | 42.45 | 0.203 | 42000 | ERW | 8.625 | 728 | [10 empty] | AGM 12 | 2001.41 | AGM 13 | 975.63 | 43.59 | 42.45 | 31.29 | 43.59 | 42.45 | 12130 | 39.91 | 6.02 | 33.7698 | -118.0072 | 43.627
GWD 12140 | Girth Weld |  | 38816.92 | 39.91 | 0.203 | 42000 | ERW | 8.625 | 728 | [10 empty] | AGM 12 | 2043.86 | AGM 13 | 933.17 | 42.45 | 39.91 | 43.59 | 42.45 | 39.91 | 12140 | 6.02 | 0.94 | 33.7699 | -118.0072 | 43.914
GWD 12150 | Girth Weld |  | 38856.82 | 6.02 | 0.203 | 42000 | ERW | 8.625 | 728 | [10 empty] | AGM 12 | 2083.77 | AGM 13 | 893.27 | 39.91 | 6.02 | 42.45 | 39.91 | 6.02 | 12150 | 0.94 | 11.79 | 33.77 | -118.0072 | 44.313
GWD 12160 | Girth Weld |  | 38862.84 | 0.94 | 0.312 | 42000 | ERW | 8.625 | 728 | [10 empty] | AGM 12 | 2089.78 | AGM 13 | 887.25 | 6.02 | 0.94 | 39.91 | 6.02 | 0.94 | 12160 | 11.79 | 42.54 | 33.77 | -118.0072 | 44.432 | Estimated WT 0.312
GWD 12170 | Girth Weld |  | 38863.78 | 11.79 | 0.312 | 42000 | ERW | 8.625 | 728 | [10 empty] | AGM 12 | 2090.72 | AGM 13 | 886.32 | 0.94 | 11.79 | 6.02 | 0.94 | 11.79 | 12170 | 42.54 | 43.49 | 33.77 | -118.0072 | 44.454
GWD 12180 | Girth Weld |  | 38875.56 | 42.54 | 0.312 | 42000 | ERW | 8.625 | 728 | [10 empty] | AGM 12 | 2102.51 | AGM 13 | 874.53 | 11.79 | 42.54 | 0.94 | 11.79 | 42.54 | 12180 | 43.49 | 43.2 | 33.77 | -118.0072 | 44.685
GWD 12190 | Girth Weld |  | 38918.11 | 43.49 | 0.312 | 42000 | ERW | 8.625 | 728 | [10 empty] | AGM 12 | 2145.05 | AGM 13 | 831.99 | 42.54 | 43.49 | 11.79 | 42.54 | 43.49 | 12190 | 43.2 | 43.88 | 33.7702 | -118.0072 | 44.456
GWD 12200 | Girth Weld |  | 38961.59 | 43.2 | 0.312 | 42000 | ERW | 8.625 | 728 | [10 empty] | AGM 12 | 2188.54 | AGM 13 | 788.5 | 43.49 | 43.2 | 42.54 | 43.49 | 43.2 | 12200 | 43.88 | 42.71 | 33.7703 | -118.0072 | 44.292
GWD 12210 | Girth Weld |  | 39004.79 | 43.88 | 0.312 | 42000 | ERW | 8.625 | 728 | [10 empty] | AGM 12 | 2231.74 | AGM 13 | 745.3 | 43.2 | 43.88 | 43.49 | 43.2 | 43.88 | 12210 | 42.71 | 43 | 33.7704 | -118.0072 | 44.639
GWD 12220 | Girth Weld |  | 39048.68 | 42.71 | 0.312 | 42000 | ERW | 8.625 | 728 | [10 empty] | AGM 12 | 2275.62 | AGM 13 | 701.41 | 43.88 | 42.71 | 43.2 | 43.88 | 42.71 | 12220 | 43 | 44.41 | 33.7705 | -118.0072 | 44.715
GWD 12230 | Girth Weld |  | 39091.39 | 43 | 0.312 | 42000 | ERW | 8.625 | 728 | [10 empty] | AGM 12 | 2318.34 | AGM 13 | 658.7 | 42.71 | 43 | 43.88 | 42.71 | 43 | 12230 | 44.41 | 44.99 | 33.7706 | -118.0072 | 44.819
GWD 12240 | Girth Weld |  | 39134.39 | 44.41 | 0.312 | 42000 | ERW | 8.625 | 728 | [10 empty] | AGM 12 | 2361.34 | AGM 13 | 615.7 | 43 | 44.41 | 42.71 | 43 | 44.41 | 12240 | 44.99 | 42.27 | 33.7707 | -118.0072 | 44.835
GWD 12250 | Girth Weld |  | 39178.8 | 44.99 | 0.312 | 42000 | ERW | 8.625 | 728 | [10 empty] | AGM 12 | 2405.74 | AGM 13 | 571.29 | 44.41 | 44.99 | 43 | 44.41 | 44.99 | 12250 | 42.27 | 47.58 | 33.7709 | -118.0072 | 45.318
GWD 12260 | Girth Weld |  | 39223.79 | 42.27 | 0.312 | 42000 | ERW | 8.625 | 728 | [10 empty] | AGM 12 | 2450.74 | AGM 13 | 526.3 | 44.99 | 42.27 | 44.41 | 44.99 | 42.27 | 12260 | 47.58 | 39.77 | 33.771 | -118.0072 | 45.736
GWD 12270 | Girth Weld |  | 39266.07 | 47.58 | 0.312 | 42000 | ERW | 8.625 | 728 | [10 empty] | AGM 12 | 2493.01 | AGM 13 | 484.03 | 42.27 | 47.58 | 44.99 | 42.27 | 47.58 | 12270 | 39.77 | 43.59 | 33.7711 | -118.0072 | 45.645
GWD 12280 | Girth Weld |  | 39313.64 | 39.77 | 0.312 | 42000 | ERW | 8.625 | 728 | [10 empty] | AGM 12 | 2540.58 | AGM 13 | 436.45 | 47.58 | 39.77 | 42.27 | 47.58 | 39.77 | 12280 | 43.59 | 45.76 | 33.7712 | -118.0072 | 45.787
GWD 12290 | Girth Weld |  | 39353.41 | 43.59 | 0.312 | 42000 | ERW | 8.625 | 728 | [10 empty] | AGM 12 | 2580.35 | AGM 13 | 396.68 | 39.77 | 43.59 | 47.58 | 39.77 | 43.59 | 12290 | 45.76 | 2.77 | 33.7713 | -118.0072 | 46
GWD 12300 | Girth Weld |  | 39397 | 45.76 | 0.312 | 42000 | ERW | 8.625 | 728 | [10 empty] | AGM 12 | 2623.95 | AGM 13 | 353.09 | 43.59 | 45.76 | 39.77 | 43.59 | 45.76 | 12300 | 2.77 | 1.26 | 33.7715 | -118.0072 | 46.025
GWD 12310 | Girth Weld |  | 39442.76 | 2.77 | 0.312 | 42000 | ERW | 8.625 | 728 | [10 empty] | AGM 12 | 2669.7 | AGM 13 | 307.33 | 45.76 | 2.77 | 43.59 | 45.76 | 2.77 | 12310 | 1.26 | 23.28 | 33.7716 | -118.0072 | 46.632
GWD 12320 | Girth Weld |  | 39445.53 | 0.55 | 0.312 | 42000 | ERW | 8.625 | 728 | [10 empty] | AGM 12 | 2672.47 | AGM 13 | 304.56 | 2.77 | 1.26 | 45.76 | 2.77 | 1.26 | 12320 | 23.28 | 1.55 | 33.7716 | -118.0072 | 46.771
BND 95 | Bend |  | 39446.08 | 0.71 | 0.312 | 42000 | ERW | 8.625 | 728 |  |  | 23.388 | [7 empty] | AGM 12 | 2673.02 | AGM 13 | 304.01 | 0.55 | 0.71 | 45.76 | 2.77 | 1.26 | 12320 | 23.28 | 1.55 | 33.7716 | -118.0072 | 46.806 | 5.0D 36.5 deg left turn bend
GWD 12330 | Girth Weld |  | 39446.79 | 23.28 | 0.312 | 42000 | ERW | 8.625 | 728 | [10 empty] | AGM 12 | 2673.73 | AGM 13 | 303.31 | 1.26 | 23.28 | 2.77 | 1.26 | 23.28 | 12330 | 1.55 | 1.52 | 33.7716 | -118.0072 | 46.852
GWD 12340 | Girth Weld |  | 39470.06 | 0.34 | 0.312 | 42000 | ERW | 8.625 | 728 | [10 empty] | AGM 12 | 2697 | AGM 13 | 280.03 | 23.28 | 1.55 | 1.26 | 23.28 | 1.55 | 12340 | 1.52 | 39.64 | 33.7717 | -118.0073 | 47.975
BND 96 | Bend |  | 39470.41 | 1.21 | 0.312 | 42000 | ERW | 8.625 | 728 |  |  | 18.622 | [7 empty] | AGM 12 | 2697.35 | AGM 13 | 279.69 | 0.34 | 1.21 | 1.26 | 23.28 | 1.55 | 12340 | 1.52 | 39.64 | 33.7717 | -118.0073 | 47.975 | 3.0D 39.1 deg right turn over bend
GWD 12350 | Girth Weld |  | 39471.61 | 1.06 | 0.312 | 42000 | ERW | 8.625 | 728 | [10 empty] | AGM 12 | 2698.56 | AGM 13 | 278.48 | 1.55 | 1.52 | 23.28 | 1.55 | 1.52 | 12350 | 39.64 | 45.17 | 33.7717 | -118.0073 | 47.907
BND 97 | Bend |  | 39472.67 | 0.47 | 0.312 | 42000 | ERW | 8.625 | 728 |  |  | 18.268 | [7 empty] | AGM 12 | 2699.61 | AGM 13 | 277.42 | 1.06 | 0.47 | 23.28 | 1.55 | 1.52 | 12350 | 39.64 | 45.17 | 33.7717 | -118.0073 | 47.824 | 5.0D 36.1 deg left turn sag bend
GWD 12360 | Girth Weld |  | 39473.14 | 39.64 | 0.312 | 42000 | ERW | 8.625 | 728 | [10 empty] | AGM 12 | 2700.08 | AGM 13 | 276.95 | 1.52 | 39.64 | 1.55 | 1.52 | 39.64 | 12360 | 45.17 | 1.59 | 33.7717 | -118.0073 | 47.794
GWD 12370 | Girth Weld |  | 39512.78 | 45.17 | 0.312 | 42000 | ERW | 8.625 | 728 | [10 empty] | AGM 12 | 2739.72 | AGM 13 | 237.31 | 39.64 | 45.17 | 1.52 | 39.64 | 45.17 | 12370 | 1.59 | 1.89 | 33.7718 | -118.0074 | 46.874
GWD 12380 | Girth Weld |  | 39557.95 | 0.76 | 0.312 | 42000 | ERW | 8.625 | 728 | [10 empty] | AGM 12 | 2784.89 | AGM 13 | 192.14 | 45.17 | 1.59 | 39.64 | 45.17 | 1.59 | 12380 | 1.89 | 1.51 | 33.7719 | -118.0074 | 47.375
BND 98 | Bend |  | 39558.71 | 0.83 | 0.312 | 42000 | ERW | 8.625 | 728 |  |  | 24.544 | [7 empty] | AGM 12 | 2785.65 | AGM 13 | 191.39 | 0.76 | 0.83 | 39.64 | 45.17 | 1.59 | 12380 | 1.89 | 1.51 | 33.7719 | -118.0074 | 47.205 | 3.0D 48.7 deg left turn over bend
GWD 12390 | Girth Weld |  | 39559.54 | 1.89 | 0.312 | 42000 | ERW | 8.625 | 728 | [10 empty] | AGM 12 | 2786.48 | AGM 13 | 190.55 | 1.59 | 1.89 | 45.17 | 1.59 | 1.89 | 12390 | 1.51 | 3.6 | 33.7719 | -118.0074 | 46.732
GWD 12400 | Girth Weld |  | 39561.43 | 0.71 | 0.312 | 42000 | ERW | 8.625 | 728 | [10 empty] | AGM 12 | 2788.37 | AGM 13 | 188.66 | 1.89 | 1.51 | 1.59 | 1.89 | 1.51 | 12400 | 3.6 | 1.21 | 33.7719 | -118.0074 | 45.347
BND 99 | Bend |  | 39562.14 | 0.79 | 0.312 | 42000 | ERW | 8.625 | 728 |  |  | 24.689 | [7 empty] | AGM 12 | 2789.09 | AGM 13 | 187.95 | 0.71 | 0.79 | 1.59 | 1.89 | 1.51 | 12400 | 3.6 | 1.21 | 33.7719 | -118.0074 | 44.953 | 3.0D 47.3 deg right turn sag bend
GWD 12410 | Girth Weld |  | 39562.94 | 3.6 | 0.312 | 42000 | ERW | 8.625 | 728 | [10 empty] | AGM 12 | 2789.88 | AGM 13 | 187.15 | 1.51 | 3.6 | 1.89 | 1.51 | 3.6 | 12410 | 1.21 | 23.67 | 33.7719 | -118.0075 | 44.742
GWD 12420 | Girth Weld |  | 39566.54 | 0.48 | 0.312 | 42000 | ERW | 8.625 | 728 | [10 empty] | AGM 12 | 2793.48 | AGM 13 | 183.55 | 3.6 | 1.21 | 1.51 | 3.6 | 1.21 | 12420 | 23.67 | 2.39 | 33.7719 | -118.0075 | 44.639
BND 100 | Bend |  | 39567.02 | 0.73 | 0.312 | 42000 | ERW | 8.625 | 728 |  |  | 24.669 | [7 empty] | AGM 12 | 2793.96 | AGM 13 | 183.07 | 0.48 | 0.73 | 1.51 | 3.6 | 1.21 | 12420 | 23.67 | 2.39 | 33.7719 | -118.0075 | 44.633 | 5.0D 37.2 deg left turn sag bend
GWD 12430 | Girth Weld |  | 39567.75 | 23.67 | 0.312 | 42000 | ERW | 8.625 | 728 | [10 empty] | AGM 12 | 2794.69 | AGM 13 | 182.34 | 1.21 | 23.67 | 3.6 | 1.21 | 23.67 | 12430 | 2.39 | 1.01 | 33.7719 | -118.0075 | 44.638
GWD 12440 | Girth Weld |  | 39591.42 | 1.12 | 0.312 | 42000 | ERW | 8.625 | 728 | [10 empty] | AGM 12 | 2818.36 | AGM 13 | 158.68 | 23.67 | 2.39 | 1.21 | 23.67 | 2.39 | 12440 | 1.01 | 24.51 | 33.7719 | -118.0075 | 44.958
BND 101 | Bend |  | 39592.53 | 1.27 | 0.312 | 42000 | ERW | 8.625 | 728 |  |  | 31.401 | [7 empty] | AGM 12 | 2819.48 | AGM 13 | 157.56 | 1.12 | 1.27 | 1.21 | 23.67 | 2.39 | 12440 | 1.01 | 24.51 | 33.7719 | -118.0075 | 44.971 | 3.0D 70.7 deg right turn sag bend
GWD 12450 | Girth Weld |  | 39593.8 | 1.01 | 0.312 | 42000 | ERW | 8.625 | 728 | [10 empty] | AGM 12 | 2820.75 | AGM 13 | 156.29 | 2.39 | 1.01 | 23.67 | 2.39 | 1.01 | 12450 | 24.51 | 1.01 | 33.7719 | -118.0075 | 45.004
GWD 12460 | Girth Weld |  | 39594.81 | 24.51 | 0.219 | 42000 | ERW | 8.625 | 728 | [10 empty] | AGM 12 | 2821.76 | AGM 13 | 155.28 | 1.01 | 24.51 | 2.39 | 1.01 | 24.51 | 12460 | 1.01 | 3.1 | 33.7719 | -118.0075 | 45.032
GWD 12470 | Girth Weld |  | 39619.32 | 1.01 | 0.312 | 42000 | ERW | 8.625 | 728 | [10 empty] | AGM 12 | 2846.27 | AGM 13 | 130.77 | 24.51 | 1.01 | 1.01 | 24.51 | 1.01 | 12470 | 3.1 | 1.01 | 33.772 | -118.0075 | 45.797 | Estimated WT 0.312
GWD 12480 | Girth Weld |  | 39620.33 | 1.59 | 0.312 | 42000 | ERW | 8.625 | 728 | [10 empty] | AGM 12 | 2847.27 | AGM 13 | 129.76 | 1.01 | 3.1 | 24.51 | 1.01 | 3.1 | 12480 | 1.01 | 40.82 | 33.772 | -118.0075 | 45.838
BND 102 | Bend |  | 39621.92 | 1.51 | 0.312 | 42000 | ERW | 8.625 | 728 |  |  | 38.872 | [7 empty] | AGM 12 | 2848.86 | AGM 13 | 128.17 | 1.59 | 1.51 | 24.51 | 1.01 | 3.1 | 12480 | 1.01 | 40.82 | 33.772 | -118.0075 | 45.889 | 3.0D 89.2 deg left turn over bend
GWD 12490 | Girth Weld |  | 39623.43 | 1.01 | 0.312 | 42000 | ERW | 8.625 | 728 | [10 empty] | AGM 12 | 2850.38 | AGM 13 | 126.66 | 3.1 | 1.01 | 1.01 | 3.1 | 1.01 | 12490 | 40.82 | 41.17 | 33.772 | -118.0075 | 45.918
GWD 12500 | Girth Weld |  | 39624.44 | 40.82 | 0.219 | 42000 | ERW | 8.625 | 728 | [10 empty] | AGM 12 | 2851.38 | AGM 13 | 125.65 | 1.01 | 40.82 | 3.1 | 1.01 | 40.82 | 12500 | 41.17 | 11.26 | 33.772 | -118.0075 | 45.93
GWD 12510 | Girth Weld |  | 39665.26 | 41.17 | 0.219 | 42000 | ERW | 8.625 | 728 | [10 empty] | AGM 12 | 2892.2 | AGM 13 | 84.83 | 40.82 | 41.17 | 1.01 | 40.82 | 41.17 | 12510 | 11.26 | 12.39 | 33.772 | -118.0077 | 45.808
GWD 12520 | Girth Weld |  | 39706.43 | 11.26 | 0.219 | 42000 | ERW | 8.625 | 728 | [10 empty] | AGM 12 | 2933.37 | AGM 13 | 43.66 | 41.17 | 11.26 | 40.82 | 41.17 | 11.26 | 12520 | 12.39 | 0.96 | 33.772 | -118.0078 | 45.554
GWD 12530 | Girth Weld |  | 39717.69 | 12.39 | 0.219 | 42000 | ERW | 8.625 | 728 | [10 empty] | AGM 12 | 2944.63 | AGM 13 | 32.4 | 11.26 | 12.39 | 41.17 | 11.26 | 12.39 | 12530 | 0.96 | 3.11 | 33.772 | -118.0079 | 45.525
GWD 12540 | Girth Weld |  | 39730.08 | 0.96 | 0.312 | 42000 | ERW | 8.625 | 728 | [10 empty] | AGM 12 | 2957.02 | AGM 13 | 20.01 | 12.39 | 0.96 | 11.26 | 12.39 | 0.96 | 12540 | 3.11 | 1.01 | 33.772 | -118.0079 | 45.556 | Estimated WT 0.312
GWD 12550 | Girth Weld |  | 39731.04 | 1.56 | 0.312 | 42000 | ERW | 8.625 | 728 | [10 empty] | AGM 12 | 2957.98 | AGM 13 | 19.05 | 0.96 | 3.11 | 12.39 | 0.96 | 3.11 | 12550 | 1.01 | 20.43 | 33.772 | -118.0079 | 45.554
BND 103 | Bend |  | 39732.6 | 1.55 | 0.312 | 42000 | ERW | 8.625 | 728 |  |  | 38.164 | [7 empty] | AGM 12 | 2959.54 | AGM 13 | 17.49 | 1.56 | 1.55 | 12.39 | 0.96 | 3.11 | 12550 | 1.01 | 20.43 | 33.772 | -118.0079 | 45.553 | 3.0D 88.4 deg right turn bend
GWD 12560 | Girth Weld |  | 39734.15 | 1.01 | 0.312 | 42000 | ERW | 8.625 | 728 | [10 empty] | AGM 12 | 2961.09 | AGM 13 | 15.94 | 3.11 | 1.01 | 0.96 | 3.11 | 1.01 | 12560 | 20.43 | 41.07 | 33.772 | -118.0079 | 45.555
GWD 12570 | Girth Weld |  | 39735.16 | 14.93 | 0.219 | 42000 | ERW | 8.625 | 728 | [10 empty] | AGM 12 | 2962.1 | AGM 13 | 14.93 | 1.01 | 20.43 | 3.11 | 1.01 | 20.43 | 12570 | 41.07 | 1 | 33.772 | -118.0079 | 45.553
MRK 11 | Marker |  | 39750.09 | 5.5 | 0.219 | 42000 | ERW | 8.625 | 728 |  |  |  |  | 11:40 | [5 empty] | AGM 12 | 2977.03 | Valve 602 | 814.12 | 14.93 | 5.5 | 3.11 | 1.01 | 20.43 | 12570 | 41.07 | 1 | 33.772 | -118.0079 | 45.68 | AGM 13 12' West of Curb - Located in Estees Circle
GWD 12580 | Girth Weld |  | 39755.59 | 41.07 | 0.219 | 42000 | ERW | 8.625 | 728 | [10 empty] | AGM 13 | 5.5 | Valve 602 | 808.62 | 20.43 | 41.07 | 1.01 | 20.43 | 41.07 | 12580 | 1 | 3.1 | 33.772 | -118.0079 | 45.785
GWD 12590 | Girth Weld |  | 39796.66 | 1 | 0.312 | 42000 | ERW | 8.625 | 728 | [10 empty] | AGM 13 | 46.57 | Valve 602 | 767.55 | 41.07 | 1 | 20.43 | 41.07 | 1 | 12590 | 3.1 | 1 | 33.7722 | -118.0079 | 46.299 | Estimated WT 0.312
GWD 12600 | Girth Weld |  | 39797.66 | 1.49 | 0.312 | 42000 | ERW | 8.625 | 728 | [10 empty] | AGM 13 | 47.57 | Valve 602 | 766.55 | 1 | 3.1 | 41.07 | 1 | 3.1 | 12600 | 1 | 37.47 | 33.7722 | -118.0079 | 46.307
BND 104 | Bend |  | 39799.15 | 1.6 | 0.312 | 42000 | ERW | 8.625 | 728 |  |  | 40.139 | [7 empty] | AGM 13 | 49.06 | Valve 602 | 765.06 | 1.49 | 1.6 | 41.07 | 1 | 3.1 | 12600 | 1 | 37.47 | 33.7722 | -118.0079 | 46.299 | 3.0D 89.4 deg left turn over bend
GWD 12610 | Girth Weld |  | 39800.75 | 1 | 0.312 | 42000 | ERW | 8.625 | 728 | [10 empty] | AGM 13 | 50.66 | Valve 602 | 763.46 | 3.1 | 1 | 1 | 3.1 | 1 | 12610 | 37.47 | 30.48 | 33.7722 | -118.0079 | 46.267
GWD 12620 | Girth Weld |  | 39801.75 | 37.47 | 0.219 | 42000 | ERW | 8.625 | 728 | [10 empty] | AGM 13 | 51.66 | Valve 602 | 762.46 | 1 | 37.47 | 3.1 | 1 | 37.47 | 12620 | 30.48 | 32.12 | 33.7722 | -118.0079 | 46.24
GWD 12630 | Girth Weld |  | 39839.22 | 30.48 | 0.219 | 42000 | ERW | 8.625 | 728 | [10 empty] | AGM 13 | 89.13 | Valve 602 | 724.99 | 37.47 | 30.48 | 1 | 37.47 | 30.48 | 12630 | 32.12 | 38.26 | 33.7722 | -118.008 | 45.53
GWD 12640 | Girth Weld |  | 39869.7 | 32.12 | 0.219 | 42000 | ERW | 8.625 | 728 | [10 empty] | AGM 13 | 119.61 | Valve 602 | 694.51 | 30.48 | 32.12 | 37.47 | 30.48 | 32.12 | 12640 | 38.26 | 38.72 | 33.7722 | -118.0081 | 45.284
GWD 12650 | Girth Weld |  | 39901.82 | 38.26 | 0.219 | 42000 | ERW | 8.625 | 728 | [10 empty] | AGM 13 | 151.72 | Valve 602 | 662.4 | 32.12 | 38.26 | 30.48 | 32.12 | 38.26 | 12650 | 38.72 | 17 | 33.7722 | -118.0082 | 45.334
GWD 12660 | Girth Weld |  | 39940.08 | 38.72 | 0.219 | 42000 | ERW | 8.625 | 728 | [10 empty] | AGM 13 | 189.98 | Valve 602 | 624.14 | 38.26 | 38.72 | 32.12 | 38.26 | 38.72 | 12660 | 17 | 0.96 | 33.7722 | -118.0084 | 45.038
GWD 12670 | Girth Weld |  | 39978.8 | 17 | 0.219 | 42000 | ERW | 8.625 | 728 | [10 empty] | AGM 13 | 228.7 | Valve 602 | 585.42 | 38.72 | 17 | 38.26 | 38.72 | 17 | 12670 | 0.96 | 2.54 | 33.7722 | -118.0085 | 45.272
GWD 12680 | Girth Weld |  | 39995.8 | 0.96 | 0.28 | 42000 | ERW | 8.625 | 728 | [10 empty] | AGM 13 | 245.71 | Valve 602 | 568.41 | 17 | 0.96 | 38.72 | 17 | 0.96 | 12680 | 2.54 | 1.46 | 33.7722 | -118.0085 | 45.681
GWD 12690 | Girth Weld |  | 39996.76 | 1.23 | 0.28 | 42000 | ERW | 8.625 | 728 | [10 empty] | AGM 13 | 246.67 | Valve 602 | 567.45 | 0.96 | 2.54 | 17 | 0.96 | 2.54 | 12690 | 1.46 | 3.09 | 33.7722 | -118.0085 | 45.697
BND 105 | Bend |  | 39997.99 | 1.31 | 0.28 | 42000 | ERW | 8.625 | 728 |  |  | 33.185 | [7 empty] | AGM 13 | 247.9 | Valve 602 | 566.22 | 1.23 | 1.31 | 17 | 0.96 | 2.54 | 12690 | 1.46 | 3.09 | 33.7722 | -118.0085 | 45.743 | 3.0D 78.9 deg left turn sag bend
GWD 12700 | Girth Weld |  | 39999.3 | 1.46 | 0.28 | 42000 | ERW | 8.625 | 728 | [10 empty] | AGM 13 | 249.21 | Valve 602 | 564.91 | 2.54 | 1.46 | 0.96 | 2.54 | 1.46 | 12700 | 3.09 | 2.07 | 33.7722 | -118.0086 | 45.808
GWD 12710 | Girth Weld |  | 40000.76 | 1.54 | 0.28 | 42000 | ERW | 8.625 | 728 | [10 empty] | AGM 13 | 250.67 | Valve 602 | 563.45 | 1.46 | 3.09 | 2.54 | 1.46 | 3.09 | 12710 | 2.07 | 23.06 | 33.7722 | -118.0086 | 45.878
BND 106 | Bend |  | 40002.3 | 1.55 | 0.28 | 42000 | ERW | 8.625 | 728 |  |  | 40.963 | [7 empty] | AGM 13 | 252.21 | Valve 602 | 561.91 | 1.54 | 1.55 | 2.54 | 1.46 | 3.09 | 12710 | 2.07 | 23.06 | 33.7722 | -118.0086 | 45.936 | 3.0D 91.2 deg right turn over bend
GWD 12720 | Girth Weld |  | 40003.85 | 2.07 | 0.28 | 42000 | ERW | 8.625 | 728 | [10 empty] | AGM 13 | 253.76 | Valve 602 | 560.36 | 3.09 | 2.07 | 1.46 | 3.09 | 2.07 | 12720 | 23.06 | 43.07 | 33.7722 | -118.0086 | 45.956
GWD 12730 | Girth Weld |  | 40005.92 | 23.06 | 0.28 | 42000 | ERW | 8.625 | 728 | [10 empty] | AGM 13 | 255.83 | Valve 602 | 558.29 | 2.07 | 23.06 | 3.09 | 2.07 | 23.06 | 12730 | 43.07 | 42.32 | 33.7722 | -118.0086 | 45.941
GWD 12740 | Girth Weld |  | 40028.98 | 43.07 | 0.28 | 42000 | ERW | 8.625 | 728 | [10 empty] | AGM 13 | 278.89 | Valve 602 | 535.23 | 23.06 | 43.07 | 2.07 | 23.06 | 43.07 | 12740 | 42.32 | 38.06 | 33.7722 | -118.0086 | 45.473
GWD 12750 | Girth Weld |  | 40072.05 | 42.32 | 0.28 | 42000 | ERW | 8.625 | 728 | [10 empty] | AGM 13 | 321.96 | Valve 602 | 492.16 | 43.07 | 42.32 | 23.06 | 43.07 | 42.32 | 12750 | 38.06 | 43.12 | 33.7723 | -118.0088 | 45.235
GWD 12760 | Girth Weld |  | 40114.37 | 38.06 | 0.28 | 42000 | ERW | 8.625 | 728 | [10 empty] | AGM 13 | 364.28 | Valve 602 | 449.84 | 42.32 | 38.06 | 43.07 | 42.32 | 38.06 | 12760 | 43.12 | 42.21 | 33.7723 | -118.0089 | 44.24
GWD 12770 | Girth Weld |  | 40152.43 | 43.12 | 0.28 | 42000 | ERW | 8.625 | 728 | [10 empty] | AGM 13 | 402.34 | Valve 602 | 411.78 | 38.06 | 43.12 | 42.32 | 38.06 | 43.12 | 12770 | 42.21 | 42.64 | 33.7724 | -118.009 | 43.353
GWD 12780 | Girth Weld |  | 40195.54 | 42.21 | 0.28 | 42000 | ERW | 8.625 | 728 | [10 empty] | AGM 13 | 445.45 | Valve 602 | 368.67 | 43.12 | 42.21 | 38.06 | 43.12 | 42.21 | 12780 | 42.64 | 40.75 | 33.7724 | -118.0091 | 43.212
GWD 12790 | Girth Weld |  | 40237.75 | 42.64 | 0.28 | 42000 | ERW | 8.625 | 728 | [10 empty] | AGM 13 | 487.66 | Valve 602 | 326.46 | 42.21 | 42.64 | 43.12 | 42.21 | 42.64 | 12790 | 40.75 | 27.58 | 33.7725 | -118.0093 | 43.451
GWD 12800 | Girth Weld |  | 40280.39 | 40.75 | 0.28 | 42000 | ERW | 8.625 | 728 | [10 empty] | AGM 13 | 530.3 | Valve 602 | 283.82 | 42.64 | 40.75 | 42.21 | 42.64 | 40.75 | 12800 | 27.58 | 42.52 | 33.7725 | -118.0094 | 43.33
GWD 12810 | Girth Weld |  | 40321.14 | 27.58 | 0.28 | 42000 | ERW | 8.625 | 728 | [10 empty] | AGM 13 | 571.05 | Valve 602 | 243.07 | 40.75 | 27.58 | 42.64 | 40.75 | 27.58 | 12810 | 42.52 | 39.56 | 33.7725 | -118.0095 | 42.824
GWD 12820 | Girth Weld |  | 40348.72 | 42.52 | 0.28 | 42000 | ERW | 8.625 | 728 | [10 empty] | AGM 13 | 598.63 | Valve 602 | 215.49 | 27.58 | 42.52 | 40.75 | 27.58 | 42.52 | 12820 | 39.56 | 42.95 | 33.7726 | -118.0096 | 43.928
GWD 12830 | Girth Weld |  | 40391.24 | 39.56 | 0.28 | 42000 | ERW | 8.625 | 728 | [10 empty] | AGM 13 | 641.15 | Valve 602 | 172.98 | 42.52 | 39.56 | 27.58 | 42.52 | 39.56 | 12830 | 42.95 | 2.68 | 33.7726 | -118.0098 | 44.997
GWD 12840 | Girth Weld |  | 40430.8 | 42.95 | 0.28 | 42000 | ERW | 8.625 | 728 | [10 empty] | AGM 13 | 680.71 | Valve 602 | 133.41 | 39.56 | 42.95 | 42.52 | 39.56 | 42.95 | 12840 | 2.68 | 3.87 | 33.7726 | -118.0099 | 45.648
GWD 12850 | Girth Weld |  | 40473.75 | 2.68 | 0.28 | 42000 | ERW | 8.625 | 728 | [10 empty] | AGM 13 | 723.66 | Valve 602 | 90.46 | 42.95 | 2.68 | 39.56 | 42.95 | 2.68 | 12850 | 3.87 | 3.94 | 33.7727 | -118.01 | 46.094
GWD 12860 | Girth Weld |  | 40476.44 | 1.46 | 0.28 | 42000 | ERW | 8.625 | 728 | [10 empty] | AGM 13 | 726.34 | Valve 602 | 87.78 | 2.68 | 3.87 | 42.95 | 2.68 | 3.87 | 12860 | 3.94 | 39.19 | 33.7727 | -118.01 | 46.132
BND 107 | Bend |  | 40477.89 | 2.41 | 0.28 | 42000 | ERW | 8.625 | 728 |  |  | 48.949 | [7 empty] | AGM 13 | 727.8 | Valve 602 | 86.32 | 1.46 | 2.41 | 42.95 | 2.68 | 3.87 | 12860 | 3.94 | 39.19 | 33.7727 | -118.01 | 46.352 | 12.3D 26.7 deg left turn sag bend
GWD 12870 | Girth Weld |  | 40480.3 | 2.16 | 0.28 | 42000 | ERW | 8.625 | 728 | [10 empty] | AGM 13 | 730.21 | Valve 602 | 83.91 | 3.87 | 3.94 | 2.68 | 3.87 | 3.94 | 12870 | 39.19 | 12.91 | 33.7727 | -118.01 | 47.184
BND 108 | Bend |  | 40482.46 | 1.78 | 0.28 | 42000 | ERW | 8.625 | 728 |  |  | 41.407 | [7 empty] | AGM 13 | 732.37 | Valve 602 | 81.75 | 2.16 | 1.78 | 2.68 | 3.87 | 3.94 | 12870 | 39.19 | 12.91 | 33.7727 | -118.01 | 47.939 | 10.9D 24.5 deg over bend
GWD 12880 | Girth Weld |  | 40484.24 | 39.19 | 0.28 | 42000 | ERW | 8.625 | 728 | [10 empty] | AGM 13 | 734.15 | Valve 602 | 79.97 | 3.94 | 39.19 | 3.87 | 3.94 | 39.19 | 12880 | 12.91 | 3.94 | 33.7727 | -118.01 | 48.163
GWD 12890 | Girth Weld |  | 40523.43 | 12.91 | 0.28 | 42000 | ERW | 8.625 | 728 | [10 empty] | AGM 13 | 773.34 | Valve 602 | 40.78 | 39.19 | 12.91 | 3.94 | 39.19 | 12.91 | 12890 | 3.94 | 3.91 | 33.7727 | -118.0102 | 48.298
GWD 12900 | Girth Weld |  | 40536.34 | 1.76 | 0.28 | 42000 | ERW | 8.625 | 728 | [10 empty] | AGM 13 | 786.25 | Valve 602 | 27.87 | 12.91 | 3.94 | 39.19 | 12.91 | 3.94 | 12900 | 3.91 | 19.8 | 33.7727 | -118.0102 | 48.238
BND 109 | Bend |  | 40538.1 | 2.18 | 0.28 | 42000 | ERW | 8.625 | 728 |  |  | 43.073 | [7 empty] | AGM 13 | 788.01 | Valve 602 | 26.11 | 1.76 | 2.18 | 39.19 | 12.91 | 3.94 | 12900 | 3.91 | 19.8 | 33.7728 | -118.0102 | 48.053 | 11.0D 26.6 deg right turn over bend
GWD 12910 | Girth Weld |  | 40540.27 | 2.09 | 0.28 | 42000 | ERW | 8.625 | 728 | [10 empty] | AGM 13 | 790.18 | Valve 602 | 23.94 | 3.94 | 3.91 | 12.91 | 3.94 | 3.91 | 12910 | 19.8 | 0.48 | 33.7728 | -118.0102 | 47.32
BND 110 | Bend |  | 40542.37 | 1.82 | 0.28 | 42000 | ERW | 8.625 | 728 |  |  | 36.604 | [7 empty] | AGM 13 | 792.27 | Valve 602 | 21.85 | 2.09 | 1.82 | 12.91 | 3.94 | 3.91 | 12910 | 19.8 | 0.48 | 33.7728 | -118.0102 | 46.563 | 10.0D 23.8 deg sag bend
GWD 12920 | Girth Weld |  | 40544.18 | 8.42 | 0.28 | 42000 | ERW | 8.625 | 728 | [10 empty] | AGM 13 | 794.09 | Valve 602 | 20.03 | 3.91 | 19.8 | 3.94 | 3.91 | 19.8 | 12920 | 0.48 | 21.07 | 33.7728 | -118.0102 | 46.341
BND 111 | Bend |  | 40552.6 | 9.41 | 0.28 | 42000 | ERW | 8.625 | 728 |  |  | 72.11 | [7 empty] | AGM 13 | 802.51 | Valve 602 | 11.61 | 8.42 | 11.38 | 3.94 | 3.91 | 19.8 | 12920 | 0.48 | 21.07 | 33.7728 | -118.0102 | 46.153 | 13.8D 30.1 deg right turn sag bend
TAP 15 | TAP |  | 40562.01 | 1.97 | 0.28 | 42000 | ERW | 8.625 | 728 |  |  |  |  | 12:02 | [5 empty] | AGM 13 | 811.92 | Valve 602 | 2.2 | 17.83 | 1.97 | 3.94 | 3.91 | 19.8 | 12920 | 0.48 | 21.07 | 33.7728 | -118.0103 | 46.155
GWD 12930 | Girth Weld |  | 40563.98 | 0.23 | 0.28 | 42000 | ERW | 8.625 | 728 | [10 empty] | AGM 13 | 813.89 | Valve 602 | 0.23 | 19.8 | 0.48 | 3.91 | 19.8 | 0.48 | 12930 | 21.07 | 27.14 | 33.7728 | -118.0103 | 46.148
VLV 4 | Valve |  | 40564.21 | 0.25 | 0.28 | 42000 | ERW | 8.625 | 728 | [10 empty] | AGM 13 | 814.12 | AGM 14 | 2935.13 | 0.23 | 0.25 | 3.91 | 19.8 | 0.48 | 12930 | 21.07 | 27.14 | 33.7728 | -118.0103 | 46.148 | Valve 602 Located Inside Underground Vault at Valve Site¦Start Section CSFM 39¦End Section CSFM 1305
GWD 12940 | Girth Weld |  | 40564.46 | 0.44 | 0.28 | 35000 | ERW | 8.625 | 600 | [10 empty] | Valve 602 | 0.25 | AGM 14 | 2934.88 | 0.48 | 21.07 | 19.8 | 0.48 | 21.07 | 12940 | 27.14 | 28.88 | 33.7728 | -118.0103 | 46.149
TAP 16 | TAP |  | 40564.9 | 20.63 | 0.28 | 35000 | ERW | 8.625 | 600 |  |  |  |  | 11:40 | [5 empty] | Valve 602 | 0.69 | AGM 14 | 2934.44 | 0.44 | 20.63 | 19.8 | 0.48 | 21.07 | 12940 | 27.14 | 28.88 | 33.7728 | -118.0103 | 46.151
GWD 12950 | Girth Weld |  | 40585.53 | 27.14 | 0.25 | 35000 | ERW | 8.625 | 600 | [10 empty] | Valve 602 | 21.32 | AGM 14 | 2913.8 | 21.07 | 27.14 | 0.48 | 21.07 | 27.14 | 12950 | 28.88 | 41.33 | 33.7728 | -118.0103 | 46.244 | Estimated WT 0.250
GWD 12960 | Girth Weld |  | 40612.67 | 28.88 | 0.28 | 35000 | ERW | 8.625 | 600 | [10 empty] | Valve 602 | 48.46 | AGM 14 | 2886.67 | 27.14 | 28.88 | 21.07 | 27.14 | 28.88 | 12960 | 41.33 | 43.21 | 33.7729 | -118.0104 | 46.35
GWD 12970 | Girth Weld |  | 40641.55 | 41.33 | 0.28 | 35000 | ERW | 8.625 | 600 | [10 empty] | Valve 602 | 77.34 | AGM 14 | 2857.78 | 28.88 | 41.33 | 27.14 | 28.88 | 41.33 | 12970 | 43.21 | 37.74 | 33.773 | -118.0104 | 46.493
GWD 12980 | Girth Weld |  | 40682.88 | 43.21 | 0.28 | 35000 | ERW | 8.625 | 600 | [10 empty] | Valve 602 | 118.67 | AGM 14 | 2816.45 | 41.33 | 43.21 | 28.88 | 41.33 | 43.21 | 12980 | 37.74 | 44.66 | 33.7731 | -118.0105 | 46.63
GWD 12990 | Girth Weld |  | 40726.09 | 37.74 | 0.28 | 35000 | ERW | 8.625 | 600 | [10 empty] | Valve 602 | 161.88 | AGM 14 | 2773.25 | 43.21 | 37.74 | 41.33 | 43.21 | 37.74 | 12990 | 44.66 | 41.42 | 33.7732 | -118.0106 | 46.875
GWD 13000 | Girth Weld |  | 40763.83 | 44.66 | 0.25 | 35000 | ERW | 8.625 | 600 | [10 empty] | Valve 602 | 199.62 | AGM 14 | 2735.51 | 37.74 | 44.66 | 43.21 | 37.74 | 44.66 | 13000 | 41.42 | 10.73 | 33.7733 | -118.0106 | 47.198 | Estimated WT 0.250
GWD 13010 | Girth Weld |  | 40808.49 | 41.42 | 0.25 | 35000 | ERW | 8.625 | 600 | [10 empty] | Valve 602 | 244.28 | AGM 14 | 2690.85 | 44.66 | 41.42 | 37.74 | 44.66 | 41.42 | 13010 | 10.73 | 43.29 | 33.7734 | -118.0107 | 47.27
GWD 13020 | Girth Weld |  | 40849.91 | 10.73 | 0.25 | 35000 | ERW | 8.625 | 600 | [10 empty] | Valve 602 | 285.7 | AGM 14 | 2649.43 | 41.42 | 10.73 | 44.66 | 41.42 | 10.73 | 13020 | 43.29 | 40.91 | 33.7735 | -118.0108 | 47.403
GWD 13030 | Girth Weld |  | 40860.64 | 43.29 | 0.25 | 35000 | ERW | 8.625 | 600 | [10 empty] | Valve 602 | 296.43 | AGM 14 | 2638.7 | 10.73 | 43.29 | 41.42 | 10.73 | 43.29 | 13030 | 40.91 | 48.18 | 33.7735 | -118.0108 | 47.597
GWD 13040 | Girth Weld |  | 40903.92 | 40.91 | 0.25 | 35000 | ERW | 8.625 | 600 | [10 empty] | Valve 602 | 339.71 | AGM 14 | 2595.41 | 43.29 | 40.91 | 10.73 | 43.29 | 40.91 | 13040 | 48.18 | 1.15 | 33.7736 | -118.0109 | 47.657
GWD 13050 | Girth Weld |  | 40944.84 | 48.18 | 0.25 | 35000 | ERW | 8.625 | 600 | [10 empty] | Valve 602 | 380.62 | AGM 14 | 2554.5 | 40.91 | 48.18 | 43.29 | 40.91 | 48.18 | 13050 | 1.15 | 38.42 | 33.7737 | -118.011 | 47.86
GWD 13060 | Girth Weld |  | 40993.02 | 0.51 | 0.25 | 35000 | ERW | 8.625 | 600 | [10 empty] | Valve 602 | 428.81 | AGM 14 | 2506.32 | 48.18 | 1.15 | 40.91 | 48.18 | 1.15 | 13060 | 38.42 | 47.1 | 33.7738 | -118.011 | 47.764
BND 112 | Bend |  | 40993.53 | 0.64 | 0.25 | 35000 | ERW | 8.625 | 600 |  |  | 23.429 | [7 empty] | Valve 602 | 429.32 | AGM 14 | 2505.81 | 0.51 | 0.64 | 40.91 | 48.18 | 1.15 | 13060 | 38.42 | 47.1 | 33.7738 | -118.011 | 47.748 | 5.0D 36.4 deg right turn sag bend
GWD 13070 | Girth Weld |  | 40994.17 | 2.56 | 0.25 | 35000 | ERW | 8.625 | 600 | [10 empty] | Valve 602 | 429.96 | AGM 14 | 2505.17 | 1.15 | 38.42 | 48.18 | 1.15 | 38.42 | 13070 | 47.1 | 36.52 | 33.7738 | -118.011 | 47.732
CSG 8 | Casing Start |  | 40996.72 | 35.86 | 0.25 | 35000 | ERW | 8.625 | 600 |  |  | 756.352 | [7 empty] | Valve 602 | 432.51 | AGM 14 | 2502.61 | 2.56 | 35.86 | 48.18 | 1.15 | 38.42 | 13070 | 47.1 | 36.52 | 33.7738 | -118.011 | 47.699 | Casing - Start
GWD 13080 | Girth Weld |  | 41032.58 | 21.27 | 0.25 | 35000 | ERW | 8.625 | 600 | [10 empty] | Valve 602 | 468.37 | AGM 14 | 2466.75 | 38.42 | 47.1 | 1.15 | 38.42 | 47.1 | 13080 | 36.52 | 24.78 | 33.7739 | -118.011 | 47.525
MOB 6 | Metal Object |  | 41053.85 | 5.91 | 0.25 | 35000 | ERW | 8.625 | 600 |  |  | 134.382 | 23.692 | 11:06 | [5 empty] | Valve 602 | 489.64 | AGM 14 | 2445.49 | 21.27 | 25.83 | 1.15 | 38.42 | 47.1 | 13080 | 36.52 | 24.78 | 33.7739 | -118.011 | 47.46 | Close Metal Object
CSG 8 | Casing End |  | 41059.75 | 19.93 | 0.25 | 35000 | ERW | 8.625 | 600 | [10 empty] | Valve 602 | 495.54 | AGM 14 | 2439.58 | 27.17 | 19.93 | 1.15 | 38.42 | 47.1 | 13080 | 36.52 | 24.78 | 33.774 | -118.011 | 47.501 | Casing - End
GWD 13090 | Girth Weld |  | 41079.68 | 36.52 | 0.25 | 35000 | ERW | 8.625 | 600 | [10 empty] | Valve 602 | 515.47 | AGM 14 | 2419.66 | 47.1 | 36.52 | 38.42 | 47.1 | 36.52 | 13090 | 24.78 | 41.05 | 33.774 | -118.011 | 47.828
GWD 13100 | Girth Weld |  | 41116.2 | 24.78 | 0.25 | 35000 | ERW | 8.625 | 600 | [10 empty] | Valve 602 | 551.98 | AGM 14 | 2383.14 | 36.52 | 24.78 | 47.1 | 36.52 | 24.78 | 13100 | 41.05 | 41.29 | 33.7741 | -118.011 | 48.261
GWD 13110 | Girth Weld |  | 41140.98 | 4.03 | 0.312 | 35000 | ERW | 8.625 | 600 | [10 empty] | Valve 602 | 576.76 | AGM 14 | 2358.36 | 24.78 | 41.05 | 36.52 | 24.78 | 41.05 | 13110 | 41.29 | 43.4 | 33.7742 | -118.011 | 48.382 | Estimated WT 0.312
CSG 9 | Casing Start |  | 41145 | 37.02 | 0.312 | 35000 | ERW | 8.625 | 600 |  |  | 3044.646 | [7 empty] | Valve 602 | 580.79 | AGM 14 | 2354.33 | 4.03 | 37.02 | 36.52 | 24.78 | 41.05 | 13110 | 41.29 | 43.4 | 33.7742 | -118.011 | 48.433 | Casing - Start
GWD 13120 | Girth Weld |  | 41182.02 | 41.29 | 0.312 | 35000 | ERW | 8.625 | 600 | [10 empty] | Valve 602 | 617.81 | AGM 14 | 2317.31 | 41.05 | 41.29 | 24.78 | 41.05 | 41.29 | 13120 | 43.4 | 6.13 | 33.7743 | -118.011 | 48.656
GWD 13130 | Girth Weld |  | 41223.32 | 43.4 | 0.312 | 35000 | ERW | 8.625 | 600 | [10 empty] | Valve 602 | 659.1 | AGM 14 | 2276.02 | 41.29 | 43.4 | 41.05 | 41.29 | 43.4 | 13130 | 6.13 | 36.2 | 33.7744 | -118.011 | 48.939
GWD 13140 | Girth Weld |  | 41266.72 | 6.13 | 0.312 | 35000 | ERW | 8.625 | 600 | [10 empty] | Valve 602 | 702.51 | AGM 14 | 2232.62 | 43.4 | 6.13 | 41.29 | 43.4 | 6.13 | 13140 | 36.2 | 43.82 | 33.7745 | -118.011 | 48.963
GWD 13150 | Girth Weld |  | 41272.85 | 36.2 | 0.312 | 35000 | ERW | 8.625 | 600 | [10 empty] | Valve 602 | 708.64 | AGM 14 | 2226.49 | 6.13 | 36.2 | 43.4 | 6.13 | 36.2 | 13150 | 43.82 | 42.23 | 33.7745 | -118.011 | 48.986
GWD 13160 | Girth Weld |  | 41309.05 | 43.82 | 0.312 | 35000 | ERW | 8.625 | 600 | [10 empty] | Valve 602 | 744.84 | AGM 14 | 2190.28 | 36.2 | 43.82 | 6.13 | 36.2 | 43.82 | 13160 | 42.23 | 10.47 | 33.7746 | -118.011 | 49.088
GWD 13170 | Girth Weld |  | 41352.88 | 42.23 | 0.312 | 35000 | ERW | 8.625 | 600 | [10 empty] | Valve 602 | 788.67 | AGM 14 | 2146.46 | 43.82 | 42.23 | 36.2 | 43.82 | 42.23 | 13170 | 10.47 | 10.77 | 33.7748 | -118.011 | 48.981
GWD 13180 | Girth Weld |  | 41395.1 | 3.62 | 0.312 | 35000 | ERW | 8.625 | 600 | [10 empty] | Valve 602 | 830.89 | AGM 14 | 2104.23 | 42.23 | 10.47 | 43.82 | 42.23 | 10.47 | 13180 | 10.77 | 17.76 | 33.7749 | -118.011 | 49.092
CSG 9 | Casing End |  | 41398.72 | 6.85 | 0.312 | 35000 | ERW | 8.625 | 600 | [10 empty] | Valve 602 | 834.51 | AGM 14 | 2100.61 | 3.62 | 6.85 | 43.82 | 42.23 | 10.47 | 13180 | 10.77 | 17.76 | 33.7749 | -118.011 | 49.112 | Casing - End
GWD 13190 | Girth Weld |  | 41405.58 | 10.77 | 0.312 | 35000 | ERW | 8.625 | 600 | [10 empty] | Valve 602 | 841.37 | AGM 14 | 2093.76 | 10.47 | 10.77 | 42.23 | 10.47 | 10.77 | 13190 | 17.76 | 1.54 | 33.7749 | -118.011 | 49.153
GWD 13200 | Girth Weld |  | 41416.35 | 17.76 | 0.312 | 35000 | ERW | 8.625 | 600 | [10 empty] | Valve 602 | 852.14 | AGM 14 | 2082.99 | 10.77 | 17.76 | 10.47 | 10.77 | 17.76 | 13200 | 1.54 | 3.55 | 33.7749 | -118.011 | 49.145
GWD 13210 | Girth Weld |  | 41434.11 | 0.67 | 0.312 | 35000 | ERW | 8.625 | 600 | [10 empty] | Valve 602 | 869.9 | AGM 14 | 2065.23 | 17.76 | 1.54 | 10.77 | 17.76 | 1.54 | 13210 | 3.55 | 1.53 | 33.775 | -118.011 | 48.858
BND 113 | Bend |  | 41434.78 | 0.87 | 0.312 | 35000 | ERW | 8.625 | 600 |  |  | 24.497 | [7 empty] | Valve 602 | 870.57 | AGM 14 | 2064.56 | 0.67 | 0.87 | 10.77 | 17.76 | 1.54 | 13210 | 3.55 | 1.53 | 33.775 | -118.011 | 48.855 | 3.0D 47.3 deg right turn sag bend
GWD 13220 | Girth Weld |  | 41435.65 | 3.55 | 0.312 | 35000 | ERW | 8.625 | 600 | [10 empty] | Valve 602 | 871.44 | AGM 14 | 2063.69 | 1.54 | 3.55 | 17.76 | 1.54 | 3.55 | 13220 | 1.53 | 1.02 | 33.775 | -118.011 | 48.859
GWD 13230 | Girth Weld |  | 41439.2 | 0.78 | 0.312 | 35000 | ERW | 8.625 | 600 | [10 empty] | Valve 602 | 874.99 | AGM 14 | 2060.13 | 3.55 | 1.53 | 1.54 | 3.55 | 1.53 | 13230 | 1.02 | 1.67 | 33.775 | -118.011 | 48.85
BND 114 | Bend |  | 41439.98 | 0.75 | 0.312 | 35000 | ERW | 8.625 | 600 |  |  | 23.713 | [7 empty] | Valve 602 | 875.77 | AGM 14 | 2059.36 | 0.78 | 0.75 | 1.54 | 3.55 | 1.53 | 13230 | 1.02 | 1.67 | 33.775 | -118.011 | 49.009 | 3.0D 49.5 deg left turn sag bend
GWD 13240 | Girth Weld |  | 41440.73 | 1.02 | 0.312 | 35000 | ERW | 8.625 | 600 | [10 empty] | Valve 602 | 876.52 | AGM 14 | 2058.6 | 1.53 | 1.02 | 3.55 | 1.53 | 1.02 | 13240 | 1.67 | 30.65 | 33.775 | -118.011 | 49.39
GWD 13250 | Girth Weld |  | 41441.76 | 0.91 | 0.312 | 35000 | ERW | 8.625 | 600 | [10 empty] | Valve 602 | 877.54 | AGM 14 | 2057.58 | 1.02 | 1.67 | 1.53 | 1.02 | 1.67 | 13250 | 30.65 | 1.6 | 33.775 | -118.011 | 50.107
BND 115 | Bend |  | 41442.67 | 0.76 | 0.312 | 35000 | ERW | 8.625 | 600 |  |  | 23.993 | [7 empty] | Valve 602 | 878.46 | AGM 14 | 2056.67 | 0.91 | 0.76 | 1.53 | 1.02 | 1.67 | 13250 | 30.65 | 1.6 | 33.775 | -118.011 | 50.605 | 3.0D 47.0 deg right turn over bend
GWD 13260 | Girth Weld |  | 41443.43 | 30.65 | 0.312 | 35000 | ERW | 8.625 | 600 | [10 empty] | Valve 602 | 879.21 | AGM 14 | 2055.91 | 1.67 | 30.65 | 1.02 | 1.67 | 30.65 | 13260 | 1.6 | 1.95 | 33.775 | -118.011 | 50.776
GWD 13270 | Girth Weld |  | 41474.08 | 0.78 | 0.312 | 35000 | ERW | 8.625 | 600 | [10 empty] | Valve 602 | 909.86 | AGM 14 | 2025.26 | 30.65 | 1.6 | 1.67 | 30.65 | 1.6 | 13270 | 1.95 | 1.47 | 33.7751 | -118.0109 | 50.655
BND 116 | Bend |  | 41474.86 | 0.82 | 0.312 | 35000 | ERW | 8.625 | 600 |  |  | 25.434 | [7 empty] | Valve 602 | 910.64 | AGM 14 | 2024.48 | 0.78 | 0.82 | 1.67 | 30.65 | 1.6 | 13270 | 1.95 | 1.47 | 33.7751 | -118.0109 | 50.492 | 3.0D 48.7 deg over bend
GWD 13280 | Girth Weld |  | 41475.68 | 1.95 | 0.312 | 35000 | ERW | 8.625 | 600 | [10 empty] | Valve 602 | 911.46 | AGM 14 | 2023.66 | 1.6 | 1.95 | 30.65 | 1.6 | 1.95 | 13280 | 1.47 | 18.34 | 33.7751 | -118.0109 | 50.05
GWD 13290 | Girth Weld |  | 41477.63 | 0.91 | 0.312 | 35000 | ERW | 8.625 | 600 | [10 empty] | Valve 602 | 913.41 | AGM 14 | 2021.71 | 1.95 | 1.47 | 1.6 | 1.95 | 1.47 | 13290 | 18.34 | 2.05 | 33.7751 | -118.0109 | 48.634
BND 117 | Bend |  | 41478.54 | 0.57 | 0.312 | 35000 | ERW | 8.625 | 600 |  |  | 25.716 | [7 empty] | Valve 602 | 914.32 | AGM 14 | 2020.8 | 0.91 | 0.57 | 1.6 | 1.95 | 1.47 | 13290 | 18.34 | 2.05 | 33.7751 | -118.0109 | 48.122 | 3.0D 47.7 deg sag bend
GWD 13300 | Girth Weld |  | 41479.1 | 18.34 | 0.312 | 35000 | ERW | 8.625 | 600 | [10 empty] | Valve 602 | 914.89 | AGM 14 | 2020.24 | 1.47 | 18.34 | 1.95 | 1.47 | 18.34 | 13300 | 2.05 | 41.91 | 33.7751 | -118.0109 | 47.962
GWD 13310 | Girth Weld |  | 41497.44 | 0.94 | 0.312 | 35000 | ERW | 8.625 | 600 | [10 empty] | Valve 602 | 933.23 | AGM 14 | 2001.9 | 18.34 | 2.05 | 1.47 | 18.34 | 2.05 | 13310 | 41.91 | 42.17 | 33.7751 | -118.0109 | 47.812
BND 118 | Bend |  | 41498.38 | 1.12 | 0.312 | 35000 | ERW | 8.625 | 600 |  |  | 27.912 | [7 empty] | Valve 602 | 934.16 | AGM 14 | 2000.96 | 0.94 | 1.12 | 1.47 | 18.34 | 2.05 | 13310 | 41.91 | 42.17 | 33.7751 | -118.0109 | 47.802 | 3.0D 60.8 deg left turn bend
GWD 13320 | Girth Weld |  | 41499.49 | 41.91 | 0.312 | 35000 | ERW | 8.625 | 600 | [10 empty] | Valve 602 | 935.28 | AGM 14 | 1999.85 | 2.05 | 41.91 | 18.34 | 2.05 | 41.91 | 13320 | 42.17 | 42.8 | 33.7751 | -118.0109 | 47.786
GWD 13330 | Girth Weld |  | 41541.4 | 42.17 | 0.312 | 35000 | ERW | 8.625 | 600 | [10 empty] | Valve 602 | 977.19 | AGM 14 | 1957.93 | 41.91 | 42.17 | 2.05 | 41.91 | 42.17 | 13330 | 42.8 | 19.04 | 33.7752 | -118.0109 | 48.106
GWD 13340 | Girth Weld |  | 41583.58 | 42.8 | 0.312 | 35000 | ERW | 8.625 | 600 | [10 empty] | Valve 602 | 1019.37 | AGM 14 | 1915.76 | 42.17 | 42.8 | 41.91 | 42.17 | 42.8 | 13340 | 19.04 | 15.61 | 33.7753 | -118.011 | 48.181
GWD 13350 | Girth Weld |  | 41626.37 | 19.04 | 0.312 | 35000 | ERW | 8.625 | 600 | [10 empty] | Valve 602 | 1062.16 | AGM 14 | 1872.96 | 42.8 | 19.04 | 42.17 | 42.8 | 19.04 | 13350 | 15.61 | 0.52 | 33.7755 | -118.011 | 48.67
GWD 13360 | Girth Weld |  | 41645.41 | 15.61 | 0.312 | 35000 | ERW | 8.625 | 600 | [10 empty] | Valve 602 | 1081.2 | AGM 14 | 1853.93 | 19.04 | 15.61 | 42.8 | 19.04 | 15.61 | 13360 | 0.52 | 1 | 33.7755 | -118.011 | 48.929
GWD 13370 | Girth Weld |  | 41661.02 | 0.2 | 0.312 | 35000 | ERW | 8.625 | 600 | [10 empty] | Valve 602 | 1096.81 | AGM 14 | 1838.32 | 15.61 | 0.52 | 19.04 | 15.61 | 0.52 | 13370 | 1 | 21.6 | 33.7755 | -118.011 | 49.233
BND 119 | Bend |  | 41661.22 | 0.33 | 0.312 | 35000 | ERW | 8.625 | 600 |  |  | 6.26 | [7 empty] | Valve 602 | 1097 | AGM 14 | 1838.12 | 0.2 | 0.33 | 19.04 | 15.61 | 0.52 | 13370 | 1 | 21.6 | 33.7755 | -118.011 | 49.239 | 3.0D 17.5 deg right turn over bend
GWD 13380 | Girth Weld |  | 41661.54 | 1 | 0.312 | 35000 | ERW | 8.625 | 600 | [10 empty] | Valve 602 | 1097.33 | AGM 14 | 1837.8 | 0.52 | 1 | 15.61 | 0.52 | 1 | 13380 | 21.6 | 48.25 | 33.7755 | -118.011 | 49.247
GWD 13390 | Girth Weld |  | 41662.54 | 21.6 | 0.219 | 35000 | ERW | 8.625 | 600 | [10 empty] | Valve 602 | 1098.33 | AGM 14 | 1836.8 | 1 | 21.6 | 0.52 | 1 | 21.6 | 13390 | 48.25 | 48.02 | 33.7755 | -118.011 | 49.261
GWD 13400 | Girth Weld |  | 41684.14 | 48.25 | 0.25 | 35000 | ERW | 8.625 | 600 | [10 empty] | Valve 602 | 1119.93 | AGM 14 | 1815.2 | 21.6 | 48.25 | 1 | 21.6 | 48.25 | 13400 | 48.02 | 48.22 | 33.7756 | -118.011 | 49.635 | Estimated WT 0.250
GWD 13410 | Girth Weld |  | 41732.39 | 48.02 | 0.25 | 35000 | ERW | 8.625 | 600 | [10 empty] | Valve 602 | 1168.18 | AGM 14 | 1766.95 | 48.25 | 48.02 | 21.6 | 48.25 | 48.02 | 13410 | 48.22 | 48.35 | 33.7757 | -118.011 | 50.142
GWD 13420 | Girth Weld |  | 41780.41 | 48.22 | 0.25 | 35000 | ERW | 8.625 | 600 | [10 empty] | Valve 602 | 1216.2 | AGM 14 | 1718.93 | 48.02 | 48.22 | 48.25 | 48.02 | 48.22 | 13420 | 48.35 | 48.09 | 33.7759 | -118.011 | 50.213
GWD 13430 | Girth Weld |  | 41828.63 | 48.35 | 0.25 | 35000 | ERW | 8.625 | 600 | [10 empty] | Valve 602 | 1264.42 | AGM 14 | 1670.71 | 48.22 | 48.35 | 48.02 | 48.22 | 48.35 | 13430 | 48.09 | 48.22 | 33.776 | -118.011 | 50.497
GWD 13440 | Girth Weld |  | 41876.99 | 48.09 | 0.25 | 35000 | ERW | 8.625 | 600 | [10 empty] | Valve 602 | 1312.77 | AGM 14 | 1622.35 | 48.35 | 48.09 | 48.22 | 48.35 | 48.09 | 13440 | 48.22 | 47.5 | 33.7761 | -118.011 | 51.025
GWD 13450 | Girth Weld |  | 41925.08 | 48.22 | 0.25 | 35000 | ERW | 8.625 | 600 | [10 empty] | Valve 602 | 1360.87 | AGM 14 | 1574.26 | 48.09 | 48.22 | 48.35 | 48.09 | 48.22 | 13450 | 47.5 | 48.23 | 33.7763 | -118.011 | 51.338
GWD 13460 | Girth Weld |  | 41973.29 | 47.5 | 0.25 | 35000 | ERW | 8.625 | 600 | [10 empty] | Valve 602 | 1409.08 | AGM 14 | 1526.04 | 48.22 | 47.5 | 48.09 | 48.22 | 47.5 | 13460 | 48.23 | 48.26 | 33.7764 | -118.011 | 51.485
GWD 13470 | Girth Weld |  | 42020.79 | 48.23 | 0.25 | 35000 | ERW | 8.625 | 600 | [10 empty] | Valve 602 | 1456.58 | AGM 14 | 1478.55 | 47.5 | 48.23 | 48.22 | 47.5 | 48.23 | 13470 | 48.26 | 48.17 | 33.7765 | -118.011 | 52.228
GWD 13480 | Girth Weld |  | 42069.02 | 48.26 | 0.25 | 35000 | ERW | 8.625 | 600 | [10 empty] | Valve 602 | 1504.8 | AGM 14 | 1430.32 | 48.23 | 48.26 | 47.5 | 48.23 | 48.26 | 13480 | 48.17 | 47.77 | 33.7767 | -118.011 | 53.234
GWD 13490 | Girth Weld |  | 42117.28 | 48.17 | 0.25 | 35000 | ERW | 8.625 | 600 | [10 empty] | Valve 602 | 1553.07 | AGM 14 | 1382.06 | 48.26 | 48.17 | 48.23 | 48.26 | 48.17 | 13490 | 47.77 | 47.05 | 33.7768 | -118.011 | 52.781
GWD 13500 | Girth Weld |  | 42165.45 | 47.77 | 0.25 | 35000 | ERW | 8.625 | 600 | [10 empty] | Valve 602 | 1601.24 | AGM 14 | 1333.89 | 48.17 | 47.77 | 48.26 | 48.17 | 47.77 | 13500 | 47.05 | 45.94 | 33.7769 | -118.011 | 53.273
GWD 13510 | Girth Weld |  | 42213.22 | 47.05 | 0.25 | 35000 | ERW | 8.625 | 600 | [10 empty] | Valve 602 | 1649.01 | AGM 14 | 1286.11 | 47.77 | 47.05 | 48.17 | 47.77 | 47.05 | 13510 | 45.94 | 0.98 | 33.7771 | -118.011 | 53.457
GWD 13520 | Girth Weld |  | 42260.27 | 45.94 | 0.25 | 35000 | ERW | 8.625 | 600 | [10 empty] | Valve 602 | 1696.06 | AGM 14 | 1239.07 | 47.05 | 45.94 | 47.77 | 47.05 | 45.94 | 13520 | 0.98 | 0.75 | 33.7772 | -118.011 | 53.237
GWD 13530 | Girth Weld |  | 42306.21 | 0.98 | 0.28 | 35000 | ERW | 8.625 | 600 | [10 empty] | Valve 602 | 1742 | AGM 14 | 1193.12 | 45.94 | 0.98 | 47.05 | 45.94 | 0.98 | 13530 | 0.75 | 21.06 | 33.7773 | -118.011 | 52.37
GWD 13540 | Girth Weld |  | 42307.2 | 0.15 | 0.28 | 35000 | ERW | 8.625 | 600 | [10 empty] | Valve 602 | 1742.98 | AGM 14 | 1192.14 | 0.98 | 0.75 | 45.94 | 0.98 | 0.75 | 13540 | 21.06 | 40.98 | 33.7773 | -118.011 | 52.37
BND 120 | Bend |  | 42307.35 | 0.6 | 0.28 | 35000 | ERW | 8.625 | 600 |  |  | 8.976 | [7 empty] | Valve 602 | 1743.13 | AGM 14 | 1191.99 | 0.15 | 0.6 | 45.94 | 0.98 | 0.75 | 13540 | 21.06 | 40.98 | 33.7773 | -118.011 | 52.371 | 3.0D 25.7 deg right turn bend
GWD 13550 | Girth Weld |  | 42307.94 | 21.06 | 0.28 | 35000 | ERW | 8.625 | 600 | [10 empty] | Valve 602 | 1743.73 | AGM 14 | 1191.39 | 0.75 | 21.06 | 0.98 | 0.75 | 21.06 | 13550 | 40.98 | 41.11 | 33.7773 | -118.011 | 52.369
GWD 13560 | Girth Weld |  | 42329 | 40.98 | 0.28 | 35000 | ERW | 8.625 | 600 | [10 empty] | Valve 602 | 1764.79 | AGM 14 | 1170.34 | 21.06 | 40.98 | 0.75 | 21.06 | 40.98 | 13560 | 41.11 | 42.58 | 33.7774 | -118.011 | 52.36
GWD 13570 | Girth Weld |  | 42369.98 | 41.11 | 0.28 | 35000 | ERW | 8.625 | 600 | [10 empty] | Valve 602 | 1805.77 | AGM 14 | 1129.36 | 40.98 | 41.11 | 21.06 | 40.98 | 41.11 | 13570 | 42.58 | 43.07 | 33.7775 | -118.0109 | 52.184
GWD 13580 | Girth Weld |  | 42411.09 | 42.58 | 0.28 | 35000 | ERW | 8.625 | 600 | [10 empty] | Valve 602 | 1846.87 | AGM 14 | 1088.25 | 41.11 | 42.58 | 40.98 | 41.11 | 42.58 | 13580 | 43.07 | 42.55 | 33.7776 | -118.0109 | 52.133
GWD 13590 | Girth Weld |  | 42453.67 | 43.07 | 0.28 | 35000 | ERW | 8.625 | 600 | [10 empty] | Valve 602 | 1889.46 | AGM 14 | 1045.67 | 42.58 | 43.07 | 41.11 | 42.58 | 43.07 | 13590 | 42.55 | 42.54 | 33.7777 | -118.0108 | 52.223
GWD 13600 | Girth Weld |  | 42496.74 | 42.55 | 0.28 | 35000 | ERW | 8.625 | 600 | [10 empty] | Valve 602 | 1932.53 | AGM 14 | 1002.6 | 43.07 | 42.55 | 42.58 | 43.07 | 42.55 | 13600 | 42.54 | 1.56 | 33.7778 | -118.0108 | 51.953
GWD 13610 | Girth Weld |  | 42539.29 | 42.54 | 0.28 | 35000 | ERW | 8.625 | 600 | [10 empty] | Valve 602 | 1975.08 | AGM 14 | 960.05 | 42.55 | 42.54 | 43.07 | 42.55 | 42.54 | 13610 | 1.56 | 41.39 | 33.7779 | -118.0107 | 52.806
GWD 13620 | Girth Weld |  | 42581.83 | 0.69 | 0.28 | 35000 | ERW | 8.625 | 600 | [10 empty] | Valve 602 | 2017.62 | AGM 14 | 917.51 | 42.54 | 1.56 | 42.55 | 42.54 | 1.56 | 13620 | 41.39 | 42.25 | 33.778 | -118.0107 | 52.663
BND 121 | Bend |  | 42582.52 | 0.87 | 0.28 | 35000 | ERW | 8.625 | 600 |  |  | 25.197 | [7 empty] | Valve 602 | 2018.31 | AGM 14 | 916.81 | 0.69 | 0.87 | 42.55 | 42.54 | 1.56 | 13620 | 41.39 | 42.25 | 33.778 | -118.0107 | 52.656 | 3.0D 46.9 deg left turn bend
GWD 13630 | Girth Weld |  | 42583.39 | 41.39 | 0.28 | 35000 | ERW | 8.625 | 600 | [10 empty] | Valve 602 | 2019.18 | AGM 14 | 915.95 | 1.56 | 41.39 | 42.54 | 1.56 | 41.39 | 13630 | 42.25 | 42.47 | 33.778 | -118.0107 | 52.647
GWD 13640 | Girth Weld |  | 42624.78 | 42.25 | 0.28 | 35000 | ERW | 8.625 | 600 | [10 empty] | Valve 602 | 2060.57 | AGM 14 | 874.56 | 41.39 | 42.25 | 1.56 | 41.39 | 42.25 | 13640 | 42.47 | 42.69 | 33.7781 | -118.0107 | 52.825
GWD 13650 | Girth Weld |  | 42667.03 | 42.47 | 0.28 | 35000 | ERW | 8.625 | 600 | [10 empty] | Valve 602 | 2102.82 | AGM 14 | 832.31 | 42.25 | 42.47 | 41.39 | 42.25 | 42.47 | 13650 | 42.69 | 42.14 | 33.7782 | -118.0108 | 53.071
GWD 13660 | Girth Weld |  | 42709.5 | 42.69 | 0.28 | 35000 | ERW | 8.625 | 600 | [10 empty] | Valve 602 | 2145.29 | AGM 14 | 789.84 | 42.47 | 42.69 | 42.25 | 42.47 | 42.69 | 13660 | 42.14 | 42.74 | 33.7783 | -118.0108 | 53.18
GWD 13670 | Girth Weld |  | 42752.18 | 42.14 | 0.28 | 35000 | ERW | 8.625 | 600 | [10 empty] | Valve 602 | 2187.97 | AGM 14 | 747.15 | 42.69 | 42.14 | 42.47 | 42.69 | 42.14 | 13670 | 42.74 | 42.12 | 33.7785 | -118.0108 | 53.182
GWD 13680 | Girth Weld |  | 42794.32 | 42.74 | 0.28 | 35000 | ERW | 8.625 | 600 | [10 empty] | Valve 602 | 2230.11 | AGM 14 | 705.02 | 42.14 | 42.74 | 42.69 | 42.14 | 42.74 | 13680 | 42.12 | 41.41 | 33.7786 | -118.0109 | 53.193
GWD 13690 | Girth Weld |  | 42837.06 | 42.12 | 0.28 | 35000 | ERW | 8.625 | 600 | [10 empty] | Valve 602 | 2272.85 | AGM 14 | 662.27 | 42.74 | 42.12 | 42.14 | 42.74 | 42.12 | 13690 | 41.41 | 42.39 | 33.7787 | -118.0109 | 53.18
GWD 13700 | Girth Weld |  | 42879.18 | 41.41 | 0.28 | 35000 | ERW | 8.625 | 600 | [10 empty] | Valve 602 | 2314.97 | AGM 14 | 620.15 | 42.12 | 41.41 | 42.74 | 42.12 | 41.41 | 13700 | 42.39 | 0.4 | 33.7788 | -118.0109 | 53.545
GWD 13710 | Girth Weld |  | 42920.59 | 42.39 | 0.28 | 35000 | ERW | 8.625 | 600 | [10 empty] | Valve 602 | 2356.38 | AGM 14 | 578.75 | 41.41 | 42.39 | 42.12 | 41.41 | 42.39 | 13710 | 0.4 | 41.2 | 33.7789 | -118.0109 | 53.523
GWD 13720 | Girth Weld |  | 42962.98 | 0.15 | 0.28 | 35000 | ERW | 8.625 | 600 | [10 empty] | Valve 602 | 2398.77 | AGM 14 | 536.35 | 42.39 | 0.4 | 41.41 | 42.39 | 0.4 | 13720 | 41.2 | 42.2 | 33.779 | -118.0109 | 53.344
BND 122 | Bend |  | 42963.13 | 0.26 | 0.28 | 35000 | ERW | 8.625 | 600 |  |  | 4.843 | [7 empty] | Valve 602 | 2398.92 | AGM 14 | 536.21 | 0.15 | 0.26 | 41.41 | 42.39 | 0.4 | 13720 | 41.2 | 42.2 | 33.779 | -118.0109 | 53.344 | 3.0D 13.6 deg left turn bend
GWD 13730 | Girth Weld |  | 42963.39 | 41.2 | 0.28 | 35000 | ERW | 8.625 | 600 | [10 empty] | Valve 602 | 2399.18 | AGM 14 | 535.95 | 0.4 | 41.2 | 42.39 | 0.4 | 41.2 | 13730 | 42.2 | 18.91 | 33.779 | -118.0109 | 53.344
GWD 13740 | Girth Weld |  | 43004.59 | 42.2 | 0.28 | 35000 | ERW | 8.625 | 600 | [10 empty] | Valve 602 | 2440.38 | AGM 14 | 494.75 | 41.2 | 42.2 | 0.4 | 41.2 | 42.2 | 13740 | 18.91 | 18.61 | 33.7791 | -118.0109 | 53.486
GWD 13750 | Girth Weld |  | 43046.79 | 18.91 | 0.28 | 35000 | ERW | 8.625 | 600 | [10 empty] | Valve 602 | 2482.57 | AGM 14 | 452.55 | 42.2 | 18.91 | 41.2 | 42.2 | 18.91 | 13750 | 18.61 | 0.5 | 33.7793 | -118.011 | 53.724
GWD 13760 | Girth Weld |  | 43065.7 | 18.61 | 0.28 | 35000 | ERW | 8.625 | 600 | [10 empty] | Valve 602 | 2501.48 | AGM 14 | 433.64 | 18.91 | 18.61 | 42.2 | 18.91 | 18.61 | 13760 | 0.5 | 1.18 | 33.7793 | -118.011 | 53.72
GWD 13770 | Girth Weld |  | 43084.31 | 0.32 | 0.28 | 35000 | ERW | 8.625 | 600 | [10 empty] | Valve 602 | 2520.09 | AGM 14 | 415.03 | 18.61 | 0.5 | 18.91 | 18.61 | 0.5 | 13770 | 1.18 | 47.17 | 33.7793 | -118.011 | 53.73
BND 123 | Bend |  | 43084.63 | 0.17 | 0.28 | 35000 | ERW | 8.625 | 600 |  |  | 5.945 | [7 empty] | Valve 602 | 2520.42 | AGM 14 | 414.71 | 0.32 | 0.17 | 18.91 | 18.61 | 0.5 | 13770 | 1.18 | 47.17 | 33.7794 | -118.011 | 53.733 | 3.5D 14.6 deg right turn sag bend
GWD 13780 | Girth Weld |  | 43084.8 | 1.18 | 0.25 | 35000 | ERW | 8.625 | 600 | [10 empty] | Valve 602 | 2520.59 | AGM 14 | 414.54 | 0.5 | 1.18 | 18.61 | 0.5 | 1.18 | 13780 | 47.17 | 47.42 | 33.7794 | -118.011 | 53.733 | Estimated WT 0.250
GWD 13790 | Girth Weld |  | 43085.98 | 47.17 | 0.25 | 35000 | ERW | 8.625 | 600 | [10 empty] | Valve 602 | 2521.76 | AGM 14 | 413.36 | 1.18 | 47.17 | 0.5 | 1.18 | 47.17 | 13790 | 47.42 | 48.27 | 33.7794 | -118.011 | 53.747
GWD 13800 | Girth Weld |  | 43133.15 | 47.42 | 0.25 | 35000 | ERW | 8.625 | 600 | [10 empty] | Valve 602 | 2568.94 | AGM 14 | 366.19 | 47.17 | 47.42 | 1.18 | 47.17 | 47.42 | 13800 | 48.27 | 47.22 | 33.7795 | -118.011 | 55.033
GWD 13810 | Girth Weld |  | 43180.57 | 48.27 | 0.25 | 35000 | ERW | 8.625 | 600 | [10 empty] | Valve 602 | 2616.36 | AGM 14 | 318.77 | 47.42 | 48.27 | 47.17 | 47.42 | 48.27 | 13810 | 47.22 | 47.23 | 33.7796 | -118.011 | 55.517
GWD 13820 | Girth Weld |  | 43228.84 | 47.22 | 0.25 | 35000 | ERW | 8.625 | 600 | [10 empty] | Valve 602 | 2664.63 | AGM 14 | 270.5 | 48.27 | 47.22 | 47.42 | 48.27 | 47.22 | 13820 | 47.23 | 47.94 | 33.7797 | -118.011 | 55.344
GWD 13830 | Girth Weld |  | 43276.06 | 47.23 | 0.25 | 35000 | ERW | 8.625 | 600 | [10 empty] | Valve 602 | 2711.85 | AGM 14 | 223.27 | 47.22 | 47.23 | 48.27 | 47.22 | 47.23 | 13830 | 47.94 | 47.73 | 33.7799 | -118.011 | 55.153
GWD 13840 | Girth Weld |  | 43323.3 | 47.94 | 0.25 | 35000 | ERW | 8.625 | 600 | [10 empty] | Valve 602 | 2759.08 | AGM 14 | 176.04 | 47.23 | 47.94 | 47.22 | 47.23 | 47.94 | 13840 | 47.73 | 46.3 | 33.78 | -118.011 | 55.176
GWD 13850 | Girth Weld |  | 43371.23 | 47.73 | 0.25 | 35000 | ERW | 8.625 | 600 | [10 empty] | Valve 602 | 2807.02 | AGM 14 | 128.1 | 47.94 | 47.73 | 47.23 | 47.94 | 47.73 | 13850 | 46.3 | 47.62 | 33.7801 | -118.011 | 55.281
GWD 13860 | Girth Weld |  | 43418.97 | 46.3 | 0.25 | 35000 | ERW | 8.625 | 600 | [10 empty] | Valve 602 | 2854.75 | AGM 14 | 80.37 | 47.73 | 46.3 | 47.94 | 47.73 | 46.3 | 13860 | 47.62 | 38.7 | 33.7803 | -118.011 | 55.258
GWD 13870 | Girth Weld |  | 43465.27 | 34.07 | 0.25 | 35000 | ERW | 8.625 | 600 | [10 empty] | Valve 602 | 2901.05 | AGM 14 | 34.07 | 46.3 | 47.62 | 47.73 | 46.3 | 47.62 | 13870 | 38.7 | 48.26 | 33.7804 | -118.011 | 55.157
MRK 12 | Marker |  | 43499.34 | 13.54 | 0.25 | 35000 | ERW | 8.625 | 600 |  |  |  |  | 11:33 | [5 empty] | Valve 602 | 2935.13 | AGM 15 | 2648.95 | 34.07 | 13.54 | 47.73 | 46.3 | 47.62 | 13870 | 38.7 | 48.26 | 33.7805 | -118.011 | 55.369 | AGM 14 6' East of Knott St Curb at Paint Mark
GWD 13880 | Girth Weld |  | 43512.88 | 38.7 | 0.25 | 35000 | ERW | 8.625 | 600 | [10 empty] | AGM 14 | 13.54 | AGM 15 | 2635.41 | 47.62 | 38.7 | 46.3 | 47.62 | 38.7 | 13880 | 48.26 | 4.91 | 33.7805 | -118.011 | 55.562
GWD 13890 | Girth Weld |  | 43551.58 | 48.26 | 0.25 | 35000 | ERW | 8.625 | 600 | [10 empty] | AGM 14 | 52.24 | AGM 15 | 2596.71 | 38.7 | 48.26 | 47.62 | 38.7 | 48.26 | 13890 | 4.91 | 1.57 | 33.7806 | -118.011 | 55.848
GWD 13900 | Girth Weld |  | 43599.84 | 4.91 | 0.25 | 35000 | ERW | 8.625 | 600 | [10 empty] | AGM 14 | 100.51 | AGM 15 | 2548.44 | 48.26 | 4.91 | 38.7 | 48.26 | 4.91 | 13900 | 1.57 | 3.31 | 33.7808 | -118.011 | 55.966
GWD 13910 | Girth Weld |  | 43604.75 | 0.74 | 0.25 | 35000 | ERW | 8.625 | 600 | [10 empty] | AGM 14 | 105.41 | AGM 15 | 2543.54 | 4.91 | 1.57 | 48.26 | 4.91 | 1.57 | 13910 | 3.31 | 1.52 | 33.7808 | -118.011 | 56.033
BND 124 | Bend |  | 43605.5 | 0.83 | 0.25 | 35000 | ERW | 8.625 | 600 |  |  | 23.947 | [7 empty] | AGM 14 | 106.16 | AGM 15 | 2542.79 | 0.74 | 0.83 | 48.26 | 4.91 | 1.57 | 13910 | 3.31 | 1.52 | 33.7808 | -118.011 | 55.917 | 3.0D 49.5 deg right turn over bend
GWD 13920 | Girth Weld |  | 43606.32 | 3.31 | 0.28 | 35000 | ERW | 8.625 | 600 | [10 empty] | AGM 14 | 106.98 | AGM 15 | 2541.97 | 1.57 | 3.31 | 4.91 | 1.57 | 3.31 | 13920 | 1.52 | 13.23 | 33.7808 | -118.011 | 55.58
GWD 13930 | Girth Weld |  | 43609.63 | 0.85 | 0.28 | 35000 | ERW | 8.625 | 600 | [10 empty] | AGM 14 | 110.29 | AGM 15 | 2538.66 | 3.31 | 1.52 | 1.57 | 3.31 | 1.52 | 13930 | 13.23 | 42.92 | 33.7808 | -118.011 | 53.75
BND 125 | Bend |  | 43610.49 | 0.66 | 0.28 | 35000 | ERW | 8.625 | 600 |  |  | 25.359 | [7 empty] | AGM 14 | 111.15 | AGM 15 | 2537.8 | 0.85 | 0.66 | 1.57 | 3.31 | 1.52 | 13930 | 13.23 | 42.92 | 33.7808 | -118.011 | 53.372 | 3.0D 49.0 deg left turn sag bend
GWD 13940 | Girth Weld |  | 43611.15 | 13.23 | 0.28 | 35000 | ERW | 8.625 | 600 | [10 empty] | AGM 14 | 111.81 | AGM 15 | 2537.14 | 1.52 | 13.23 | 3.31 | 1.52 | 13.23 | 13940 | 42.92 | 1.49 | 33.7808 | -118.011 | 53.233
GWD 13950 | Girth Weld |  | 43624.38 | 42.92 | 0.28 | 35000 | ERW | 8.625 | 600 | [10 empty] | AGM 14 | 125.04 | AGM 15 | 2523.91 | 13.23 | 42.92 | 1.52 | 13.23 | 42.92 | 13950 | 1.49 | 1.58 | 33.7808 | -118.011 | 53.164
GWD 13960 | Girth Weld |  | 43667.3 | 0.47 | 0.28 | 35000 | ERW | 8.625 | 600 | [10 empty] | AGM 14 | 167.96 | AGM 15 | 2480.99 | 42.92 | 1.49 | 13.23 | 42.92 | 1.49 | 13960 | 1.58 | 31.68 | 33.7809 | -118.011 | 53.012
BND 126 | Bend |  | 43667.77 | 1.02 | 0.28 | 35000 | ERW | 8.625 | 600 |  |  | 17.913 | [7 empty] | AGM 14 | 168.43 | AGM 15 | 2480.52 | 0.47 | 1.02 | 13.23 | 42.92 | 1.49 | 13960 | 1.58 | 31.68 | 33.7809 | -118.011 | 53.087 | 3.0D 40.2 deg left turn sag bend
GWD 13970 | Girth Weld |  | 43668.79 | 1.24 | 0.28 | 35000 | ERW | 8.625 | 600 | [10 empty] | AGM 14 | 169.45 | AGM 15 | 2479.5 | 1.49 | 1.58 | 42.92 | 1.49 | 1.58 | 13970 | 31.68 | 1.65 | 33.781 | -118.011 | 53.575
BND 127 | Bend |  | 43670.03 | 0.34 | 0.28 | 35000 | ERW | 8.625 | 600 |  |  | 18.937 | [7 empty] | AGM 14 | 170.69 | AGM 15 | 2478.26 | 1.24 | 0.34 | 42.92 | 1.49 | 1.58 | 13970 | 31.68 | 1.65 | 33.781 | -118.011 | 54.198 | 5.0D 37.1 deg right turn over bend
GWD 13980 | Girth Weld |  | 43670.37 | 31.68 | 0.28 | 35000 | ERW | 8.625 | 600 | [10 empty] | AGM 14 | 171.03 | AGM 15 | 2477.92 | 1.58 | 31.68 | 1.49 | 1.58 | 31.68 | 13980 | 1.65 | 1.48 | 33.781 | -118.011 | 54.281
GWD 13990 | Girth Weld |  | 43702.05 | 0.38 | 0.28 | 35000 | ERW | 8.625 | 600 | [10 empty] | AGM 14 | 202.72 | AGM 15 | 2446.23 | 31.68 | 1.65 | 1.58 | 31.68 | 1.65 | 13990 | 1.48 | 42.08 | 33.781 | -118.011 | 54.432
BND 128 | Bend |  | 43702.43 | 1.27 | 0.28 | 35000 | ERW | 8.625 | 600 |  |  | 18.804 | [7 empty] | AGM 14 | 203.09 | AGM 15 | 2445.86 | 0.38 | 1.27 | 1.58 | 31.68 | 1.65 | 13990 | 1.48 | 42.08 | 33.781 | -118.011 | 54.367 | 3.0D 40.2 deg left turn over bend
GWD 14000 | Girth Weld |  | 43703.7 | 1.01 | 0.28 | 35000 | ERW | 8.625 | 600 | [10 empty] | AGM 14 | 204.37 | AGM 15 | 2444.58 | 1.65 | 1.48 | 31.68 | 1.65 | 1.48 | 14000 | 42.08 | 4.17 | 33.781 | -118.011 | 53.746
BND 129 | Bend |  | 43704.71 | 0.47 | 0.28 | 35000 | ERW | 8.625 | 600 |  |  | 18.89 | [7 empty] | AGM 14 | 205.38 | AGM 15 | 2443.57 | 1.01 | 0.47 | 31.68 | 1.65 | 1.48 | 14000 | 42.08 | 4.17 | 33.781 | -118.011 | 53.283 | 3.0D 37.5 deg right turn sag bend
GWD 14010 | Girth Weld |  | 43705.18 | 42.08 | 0.28 | 35000 | ERW | 8.625 | 600 | [10 empty] | AGM 14 | 205.85 | AGM 15 | 2443.1 | 1.48 | 42.08 | 1.65 | 1.48 | 42.08 | 14010 | 4.17 | 1.54 | 33.781 | -118.011 | 53.203
GWD 14020 | Girth Weld |  | 43747.26 | 4.17 | 0.28 | 35000 | ERW | 8.625 | 600 | [10 empty] | AGM 14 | 247.93 | AGM 15 | 2401.02 | 42.08 | 4.17 | 1.48 | 42.08 | 4.17 | 14020 | 1.54 | 4.18 | 33.7812 | -118.011 | 53.93
GWD 14030 | Girth Weld |  | 43751.43 | 0.64 | 0.28 | 35000 | ERW | 8.625 | 600 | [10 empty] | AGM 14 | 252.09 | AGM 15 | 2396.86 | 4.17 | 1.54 | 42.08 | 4.17 | 1.54 | 14030 | 4.18 | 1.59 | 33.7812 | -118.011 | 53.884
BND 130 | Bend |  | 43752.07 | 0.91 | 0.28 | 35000 | ERW | 8.625 | 600 |  |  | 24.728 | [7 empty] | AGM 14 | 252.73 | AGM 15 | 2396.22 | 0.64 | 0.91 | 42.08 | 4.17 | 1.54 | 14030 | 4.18 | 1.59 | 33.7812 | -118.011 | 53.983 | 3.0D 47.7 deg left turn sag bend
GWD 14040 | Girth Weld |  | 43752.98 | 4.18 | 0.28 | 35000 | ERW | 8.625 | 600 | [10 empty] | AGM 14 | 253.64 | AGM 15 | 2395.31 | 1.54 | 4.18 | 4.17 | 1.54 | 4.18 | 14040 | 1.59 | 1.57 | 33.7812 | -118.011 | 54.345
GWD 14050 | Girth Weld |  | 43757.16 | 1.59 | 0.28 | 35000 | ERW | 8.625 | 600 | [10 empty] | AGM 14 | 257.82 | AGM 15 | 2391.13 | 4.18 | 1.59 | 1.54 | 4.18 | 1.59 | 14050 | 1.57 | 1.93 | 33.7812 | -118.011 | 56.595
GWD 14060 | Girth Weld |  | 43758.75 | 0 | 0.28 | 35000 | ERW | 8.625 | 600 | [10 empty] | AGM 14 | 259.41 | AGM 15 | 2389.54 | 1.59 | 1.57 | 4.18 | 1.59 | 1.57 | 14060 | 1.93 | 1.53 | 33.7812 | -118.011 | 57.02
BND 131 | Bend |  | 43758.75 | 1.57 | 0.28 | 35000 | ERW | 8.625 | 600 |  |  | 43.016 | [7 empty] | AGM 14 | 259.42 | AGM 15 | 2389.53 | 0 | 1.57 | 4.18 | 1.59 | 1.57 | 14060 | 1.93 | 1.53 | 33.7812 | -118.011 | 57.021 | 3.0D 78.3 deg right turn over bend
GWD 14070 | Girth Weld |  | 43760.32 | 1.93 | 0.28 | 35000 | ERW | 8.625 | 600 | [10 empty] | AGM 14 | 260.99 | AGM 15 | 2387.96 | 1.57 | 1.93 | 1.59 | 1.57 | 1.93 | 14070 | 1.53 | 4.7 | 33.7812 | -118.011 | 57.113
GWD 14080 | Girth Weld |  | 43762.25 | 0.91 | 0.28 | 35000 | ERW | 8.625 | 600 | [10 empty] | AGM 14 | 262.92 | AGM 15 | 2386.03 | 1.93 | 1.53 | 1.57 | 1.93 | 1.53 | 14080 | 4.7 | 4.39 | 33.7812 | -118.011 | 57.323
BND 132 | Bend |  | 43763.17 | 0.62 | 0.28 | 35000 | ERW | 8.625 | 600 |  |  | 26.644 | [7 empty] | AGM 14 | 263.83 | AGM 15 | 2385.12 | 0.91 | 0.62 | 1.57 | 1.93 | 1.53 | 14080 | 4.7 | 4.39 | 33.7812 | -118.011 | 57.42 | 3.0D 47.7 deg left turn over bend
GWD 14090 | Girth Weld |  | 43763.79 | 4.7 | 0.219 | 35000 | ERW | 8.625 | 600 | [10 empty] | AGM 14 | 264.45 | AGM 15 | 2384.5 | 1.53 | 4.7 | 1.93 | 1.53 | 4.7 | 14090 | 4.39 | 44.95 | 33.7812 | -118.011 | 57.452
GWD 14100 | Girth Weld |  | 43768.49 | 4.39 | 0.219 | 35000 | ERW | 8.625 | 600 | [10 empty] | AGM 14 | 269.15 | AGM 15 | 2379.8 | 4.7 | 4.39 | 1.53 | 4.7 | 4.39 | 14100 | 44.95 | 39.51 | 33.7812 | -118.011 | 57.477
GWD 14110 | Girth Weld |  | 43772.88 | 44.95 | 0.219 | 35000 | ERW | 8.625 | 600 | [10 empty] | AGM 14 | 273.54 | AGM 15 | 2375.41 | 4.39 | 44.95 | 4.7 | 4.39 | 44.95 | 14110 | 39.51 | 47.67 | 33.7812 | -118.011 | 57.539
GWD 14120 | Girth Weld |  | 43817.83 | 39.51 | 0.219 | 35000 | ERW | 8.625 | 600 | [10 empty] | AGM 14 | 318.49 | AGM 15 | 2330.46 | 44.95 | 39.51 | 4.39 | 44.95 | 39.51 | 14120 | 47.67 | 47.61 | 33.7814 | -118.011 | 58.581
GWD 14130 | Girth Weld |  | 43857.35 | 47.67 | 0.219 | 35000 | ERW | 8.625 | 600 | [10 empty] | AGM 14 | 358.01 | AGM 15 | 2290.94 | 39.51 | 47.67 | 44.95 | 39.51 | 47.67 | 14130 | 47.61 | 44.9 | 33.7815 | -118.011 | 58.655
GWD 14140 | Girth Weld |  | 43905.02 | 47.61 | 0.219 | 35000 | ERW | 8.625 | 600 | [10 empty] | AGM 14 | 405.68 | AGM 15 | 2243.27 | 47.67 | 47.61 | 39.51 | 47.67 | 47.61 | 14140 | 44.9 | 47.9 | 33.7816 | -118.011 | 58.957
GWD 14150 | Girth Weld |  | 43952.63 | 44.9 | 0.219 | 35000 | ERW | 8.625 | 600 | [10 empty] | AGM 14 | 453.3 | AGM 15 | 2195.65 | 47.61 | 44.9 | 47.67 | 47.61 | 44.9 | 14150 | 47.9 | 47.74 | 33.7817 | -118.011 | 59.045
GWD 14160 | Girth Weld |  | 43997.53 | 47.9 | 0.219 | 35000 | ERW | 8.625 | 600 | [10 empty] | AGM 14 | 498.19 | AGM 15 | 2150.76 | 44.9 | 47.9 | 47.61 | 44.9 | 47.9 | 14160 | 47.74 | 47.71 | 33.7818 | -118.011 | 58.859
GWD 14170 | Girth Weld |  | 44045.43 | 47.74 | 0.219 | 35000 | ERW | 8.625 | 600 | [10 empty] | AGM 14 | 546.09 | AGM 15 | 2102.86 | 47.9 | 47.74 | 44.9 | 47.9 | 47.74 | 14170 | 47.71 | 47.82 | 33.782 | -118.011 | 58.87
GWD 14180 | Girth Weld |  | 44093.17 | 47.71 | 0.219 | 35000 | ERW | 8.625 | 600 | [10 empty] | AGM 14 | 593.84 | AGM 15 | 2055.11 | 47.74 | 47.71 | 47.9 | 47.74 | 47.71 | 14180 | 47.82 | 47.75 | 33.7821 | -118.011 | 58.922
GWD 14190 | Girth Weld |  | 44140.89 | 47.82 | 0.219 | 35000 | ERW | 8.625 | 600 | [10 empty] | AGM 14 | 641.55 | AGM 15 | 2007.4 | 47.71 | 47.82 | 47.74 | 47.71 | 47.82 | 14190 | 47.75 | 47.89 | 33.7822 | -118.011 | 58.571
GWD 14200 | Girth Weld |  | 44188.7 | 47.75 | 0.219 | 35000 | ERW | 8.625 | 600 | [10 empty] | AGM 14 | 689.37 | AGM 15 | 1959.58 | 47.82 | 47.75 | 47.71 | 47.82 | 47.75 | 14200 | 47.89 | 47.97 | 33.7824 | -118.011 | 58.378
GWD 14210 | Girth Weld |  | 44236.46 | 47.89 | 0.219 | 35000 | ERW | 8.625 | 600 | [10 empty] | AGM 14 | 737.12 | AGM 15 | 1911.83 | 47.75 | 47.89 | 47.82 | 47.75 | 47.89 | 14210 | 47.97 | 47.78 | 33.7825 | -118.011 | 58.296
GWD 14220 | Girth Weld |  | 44284.35 | 47.97 | 0.219 | 35000 | ERW | 8.625 | 600 | [10 empty] | AGM 14 | 785.01 | AGM 15 | 1863.94 | 47.89 | 47.97 | 47.75 | 47.89 | 47.97 | 14220 | 47.78 | 47.85 | 33.7826 | -118.011 | 58.168
GWD 14230 | Girth Weld |  | 44332.32 | 47.78 | 0.219 | 35000 | ERW | 8.625 | 600 | [10 empty] | AGM 14 | 832.98 | AGM 15 | 1815.97 | 47.97 | 47.78 | 47.89 | 47.97 | 47.78 | 14230 | 47.85 | 47.78 | 33.7828 | -118.011 | 57.859
GWD 14240 | Girth Weld |  | 44380.1 | 47.85 | 0.219 | 35000 | ERW | 8.625 | 600 | [10 empty] | AGM 14 | 880.76 | AGM 15 | 1768.19 | 47.78 | 47.85 | 47.97 | 47.78 | 47.85 | 14240 | 47.78 | 47.84 | 33.7829 | -118.011 | 57.625
GWD 14250 | Girth Weld |  | 44427.95 | 47.78 | 0.219 | 35000 | ERW | 8.625 | 600 | [10 empty] | AGM 14 | 928.61 | AGM 15 | 1720.34 | 47.85 | 47.78 | 47.78 | 47.85 | 47.78 | 14250 | 47.84 | 47.69 | 33.783 | -118.011 | 57.272
GWD 14260 | Girth Weld |  | 44475.73 | 47.84 | 0.219 | 35000 | ERW | 8.625 | 600 | [10 empty] | AGM 14 | 976.39 | AGM 15 | 1672.56 | 47.78 | 47.84 | 47.85 | 47.78 | 47.84 | 14260 | 47.69 | 47.63 | 33.7832 | -118.011 | 56.919
GWD 14270 | Girth Weld |  | 44523.57 | 47.69 | 0.219 | 35000 | ERW | 8.625 | 600 | [10 empty] | AGM 14 | 1024.23 | AGM 15 | 1624.72 | 47.84 | 47.69 | 47.78 | 47.84 | 47.69 | 14270 | 47.63 | 47.84 | 33.7833 | -118.011 | 56.173
GWD 14280 | Girth Weld |  | 44571.26 | 47.63 | 0.219 | 35000 | ERW | 8.625 | 600 | [10 empty] | AGM 14 | 1071.93 | AGM 15 | 1577.02 | 47.69 | 47.63 | 47.84 | 47.69 | 47.63 | 14280 | 47.84 | 34.05 | 33.7834 | -118.011 | 55.444
GWD 14290 | Girth Weld |  | 44618.9 | 47.84 | 0.219 | 35000 | ERW | 8.625 | 600 | [10 empty] | AGM 14 | 1119.56 | AGM 15 | 1529.39 | 47.63 | 47.84 | 47.69 | 47.63 | 47.84 | 14290 | 34.05 | 47.7 | 33.7836 | -118.011 | 54.686
GWD 14300 | Girth Weld |  | 44666.74 | 34.05 | 0.219 | 35000 | ERW | 8.625 | 600 | [10 empty] | AGM 14 | 1167.4 | AGM 15 | 1481.55 | 47.84 | 34.05 | 47.63 | 47.84 | 34.05 | 14300 | 47.7 | 47.76 | 33.7837 | -118.011 | 54.073
GWD 14310 | Girth Weld |  | 44700.79 | 47.7 | 0.219 | 35000 | ERW | 8.625 | 600 | [10 empty] | AGM 14 | 1201.46 | AGM 15 | 1447.49 | 34.05 | 47.7 | 47.84 | 34.05 | 47.7 | 14310 | 47.76 | 47.49 | 33.7838 | -118.011 | 53.508
GWD 14320 | Girth Weld |  | 44748.5 | 47.76 | 0.219 | 35000 | ERW | 8.625 | 600 | [10 empty] | AGM 14 | 1249.16 | AGM 15 | 1399.79 | 47.7 | 47.76 | 34.05 | 47.7 | 47.76 | 14320 | 47.49 | 41.65 | 33.7839 | -118.011 | 53.17
GWD 14330 | Girth Weld |  | 44796.26 | 47.49 | 0.219 | 35000 | ERW | 8.625 | 600 | [10 empty] | AGM 14 | 1296.92 | AGM 15 | 1352.03 | 47.76 | 47.49 | 47.7 | 47.76 | 47.49 | 14330 | 41.65 | 47.69 | 33.784 | -118.011 | 52.753
GWD 14340 | Girth Weld |  | 44843.75 | 41.65 | 0.219 | 35000 | ERW | 8.625 | 600 | [10 empty] | AGM 14 | 1344.41 | AGM 15 | 1304.54 | 47.49 | 41.65 | 47.76 | 47.49 | 41.65 | 14340 | 47.69 | 47.05 | 33.7842 | -118.011 | 52.039
GWD 14350 | Girth Weld |  | 44885.39 | 47.69 | 0.219 | 35000 | ERW | 8.625 | 600 | [10 empty] | AGM 14 | 1386.06 | AGM 15 | 1262.89 | 41.65 | 47.69 | 47.49 | 41.65 | 47.69 | 14350 | 47.05 | 47.55 | 33.7843 | -118.011 | 51.607
GWD 14360 | Girth Weld |  | 44933.09 | 47.05 | 0.219 | 35000 | ERW | 8.625 | 600 | [10 empty] | AGM 14 | 1433.75 | AGM 15 | 1215.2 | 47.69 | 47.05 | 41.65 | 47.69 | 47.05 | 14360 | 47.55 | 47.67 | 33.7844 | -118.011 | 51.196
GWD 14370 | Girth Weld |  | 44980.14 | 47.55 | 0.219 | 35000 | ERW | 8.625 | 600 | [10 empty] | AGM 14 | 1480.8 | AGM 15 | 1168.15 | 47.05 | 47.55 | 47.69 | 47.05 | 47.55 | 14370 | 47.67 | 47.7 | 33.7845 | -118.011 | 50.371
GWD 14380 | Girth Weld |  | 45027.69 | 47.67 | 0.219 | 35000 | ERW | 8.625 | 600 | [10 empty] | AGM 14 | 1528.35 | AGM 15 | 1120.6 | 47.55 | 47.67 | 47.05 | 47.55 | 47.67 | 14380 | 47.7 | 47.51 | 33.7847 | -118.011 | 49.916
GWD 14390 | Girth Weld |  | 45075.36 | 47.7 | 0.219 | 35000 | ERW | 8.625 | 600 | [10 empty] | AGM 14 | 1576.02 | AGM 15 | 1072.93 | 47.67 | 47.7 | 47.55 | 47.67 | 47.7 | 14390 | 47.51 | 41.21 | 33.7848 | -118.011 | 49.108
GWD 14400 | Girth Weld |  | 45123.06 | 47.51 | 0.219 | 35000 | ERW | 8.625 | 600 | [10 empty] | AGM 14 | 1623.72 | AGM 15 | 1025.23 | 47.7 | 47.51 | 47.67 | 47.7 | 47.51 | 14400 | 41.21 | 47.66 | 33.7849 | -118.011 | 48.237
GWD 14410 | Girth Weld |  | 45170.57 | 41.21 | 0.219 | 35000 | ERW | 8.625 | 600 | [10 empty] | AGM 14 | 1671.23 | AGM 15 | 977.72 | 47.51 | 41.21 | 47.7 | 47.51 | 41.21 | 14410 | 47.66 | 46.1 | 33.7851 | -118.011 | 48.013
GWD 14420 | Girth Weld |  | 45211.78 | 47.66 | 0.219 | 35000 | ERW | 8.625 | 600 | [10 empty] | AGM 14 | 1712.45 | AGM 15 | 936.5 | 41.21 | 47.66 | 47.51 | 41.21 | 47.66 | 14420 | 46.1 | 1.54 | 33.7852 | -118.011 | 47.729
GWD 14430 | Girth Weld |  | 45259.44 | 46.1 | 0.219 | 35000 | ERW | 8.625 | 600 | [10 empty] | AGM 14 | 1760.1 | AGM 15 | 888.85 | 47.66 | 46.1 | 41.21 | 47.66 | 46.1 | 14430 | 1.54 | 2.9 | 33.7853 | -118.011 | 47.467
GWD 14440 | Girth Weld |  | 45305.54 | 0.64 | 0.219 | 35000 | ERW | 8.625 | 600 | [10 empty] | AGM 14 | 1806.2 | AGM 15 | 842.75 | 46.1 | 1.54 | 47.66 | 46.1 | 1.54 | 14440 | 2.9 | 1.5 | 33.7854 | -118.011 | 46.643
BND 133 | Bend |  | 45306.18 | 0.91 | 0.219 | 35000 | ERW | 8.625 | 600 |  |  | 24.332 | [7 empty] | AGM 14 | 1806.84 | AGM 15 | 842.11 | 0.64 | 0.91 | 47.66 | 46.1 | 1.54 | 14440 | 2.9 | 1.5 | 33.7854 | -118.011 | 46.622 | 3.0D 47.5 deg left turn bend
GWD 14450 | Girth Weld |  | 45307.08 | 2.9 | 0.28 | 35000 | ERW | 8.625 | 600 | [10 empty] | AGM 14 | 1807.75 | AGM 15 | 841.2 | 1.54 | 2.9 | 46.1 | 1.54 | 2.9 | 14450 | 1.5 | 0.98 | 33.7854 | -118.011 | 46.603
GWD 14460 | Girth Weld |  | 45309.98 | 0.72 | 0.28 | 35000 | ERW | 8.625 | 600 | [10 empty] | AGM 14 | 1810.64 | AGM 15 | 838.31 | 2.9 | 1.5 | 1.54 | 2.9 | 1.5 | 14460 | 0.98 | 36.95 | 33.7855 | -118.011 | 46.583
BND 134 | Bend |  | 45310.7 | 0.78 | 0.28 | 35000 | ERW | 8.625 | 600 |  |  | 24.601 | [7 empty] | AGM 14 | 1811.36 | AGM 15 | 837.59 | 0.72 | 0.78 | 1.54 | 2.9 | 1.5 | 14460 | 0.98 | 36.95 | 33.7855 | -118.011 | 46.596 | 3.0D 47.1 deg right turn bend
GWD 14470 | Girth Weld |  | 45311.48 | 0.98 | 0.28 | 35000 | ERW | 8.625 | 600 | [10 empty] | AGM 14 | 1812.14 | AGM 15 | 836.81 | 1.5 | 0.98 | 2.9 | 1.5 | 0.98 | 14470 | 36.95 | 4.05 | 33.7855 | -118.011 | 46.609
GWD 14480 | Girth Weld |  | 45312.46 | 36.95 | 0.28 | 35000 | ERW | 8.625 | 600 | [10 empty] | AGM 14 | 1813.13 | AGM 15 | 835.82 | 0.98 | 36.95 | 1.5 | 0.98 | 36.95 | 14480 | 4.05 | 1.61 | 33.7855 | -118.011 | 46.619
GWD 14490 | Girth Weld |  | 45349.42 | 4.05 | 0.28 | 35000 | ERW | 8.625 | 600 | [10 empty] | AGM 14 | 1850.08 | AGM 15 | 798.87 | 36.95 | 4.05 | 0.98 | 36.95 | 4.05 | 14490 | 1.61 | 5.9 | 33.7856 | -118.011 | 46.338
GWD 14500 | Girth Weld |  | 45353.47 | 0.84 | 0.28 | 35000 | ERW | 8.625 | 600 | [10 empty] | AGM 14 | 1854.13 | AGM 15 | 794.82 | 4.05 | 1.61 | 36.95 | 4.05 | 1.61 | 14500 | 5.9 | 1.56 | 33.7856 | -118.011 | 46.38
BND 135 | Bend |  | 45354.31 | 0.77 | 0.28 | 35000 | ERW | 8.625 | 600 |  |  | 24.663 | [7 empty] | AGM 14 | 1854.97 | AGM 15 | 793.98 | 0.84 | 0.77 | 36.95 | 4.05 | 1.61 | 14500 | 5.9 | 1.56 | 33.7856 | -118.011 | 46.243 | 3.0D 47.5 deg right turn over bend
GWD 14510 | Girth Weld |  | 45355.08 | 5.9 | 0.28 | 35000 | ERW | 8.625 | 600 | [10 empty] | AGM 14 | 1855.74 | AGM 15 | 793.21 | 1.61 | 5.9 | 4.05 | 1.61 | 5.9 | 14510 | 1.56 | 16.48 | 33.7856 | -118.011 | 45.847
GWD 14520 | Girth Weld |  | 45360.98 | 0.88 | 0.28 | 35000 | ERW | 8.625 | 600 | [10 empty] | AGM 14 | 1861.64 | AGM 15 | 787.31 | 5.9 | 1.56 | 1.61 | 5.9 | 1.56 | 14520 | 16.48 | 1.53 | 33.7856 | -118.011 | 41.629
BND 136 | Bend |  | 45361.86 | 0.68 | 0.28 | 35000 | ERW | 8.625 | 600 |  |  | 25.238 | [7 empty] | AGM 14 | 1862.52 | AGM 15 | 786.43 | 0.88 | 0.68 | 1.61 | 5.9 | 1.56 | 14520 | 16.48 | 1.53 | 33.7856 | -118.011 | 41.136 | 3.0D 48.3 deg left turn sag bend
GWD 14530 | Girth Weld |  | 45362.54 | 16.48 | 0.28 | 35000 | ERW | 8.625 | 600 | [10 empty] | AGM 14 | 1863.21 | AGM 15 | 785.74 | 1.56 | 16.48 | 5.9 | 1.56 | 16.48 | 14530 | 1.53 | 5.78 | 33.7856 | -118.011 | 40.969
GWD 14540 | Girth Weld |  | 45379.03 | 0.68 | 0.28 | 35000 | ERW | 8.625 | 600 | [10 empty] | AGM 14 | 1879.69 | AGM 15 | 769.26 | 16.48 | 1.53 | 1.56 | 16.48 | 1.53 | 14540 | 5.78 | 1.74 | 33.7856 | -118.011 | 41.141
BND 137 | Bend |  | 45379.7 | 0.86 | 0.28 | 35000 | ERW | 8.625 | 600 |  |  | 23.979 | [7 empty] | AGM 14 | 1880.36 | AGM 15 | 768.59 | 0.68 | 0.86 | 1.56 | 16.48 | 1.53 | 14540 | 5.78 | 1.74 | 33.7856 | -118.011 | 41.289 | 3.0D 47.2 deg left turn sag bend
GWD 14550 | Girth Weld |  | 45380.56 | 5.78 | 0.28 | 35000 | ERW | 8.625 | 600 | [10 empty] | AGM 14 | 1881.22 | AGM 15 | 767.73 | 1.53 | 5.78 | 16.48 | 1.53 | 5.78 | 14550 | 1.74 | 36.16 | 33.7856 | -118.011 | 41.75
GWD 14560 | Girth Weld |  | 45386.34 | 0.99 | 0.28 | 35000 | ERW | 8.625 | 600 | [10 empty] | AGM 14 | 1887 | AGM 15 | 761.95 | 5.78 | 1.74 | 1.53 | 5.78 | 1.74 | 14560 | 36.16 | 3.08 | 33.7857 | -118.011 | 45.884
BND 138 | Bend |  | 45387.33 | 0.75 | 0.28 | 35000 | ERW | 8.625 | 600 |  |  | 24.736 | [7 empty] | AGM 14 | 1887.99 | AGM 15 | 760.96 | 0.99 | 0.75 | 1.53 | 5.78 | 1.74 | 14560 | 36.16 | 3.08 | 33.7857 | -118.011 | 46.462 | 3.0D 48.3 deg right turn over bend
GWD 14570 | Girth Weld |  | 45388.08 | 36.16 | 0.28 | 35000 | ERW | 8.625 | 600 | [10 empty] | AGM 14 | 1888.74 | AGM 15 | 760.21 | 1.74 | 36.16 | 5.78 | 1.74 | 36.16 | 14570 | 3.08 | 6.07 | 33.7857 | -118.011 | 46.65
GWD 14580 | Girth Weld |  | 45424.23 | 1.52 | 0.28 | 35000 | ERW | 8.625 | 600 | [10 empty] | AGM 14 | 1924.9 | AGM 15 | 724.05 | 36.16 | 3.08 | 1.74 | 36.16 | 3.08 | 14580 | 6.07 | 3.19 | 33.7858 | -118.011 | 45.774
BND 139 | Bend |  | 45425.76 | 1.56 | 0.28 | 35000 | ERW | 8.625 | 600 |  |  | 40.432 | [7 empty] | AGM 14 | 1926.42 | AGM 15 | 722.53 | 1.52 | 1.56 | 1.74 | 36.16 | 3.08 | 14580 | 6.07 | 3.19 | 33.7858 | -118.011 | 45.793 | 3.0D 90.5 deg left turn sag bend
GWD 14590 | Girth Weld |  | 45427.32 | 6.07 | 0.28 | 35000 | ERW | 8.625 | 600 | [10 empty] | AGM 14 | 1927.98 | AGM 15 | 720.97 | 3.08 | 6.07 | 36.16 | 3.08 | 6.07 | 14590 | 3.19 | 1.01 | 33.7858 | -118.011 | 45.887
GWD 14600 | Girth Weld |  | 45433.39 | 1.75 | 0.28 | 35000 | ERW | 8.625 | 600 | [10 empty] | AGM 14 | 1934.05 | AGM 15 | 714.9 | 6.07 | 3.19 | 3.08 | 6.07 | 3.19 | 14600 | 1.01 | 32.3 | 33.7858 | -118.011 | 46.378
BND 140 | Bend |  | 45435.14 | 1.44 | 0.28 | 35000 | ERW | 8.625 | 600 |  |  | 43.658 | [7 empty] | AGM 14 | 1935.8 | AGM 15 | 713.15 | 1.75 | 1.44 | 3.08 | 6.07 | 3.19 | 14600 | 1.01 | 32.3 | 33.7858 | -118.011 | 46.499 | 3.0D 91.5 deg right turn over bend
GWD 14610 | Girth Weld |  | 45436.58 | 1.01 | 0.28 | 35000 | ERW | 8.625 | 600 | [10 empty] | AGM 14 | 1937.24 | AGM 15 | 711.71 | 3.19 | 1.01 | 6.07 | 3.19 | 1.01 | 14610 | 32.3 | 38.81 | 33.7858 | -118.011 | 46.534
GWD 14620 | Girth Weld |  | 45437.59 | 32.3 | 0.25 | 35000 | ERW | 8.625 | 600 | [10 empty] | AGM 14 | 1938.25 | AGM 15 | 710.7 | 1.01 | 32.3 | 3.19 | 1.01 | 32.3 | 14620 | 38.81 | 36.6 | 33.7858 | -118.011 | 46.521 | Estimated WT 0.250
GWD 14630 | Girth Weld |  | 45469.89 | 38.81 | 0.25 | 35000 | ERW | 8.625 | 600 | [10 empty] | AGM 14 | 1970.55 | AGM 15 | 678.4 | 32.3 | 38.81 | 1.01 | 32.3 | 38.81 | 14630 | 36.6 | 40.7 | 33.7859 | -118.011 | 46.364
GWD 14640 | Girth Weld |  | 45508.7 | 36.6 | 0.25 | 35000 | ERW | 8.625 | 600 | [10 empty] | AGM 14 | 2009.36 | AGM 15 | 639.59 | 38.81 | 36.6 | 32.3 | 38.81 | 36.6 | 14640 | 40.7 | 30.52 | 33.786 | -118.011 | 46.051
GWD 14650 | Girth Weld |  | 45545.29 | 40.7 | 0.25 | 35000 | ERW | 8.625 | 600 | [10 empty] | AGM 14 | 2045.96 | AGM 15 | 602.99 | 36.6 | 40.7 | 38.81 | 36.6 | 40.7 | 14650 | 30.52 | 35.07 | 33.7861 | -118.011 | 46.011
GWD 14660 | Girth Weld |  | 45586 | 30.52 | 0.25 | 35000 | ERW | 8.625 | 600 | [10 empty] | AGM 14 | 2086.66 | AGM 15 | 562.29 | 40.7 | 30.52 | 36.6 | 40.7 | 30.52 | 14660 | 35.07 | 34.11 | 33.7862 | -118.011 | 46.02
GWD 14670 | Girth Weld |  | 45616.52 | 35.07 | 0.25 | 35000 | ERW | 8.625 | 600 | [10 empty] | AGM 14 | 2117.18 | AGM 15 | 531.77 | 30.52 | 35.07 | 40.7 | 30.52 | 35.07 | 14670 | 34.11 | 31.11 | 33.7863 | -118.011 | 45.951
GWD 14680 | Girth Weld |  | 45651.59 | 34.11 | 0.25 | 35000 | ERW | 8.625 | 600 | [10 empty] | AGM 14 | 2152.25 | AGM 15 | 496.7 | 35.07 | 34.11 | 30.52 | 35.07 | 34.11 | 14680 | 31.11 | 32.48 | 33.7864 | -118.011 | 45.816
GWD 14690 | Girth Weld |  | 45685.7 | 31.11 | 0.25 | 35000 | ERW | 8.625 | 600 | [10 empty] | AGM 14 | 2186.36 | AGM 15 | 462.59 | 34.11 | 31.11 | 35.07 | 34.11 | 31.11 | 14690 | 32.48 | 40.1 | 33.7864 | -118.011 | 45.652
GWD 14700 | Girth Weld |  | 45716.81 | 32.48 | 0.25 | 35000 | ERW | 8.625 | 600 | [10 empty] | AGM 14 | 2217.47 | AGM 15 | 431.48 | 31.11 | 32.48 | 34.11 | 31.11 | 32.48 | 14700 | 40.1 | 30.58 | 33.7865 | -118.011 | 45.583
GWD 14710 | Girth Weld |  | 45749.28 | 40.1 | 0.25 | 35000 | ERW | 8.625 | 600 | [10 empty] | AGM 14 | 2249.94 | AGM 15 | 399.01 | 32.48 | 40.1 | 31.11 | 32.48 | 40.1 | 14710 | 30.58 | 42.06 | 33.7866 | -118.011 | 45.463
GWD 14720 | Girth Weld |  | 45789.39 | 30.58 | 0.25 | 35000 | ERW | 8.625 | 600 | [10 empty] | AGM 14 | 2290.05 | AGM 15 | 358.9 | 40.1 | 30.58 | 32.48 | 40.1 | 30.58 | 14720 | 42.06 | 19.35 | 33.7867 | -118.011 | 45.431
GWD 14730 | Girth Weld |  | 45819.97 | 42.06 | 0.25 | 35000 | ERW | 8.625 | 600 | [10 empty] | AGM 14 | 2320.63 | AGM 15 | 328.32 | 30.58 | 42.06 | 40.1 | 30.58 | 42.06 | 14730 | 19.35 | 28.78 | 33.7868 | -118.011 | 45.289
GWD 14740 | Girth Weld |  | 45862.03 | 19.35 | 0.25 | 35000 | ERW | 8.625 | 600 | [10 empty] | AGM 14 | 2362.7 | AGM 15 | 286.25 | 42.06 | 19.35 | 30.58 | 42.06 | 19.35 | 14740 | 28.78 | 0.88 | 33.7869 | -118.011 | 44.874
GWD 14750 | Girth Weld |  | 45881.38 | 28.78 | 0.25 | 35000 | ERW | 8.625 | 600 | [10 empty] | AGM 14 | 2382.05 | AGM 15 | 266.9 | 19.35 | 28.78 | 42.06 | 19.35 | 28.78 | 14750 | 0.88 | 1.45 | 33.787 | -118.011 | 44.758
GWD 14760 | Girth Weld |  | 45910.16 | 0.88 | 0.25 | 35000 | ERW | 8.625 | 600 | [10 empty] | AGM 14 | 2410.82 | AGM 15 | 238.13 | 28.78 | 0.88 | 19.35 | 28.78 | 0.88 | 14760 | 1.45 | 1.58 | 33.7871 | -118.011 | 45.443
GWD 14770 | Girth Weld |  | 45911.04 | 0.3 | 0.25 | 35000 | ERW | 8.625 | 600 | [10 empty] | AGM 14 | 2411.71 | AGM 15 | 237.24 | 0.88 | 1.45 | 28.78 | 0.88 | 1.45 | 14770 | 1.58 | 20.15 | 33.7871 | -118.011 | 45.457
BND 141 | Bend |  | 45911.34 | 1.16 | 0.25 | 35000 | ERW | 8.625 | 600 |  |  | 19.44 | [7 empty] | AGM 14 | 2412 | AGM 15 | 236.95 | 0.3 | 1.16 | 28.78 | 0.88 | 1.45 | 14770 | 1.58 | 20.15 | 33.7871 | -118.011 | 45.524 | 3.0D 41.6 deg right turn sag bend
GWD 14780 | Girth Weld |  | 45912.5 | 1.12 | 0.25 | 35000 | ERW | 8.625 | 600 | [10 empty] | AGM 14 | 2413.16 | AGM 15 | 235.79 | 1.45 | 1.58 | 0.88 | 1.45 | 1.58 | 14780 | 20.15 | 1.62 | 33.7871 | -118.011 | 46.122
BND 142 | Bend |  | 45913.61 | 0.46 | 0.25 | 35000 | ERW | 8.625 | 600 |  |  | 20.685 | [7 empty] | AGM 14 | 2414.28 | AGM 15 | 234.67 | 1.12 | 0.46 | 0.88 | 1.45 | 1.58 | 14780 | 20.15 | 1.62 | 33.7871 | -118.011 | 46.683 | 3.0D 38.7 deg left turn over bend
GWD 14790 | Girth Weld |  | 45914.08 | 20.15 | 0.28 | 35000 | ERW | 8.625 | 600 | [10 empty] | AGM 14 | 2414.74 | AGM 15 | 234.21 | 1.58 | 20.15 | 1.45 | 1.58 | 20.15 | 14790 | 1.62 | 1.49 | 33.7871 | -118.011 | 46.785
GWD 14800 | Girth Weld |  | 45934.22 | 0.42 | 0.28 | 35000 | ERW | 8.625 | 600 | [10 empty] | AGM 14 | 2434.89 | AGM 15 | 214.06 | 20.15 | 1.62 | 1.58 | 20.15 | 1.62 | 14800 | 1.49 | 0.95 | 33.7871 | -118.011 | 46.833
BND 143 | Bend |  | 45934.65 | 1.19 | 0.28 | 35000 | ERW | 8.625 | 600 |  |  | 19.409 | [7 empty] | AGM 14 | 2435.31 | AGM 15 | 213.64 | 0.42 | 1.19 | 1.58 | 20.15 | 1.62 | 14800 | 1.49 | 0.95 | 33.7871 | -118.011 | 46.767 | 3.0D 40.1 deg left turn over bend
GWD 14810 | Girth Weld |  | 45935.84 | 1.07 | 0.28 | 35000 | ERW | 8.625 | 600 | [10 empty] | AGM 14 | 2436.5 | AGM 15 | 212.45 | 1.62 | 1.49 | 20.15 | 1.62 | 1.49 | 14810 | 0.95 | 17.77 | 33.7871 | -118.011 | 46.19
BND 144 | Bend |  | 45936.91 | 0.42 | 0.28 | 35000 | ERW | 8.625 | 600 |  |  | 17.835 | [7 empty] | AGM 14 | 2437.57 | AGM 15 | 211.38 | 1.07 | 0.42 | 20.15 | 1.62 | 1.49 | 14810 | 0.95 | 17.77 | 33.7871 | -118.011 | 45.677 | 3.0D 36.7 deg right turn sag bend
GWD 14820 | Girth Weld |  | 45937.33 | 0.95 | 0.25 | 35000 | ERW | 8.625 | 600 | [10 empty] | AGM 14 | 2437.99 | AGM 15 | 210.96 | 1.49 | 0.95 | 1.62 | 1.49 | 0.95 | 14820 | 17.77 | 40.23 | 33.7871 | -118.011 | 45.597 | Estimated WT 0.250
GWD 14830 | Girth Weld |  | 45938.28 | 17.77 | 0.25 | 35000 | ERW | 8.625 | 600 | [10 empty] | AGM 14 | 2438.94 | AGM 15 | 210.01 | 0.95 | 17.77 | 1.49 | 0.95 | 17.77 | 14830 | 40.23 | 33.55 | 33.7871 | -118.011 | 45.547
GWD 14840 | Girth Weld |  | 45956.05 | 40.23 | 0.25 | 35000 | ERW | 8.625 | 600 | [10 empty] | AGM 14 | 2456.71 | AGM 15 | 192.24 | 17.77 | 40.23 | 0.95 | 17.77 | 40.23 | 14840 | 33.55 | 40.24 | 33.7872 | -118.011 | 45.305
GWD 14850 | Girth Weld |  | 45996.28 | 33.55 | 0.25 | 35000 | SMLS | 8.625 | 600 | [10 empty] | AGM 14 | 2496.94 | AGM 15 | 152.01 | 40.23 | 33.55 | 17.77 | 40.23 | 33.55 | 14850 | 40.24 | 42.28 | 33.7873 | -118.011 | 45.318
GWD 14860 | Girth Weld |  | 46029.83 | 40.24 | 0.25 | 35000 | ERW | 8.625 | 600 | [10 empty] | AGM 14 | 2530.5 | AGM 15 | 118.45 | 33.55 | 40.24 | 40.23 | 33.55 | 40.24 | 14860 | 42.28 | 40.4 | 33.7874 | -118.011 | 45.743
GWD 14870 | Girth Weld |  | 46070.08 | 42.28 | 0.25 | 35000 | ERW | 8.625 | 600 | [10 empty] | AGM 14 | 2570.74 | AGM 15 | 78.21 | 40.24 | 42.28 | 33.55 | 40.24 | 42.28 | 14870 | 40.4 | 39.15 | 33.7875 | -118.011 | 45.906
GWD 14880 | Girth Weld |  | 46112.36 | 35.92 | 0.25 | 35000 | ERW | 8.625 | 600 | [10 empty] | AGM 14 | 2613.03 | AGM 15 | 35.92 | 42.28 | 40.4 | 40.24 | 42.28 | 40.4 | 14880 | 39.15 | 40.63 | 33.7876 | -118.011 | 46.432
MRK 13 | Marker |  | 46148.29 | 4.47 | 0.25 | 35000 | ERW | 8.625 | 600 |  |  |  |  | 11:35 | [5 empty] | AGM 14 | 2648.95 | AGM 16 | 3042.72 | 35.92 | 4.47 | 40.24 | 42.28 | 40.4 | 14880 | 39.15 | 40.63 | 33.7877 | -118.011 | 46.848 | AGM 15 8' West of Curb - Located in Knott St
GWD 14890 | Girth Weld |  | 46152.76 | 39.15 | 0.25 | 35000 | ERW | 8.625 | 600 | [10 empty] | AGM 15 | 4.47 | AGM 16 | 3038.24 | 40.4 | 39.15 | 42.28 | 40.4 | 39.15 | 14890 | 40.63 | 41.5 | 33.7877 | -118.011 | 46.869
GWD 14900 | Girth Weld |  | 46191.91 | 40.63 | 0.25 | 35000 | ERW | 8.625 | 600 | [10 empty] | AGM 15 | 43.63 | AGM 16 | 2999.09 | 39.15 | 40.63 | 40.4 | 39.15 | 40.63 | 14900 | 41.5 | 33.63 | 33.7878 | -118.011 | 47.095
GWD 14910 | Girth Weld |  | 46232.54 | 41.5 | 0.25 | 35000 | ERW | 8.625 | 600 | [10 empty] | AGM 15 | 84.26 | AGM 16 | 2958.46 | 40.63 | 41.5 | 39.15 | 40.63 | 41.5 | 14910 | 33.63 | 1.56 | 33.788 | -118.011 | 47.246
GWD 14920 | Girth Weld |  | 46274.05 | 33.63 | 0.25 | 35000 | SMLS | 8.625 | 600 | [10 empty] | AGM 15 | 125.76 | AGM 16 | 2916.96 | 41.5 | 33.63 | 40.63 | 41.5 | 33.63 | 14920 | 1.56 | 0.99 | 33.7881 | -118.011 | 47.336
GWD 14930 | Girth Weld |  | 46307.67 | 0.67 | 0.25 | 35000 | SMLS | 8.625 | 600 | [10 empty] | AGM 15 | 159.38 | AGM 16 | 2883.33 | 33.63 | 1.56 | 41.5 | 33.63 | 1.56 | 14930 | 0.99 | 5.12 | 33.7882 | -118.011 | 47.229
BND 145 | Bend |  | 46308.35 | 0.88 | 0.25 | 35000 | SMLS | 8.625 | 600 |  |  | 24.541 | [7 empty] | AGM 15 | 160.06 | AGM 16 | 2882.66 | 0.67 | 0.88 | 41.5 | 33.63 | 1.56 | 14930 | 0.99 | 5.12 | 33.7882 | -118.011 | 47.22 | 3.0D 47.7 deg right turn over bend
GWD 14940 | Girth Weld |  | 46309.23 | 0.99 | 0.28 | 35000 | ERW | 8.625 | 600 | [10 empty] | AGM 15 | 160.94 | AGM 16 | 2881.77 | 1.56 | 0.99 | 33.63 | 1.56 | 0.99 | 14940 | 5.12 | 1 | 33.7882 | -118.011 | 47.2
GWD 14950 | Girth Weld |  | 46310.22 | 5.12 | 0.25 | 35000 | ERW | 8.625 | 600 | [10 empty] | AGM 15 | 161.93 | AGM 16 | 2880.78 | 0.99 | 5.12 | 1.56 | 0.99 | 5.12 | 14950 | 1 | 1.73 | 33.7882 | -118.011 | 47.167 | Estimated WT 0.250
GWD 14960 | Girth Weld |  | 46315.34 | 1 | 0.28 | 35000 | ERW | 8.625 | 600 | [10 empty] | AGM 15 | 167.05 | AGM 16 | 2875.67 | 5.12 | 1 | 0.99 | 5.12 | 1 | 14960 | 1.73 | 24.98 | 33.7882 | -118.011 | 46.993
GWD 14970 | Girth Weld |  | 46316.34 | 0.8 | 0.28 | 35000 | ERW | 8.625 | 600 | [10 empty] | AGM 15 | 168.05 | AGM 16 | 2874.66 | 1 | 1.73 | 5.12 | 1 | 1.73 | 14970 | 24.98 | 21.22 | 33.7882 | -118.011 | 46.964
BND 146 | Bend |  | 46317.14 | 0.92 | 0.28 | 35000 | ERW | 8.625 | 600 |  |  | 25.063 | [7 empty] | AGM 15 | 168.86 | AGM 16 | 2873.86 | 0.8 | 0.92 | 5.12 | 1 | 1.73 | 14970 | 24.98 | 21.22 | 33.7882 | -118.011 | 46.948 | 3.0D 47.7 deg left turn sag bend
GWD 14980 | Girth Weld |  | 46318.07 | 24.98 | 0.28 | 35000 | ERW | 8.625 | 600 | [10 empty] | AGM 15 | 169.78 | AGM 16 | 2872.94 | 1.73 | 24.98 | 1 | 1.73 | 24.98 | 14980 | 21.22 | 17.54 | 33.7882 | -118.011 | 46.938
GWD 14990 | Girth Weld |  | 46343.04 | 21.22 | 0.25 | 35000 | ERW | 8.625 | 600 | [10 empty] | AGM 15 | 194.75 | AGM 16 | 2847.96 | 24.98 | 21.22 | 1.73 | 24.98 | 21.22 | 14990 | 17.54 | 42.69 | 33.7882 | -118.011 | 46.904 | Estimated WT 0.250
GWD 15000 | Girth Weld |  | 46364.26 | 17.54 | 0.28 | 35000 | ERW | 8.625 | 600 | [10 empty] | AGM 15 | 215.97 | AGM 16 | 2826.75 | 21.22 | 17.54 | 24.98 | 21.22 | 17.54 | 15000 | 42.69 | 38.18 | 33.7883 | -118.011 | 46.844
GWD 15010 | Girth Weld |  | 46381.8 | 42.69 | 0.28 | 35000 | ERW | 8.625 | 600 | [10 empty] | AGM 15 | 233.51 | AGM 16 | 2809.2 | 17.54 | 42.69 | 21.22 | 17.54 | 42.69 | 15010 | 38.18 | 42.49 | 33.7884 | -118.011 | 46.562
GWD 15020 | Girth Weld |  | 46424.49 | 38.18 | 0.28 | 35000 | ERW | 8.625 | 600 | [10 empty] | AGM 15 | 276.2 | AGM 16 | 2766.52 | 42.69 | 38.18 | 17.54 | 42.69 | 38.18 | 15020 | 42.49 | 40.87 | 33.7885 | -118.011 | 46.046
GWD 15030 | Girth Weld |  | 46462.67 | 42.49 | 0.28 | 35000 | ERW | 8.625 | 600 | [10 empty] | AGM 15 | 314.38 | AGM 16 | 2728.34 | 38.18 | 42.49 | 42.69 | 38.18 | 42.49 | 15030 | 40.87 | 41.27 | 33.7886 | -118.011 | 46.46
GWD 15040 | Girth Weld |  | 46505.16 | 40.87 | 0.28 | 35000 | ERW | 8.625 | 600 | [10 empty] | AGM 15 | 356.87 | AGM 16 | 2685.85 | 42.49 | 40.87 | 38.18 | 42.49 | 40.87 | 15040 | 41.27 | 40.92 | 33.7887 | -118.011 | 46.716
GWD 15050 | Girth Weld |  | 46546.03 | 41.27 | 0.28 | 35000 | ERW | 8.625 | 600 | [10 empty] | AGM 15 | 397.74 | AGM 16 | 2644.97 | 40.87 | 41.27 | 42.49 | 40.87 | 41.27 | 15050 | 40.92 | 42.76 | 33.7888 | -118.011 | 46.315
GWD 15060 | Girth Weld |  | 46587.3 | 40.92 | 0.28 | 35000 | ERW | 8.625 | 600 | [10 empty] | AGM 15 | 439.02 | AGM 16 | 2603.7 | 41.27 | 40.92 | 40.87 | 41.27 | 40.92 | 15060 | 42.76 | 42.78 | 33.7889 | -118.011 | 46.296
GWD 15070 | Girth Weld |  | 46628.22 | 42.76 | 0.28 | 35000 | ERW | 8.625 | 600 | [10 empty] | AGM 15 | 479.94 | AGM 16 | 2562.78 | 40.92 | 42.76 | 41.27 | 40.92 | 42.76 | 15070 | 42.78 | 42.42 | 33.789 | -118.011 | 46.628
GWD 15080 | Girth Weld |  | 46670.99 | 42.78 | 0.28 | 35000 | ERW | 8.625 | 600 | [10 empty] | AGM 15 | 522.7 | AGM 16 | 2520.02 | 42.76 | 42.78 | 40.92 | 42.76 | 42.78 | 15080 | 42.42 | 41.22 | 33.7891 | -118.011 | 46.699
GWD 15090 | Girth Weld |  | 46713.77 | 42.42 | 0.28 | 35000 | ERW | 8.625 | 600 | [10 empty] | AGM 15 | 565.48 | AGM 16 | 2477.23 | 42.78 | 42.42 | 42.76 | 42.78 | 42.42 | 15090 | 41.22 | 41.56 | 33.7893 | -118.011 | 46.897
GWD 15100 | Girth Weld |  | 46756.19 | 41.22 | 0.28 | 35000 | ERW | 8.625 | 600 | [10 empty] | AGM 15 | 607.9 | AGM 16 | 2434.81 | 42.42 | 41.22 | 42.78 | 42.42 | 41.22 | 15100 | 41.56 | 41.79 | 33.7894 | -118.011 | 47.362
GWD 15110 | Girth Weld |  | 46797.41 | 41.56 | 0.28 | 35000 | ERW | 8.625 | 600 | [10 empty] | AGM 15 | 649.13 | AGM 16 | 2393.59 | 41.22 | 41.56 | 42.42 | 41.22 | 41.56 | 15110 | 41.79 | 42.48 | 33.7895 | -118.011 | 47.005
GWD 15120 | Girth Weld |  | 46838.97 | 41.79 | 0.28 | 35000 | ERW | 8.625 | 600 | [10 empty] | AGM 15 | 690.68 | AGM 16 | 2352.03 | 41.56 | 41.79 | 41.22 | 41.56 | 41.79 | 15120 | 42.48 | 41 | 33.7896 | -118.011 | 47.02
GWD 15130 | Girth Weld |  | 46880.76 | 42.48 | 0.28 | 35000 | ERW | 8.625 | 600 | [10 empty] | AGM 15 | 732.48 | AGM 16 | 2310.24 | 41.79 | 42.48 | 41.56 | 41.79 | 42.48 | 15130 | 41 | 42.47 | 33.7897 | -118.011 | 47.25
GWD 15140 | Girth Weld |  | 46923.24 | 41 | 0.28 | 35000 | ERW | 8.625 | 600 | [10 empty] | AGM 15 | 774.96 | AGM 16 | 2267.76 | 42.48 | 41 | 41.79 | 42.48 | 41 | 15140 | 42.47 | 41.2 | 33.7898 | -118.011 | 47.706
GWD 15150 | Girth Weld |  | 46964.24 | 42.47 | 0.28 | 35000 | ERW | 8.625 | 600 | [10 empty] | AGM 15 | 815.96 | AGM 16 | 2226.76 | 41 | 42.47 | 42.48 | 41 | 42.47 | 15150 | 41.2 | 41.81 | 33.79 | -118.011 | 47.489
GWD 15160 | Girth Weld |  | 47006.71 | 41.2 | 0.28 | 35000 | ERW | 8.625 | 600 | [10 empty] | AGM 15 | 858.43 | AGM 16 | 2184.29 | 42.47 | 41.2 | 41 | 42.47 | 41.2 | 15160 | 41.81 | 42.7 | 33.7901 | -118.011 | 48.008
GWD 15170 | Girth Weld |  | 47047.92 | 41.81 | 0.28 | 35000 | ERW | 8.625 | 600 | [10 empty] | AGM 15 | 899.63 | AGM 16 | 2143.09 | 41.2 | 41.81 | 42.47 | 41.2 | 41.81 | 15170 | 42.7 | 41.69 | 33.7902 | -118.011 | 48.136
GWD 15180 | Girth Weld |  | 47089.72 | 42.7 | 0.28 | 35000 | ERW | 8.625 | 600 | [10 empty] | AGM 15 | 941.43 | AGM 16 | 2101.28 | 41.81 | 42.7 | 41.2 | 41.81 | 42.7 | 15180 | 41.69 | 42.24 | 33.7903 | -118.011 | 48.406
GWD 15190 | Girth Weld |  | 47132.42 | 41.69 | 0.28 | 35000 | ERW | 8.625 | 600 | [10 empty] | AGM 15 | 984.13 | AGM 16 | 2058.58 | 42.7 | 41.69 | 41.81 | 42.7 | 41.69 | 15190 | 42.24 | 41.99 | 33.7904 | -118.011 | 48.341
GWD 15200 | Girth Weld |  | 47174.11 | 42.24 | 0.28 | 35000 | ERW | 8.625 | 600 | [10 empty] | AGM 15 | 1025.82 | AGM 16 | 2016.89 | 41.69 | 42.24 | 42.7 | 41.69 | 42.24 | 15200 | 41.99 | 42.46 | 33.7905 | -118.011 | 47.92
GWD 15210 | Girth Weld |  | 47216.35 | 41.99 | 0.28 | 35000 | ERW | 8.625 | 600 | [10 empty] | AGM 15 | 1068.06 | AGM 16 | 1974.66 | 42.24 | 41.99 | 41.69 | 42.24 | 41.99 | 15210 | 42.46 | 42.46 | 33.7906 | -118.011 | 47.191
GWD 15220 | Girth Weld |  | 47258.34 | 42.46 | 0.28 | 35000 | ERW | 8.625 | 600 | [10 empty] | AGM 15 | 1110.05 | AGM 16 | 1932.67 | 41.99 | 42.46 | 42.24 | 41.99 | 42.46 | 15220 | 42.46 | 42.28 | 33.7908 | -118.011 | 46.889
GWD 15230 | Girth Weld |  | 47300.8 | 42.46 | 0.28 | 35000 | ERW | 8.625 | 600 | [10 empty] | AGM 15 | 1152.51 | AGM 16 | 1890.21 | 42.46 | 42.46 | 41.99 | 42.46 | 42.46 | 15230 | 42.28 | 41.77 | 33.7909 | -118.011 | 47.191
GWD 15240 | Girth Weld |  | 47343.26 | 42.28 | 0.28 | 35000 | ERW | 8.625 | 600 | [10 empty] | AGM 15 | 1194.97 | AGM 16 | 1847.75 | 42.46 | 42.28 | 42.46 | 42.46 | 42.28 | 15240 | 41.77 | 42.03 | 33.791 | -118.011 | 47.312
GWD 15250 | Girth Weld |  | 47385.54 | 41.77 | 0.28 | 35000 | ERW | 8.625 | 600 | [10 empty] | AGM 15 | 1237.25 | AGM 16 | 1805.46 | 42.28 | 41.77 | 42.46 | 42.28 | 41.77 | 15250 | 42.03 | 39.05 | 33.7911 | -118.011 | 47.358
GWD 15260 | Girth Weld |  | 47427.31 | 42.03 | 0.28 | 35000 | ERW | 8.625 | 600 | [10 empty] | AGM 15 | 1279.02 | AGM 16 | 1763.69 | 41.77 | 42.03 | 42.28 | 41.77 | 42.03 | 15260 | 39.05 | 43.2 | 33.7912 | -118.011 | 48.24
GWD 15270 | Girth Weld |  | 47469.34 | 39.05 | 0.28 | 35000 | ERW | 8.625 | 600 | [10 empty] | AGM 15 | 1321.06 | AGM 16 | 1721.66 | 42.03 | 39.05 | 41.77 | 42.03 | 39.05 | 15270 | 43.2 | 41.6 | 33.7913 | -118.011 | 48.211
GWD 15280 | Girth Weld |  | 47508.39 | 43.2 | 0.28 | 35000 | ERW | 8.625 | 600 | [10 empty] | AGM 15 | 1360.11 | AGM 16 | 1682.61 | 39.05 | 43.2 | 42.03 | 39.05 | 43.2 | 15280 | 41.6 | 42.04 | 33.7915 | -118.0109 | 48.116
GWD 15290 | Girth Weld |  | 47551.6 | 41.6 | 0.28 | 35000 | ERW | 8.625 | 600 | [10 empty] | AGM 15 | 1403.31 | AGM 16 | 1639.41 | 43.2 | 41.6 | 39.05 | 43.2 | 41.6 | 15290 | 42.04 | 36.16 | 33.7916 | -118.0109 | 48.174
GWD 15300 | Girth Weld |  | 47593.19 | 42.04 | 0.28 | 35000 | ERW | 8.625 | 600 | [10 empty] | AGM 15 | 1444.91 | AGM 16 | 1597.81 | 41.6 | 42.04 | 43.2 | 41.6 | 42.04 | 15300 | 36.16 | 41.05 | 33.7917 | -118.0109 | 48.268
GWD 15310 | Girth Weld |  | 47635.23 | 36.16 | 0.28 | 35000 | ERW | 8.625 | 600 | [10 empty] | AGM 15 | 1486.94 | AGM 16 | 1555.78 | 42.04 | 36.16 | 41.6 | 42.04 | 36.16 | 15310 | 41.05 | 42.68 | 33.7918 | -118.0109 | 48.258
GWD 15320 | Girth Weld |  | 47671.39 | 41.05 | 0.28 | 35000 | ERW | 8.625 | 600 | [10 empty] | AGM 15 | 1523.1 | AGM 16 | 1519.62 | 36.16 | 41.05 | 42.04 | 36.16 | 41.05 | 15320 | 42.68 | 40.97 | 33.7919 | -118.0109 | 48.248
GWD 15330 | Girth Weld |  | 47712.43 | 42.68 | 0.28 | 35000 | ERW | 8.625 | 600 | [10 empty] | AGM 15 | 1564.15 | AGM 16 | 1478.57 | 41.05 | 42.68 | 36.16 | 41.05 | 42.68 | 15330 | 40.97 | 41.48 | 33.792 | -118.0109 | 48.185
GWD 15340 | Girth Weld |  | 47755.11 | 40.97 | 0.28 | 35000 | ERW | 8.625 | 600 | [10 empty] | AGM 15 | 1606.82 | AGM 16 | 1435.89 | 42.68 | 40.97 | 41.05 | 42.68 | 40.97 | 15340 | 41.48 | 41.95 | 33.7921 | -118.0109 | 48.259
GWD 15350 | Girth Weld |  | 47796.08 | 41.48 | 0.28 | 35000 | ERW | 8.625 | 600 | [10 empty] | AGM 15 | 1647.79 | AGM 16 | 1394.92 | 40.97 | 41.48 | 42.68 | 40.97 | 41.48 | 15350 | 41.95 | 42.03 | 33.7922 | -118.0109 | 48.546
GWD 15360 | Girth Weld |  | 47837.56 | 41.95 | 0.28 | 35000 | ERW | 8.625 | 600 | [10 empty] | AGM 15 | 1689.27 | AGM 16 | 1353.45 | 41.48 | 41.95 | 40.97 | 41.48 | 41.95 | 15360 | 42.03 | 42.13 | 33.7924 | -118.0109 | 48.337
GWD 15370 | Girth Weld |  | 47879.51 | 42.03 | 0.28 | 35000 | ERW | 8.625 | 600 | [10 empty] | AGM 15 | 1731.22 | AGM 16 | 1311.5 | 41.95 | 42.03 | 41.48 | 41.95 | 42.03 | 15370 | 42.13 | 42.14 | 33.7925 | -118.0109 | 48.11
GWD 15380 | Girth Weld |  | 47921.54 | 42.13 | 0.28 | 35000 | ERW | 8.625 | 600 | [10 empty] | AGM 15 | 1773.25 | AGM 16 | 1269.47 | 42.03 | 42.13 | 41.95 | 42.03 | 42.13 | 15380 | 42.14 | 38.28 | 33.7926 | -118.0109 | 48.336
GWD 15390 | Girth Weld |  | 47963.67 | 42.14 | 0.28 | 35000 | ERW | 8.625 | 600 | [10 empty] | AGM 15 | 1815.38 | AGM 16 | 1227.33 | 42.13 | 42.14 | 42.03 | 42.13 | 42.14 | 15390 | 38.28 | 31.47 | 33.7927 | -118.0109 | 48.102
GWD 15400 | Girth Weld |  | 48005.81 | 38.28 | 0.28 | 35000 | ERW | 8.625 | 600 | [10 empty] | AGM 15 | 1857.52 | AGM 16 | 1185.19 | 42.14 | 38.28 | 42.13 | 42.14 | 38.28 | 15400 | 31.47 | 4.79 | 33.7928 | -118.0109 | 48.24
GWD 15410 | Girth Weld |  | 48044.09 | 31.47 | 0.28 | 35000 | ERW | 8.625 | 600 | [10 empty] | AGM 15 | 1895.8 | AGM 16 | 1146.92 | 38.28 | 31.47 | 42.14 | 38.28 | 31.47 | 15410 | 4.79 | 40.84 | 33.7929 | -118.0109 | 48.188
GWD 15420 | Girth Weld |  | 48075.55 | 4.79 | 0.25 | 35000 | ERW | 8.625 | 600 | [10 empty] | AGM 15 | 1927.27 | AGM 16 | 1115.45 | 31.47 | 4.79 | 38.28 | 31.47 | 4.79 | 15420 | 40.84 | 31.07 | 33.793 | -118.0109 | 47.901 | Estimated WT 0.250
GWD 15430 | Girth Weld |  | 48080.35 | 40.84 | 0.25 | 35000 | ERW | 8.625 | 600 | [10 empty] | AGM 15 | 1932.06 | AGM 16 | 1110.66 | 4.79 | 40.84 | 31.47 | 4.79 | 40.84 | 15430 | 31.07 | 41.62 | 33.793 | -118.0109 | 47.881
GWD 15440 | Girth Weld |  | 48121.18 | 31.07 | 0.25 | 35000 | ERW | 8.625 | 600 | [10 empty] | AGM 15 | 1972.9 | AGM 16 | 1069.82 | 40.84 | 31.07 | 4.79 | 40.84 | 31.07 | 15440 | 41.62 | 38.34 | 33.7931 | -118.0109 | 48.839
GWD 15450 | Girth Weld |  | 48152.26 | 41.62 | 0.25 | 35000 | ERW | 8.625 | 600 | [10 empty] | AGM 15 | 2003.97 | AGM 16 | 1038.75 | 31.07 | 41.62 | 40.84 | 31.07 | 41.62 | 15450 | 38.34 | 41.22 | 33.7932 | -118.0109 | 48.907
GWD 15460 | Girth Weld |  | 48193.88 | 38.34 | 0.25 | 35000 | ERW | 8.625 | 600 | [10 empty] | AGM 15 | 2045.59 | AGM 16 | 997.12 | 41.62 | 38.34 | 31.07 | 41.62 | 38.34 | 15460 | 41.22 | 41.53 | 33.7933 | -118.0109 | 49.021
GWD 15470 | Girth Weld |  | 48232.22 | 41.22 | 0.25 | 35000 | ERW | 8.625 | 600 | [10 empty] | AGM 15 | 2083.93 | AGM 16 | 958.78 | 38.34 | 41.22 | 41.62 | 38.34 | 41.22 | 15470 | 41.53 | 39.16 | 33.7934 | -118.0109 | 48.89
GWD 15480 | Girth Weld |  | 48273.44 | 23.81 | 0.25 | 35000 | ERW | 8.625 | 600 | [10 empty] | AGM 15 | 2125.16 | AGM 16 | 917.56 | 41.22 | 41.53 | 38.34 | 41.22 | 41.53 | 15480 | 39.16 | 33.74 | 33.7936 | -118.0109 | 49.193
DNT 6 | Deformation |  | 48297.26 | 17.71 | 0.25 | 35000 | ERW | 8.625 | 600 | 2.0025 | 0.173 | 4.414 | 2.6 | 5:27 | [5 empty] | AGM 15 | 2148.97 | AGM 16 | 893.75 | 23.81 | 17.71 | 38.34 | 41.22 | 41.53 | 15480 | 39.16 | 33.74 | 33.7936 | -118.0109 | 49.421
GWD 15490 | Girth Weld |  | 48314.97 | 39.16 | 0.25 | 35000 | ERW | 8.625 | 600 | [10 empty] | AGM 15 | 2166.68 | AGM 16 | 876.03 | 41.53 | 39.16 | 41.22 | 41.53 | 39.16 | 15490 | 33.74 | 40.24 | 33.7937 | -118.0109 | 49.517
GWD 15500 | Girth Weld |  | 48354.13 | 33.74 | 0.25 | 35000 | ERW | 8.625 | 600 | [10 empty] | AGM 15 | 2205.85 | AGM 16 | 836.87 | 39.16 | 33.74 | 41.53 | 39.16 | 33.74 | 15500 | 40.24 | 41.84 | 33.7938 | -118.0109 | 49.676
GWD 15510 | Girth Weld |  | 48387.88 | 40.24 | 0.25 | 35000 | ERW | 8.625 | 600 | [10 empty] | AGM 15 | 2239.59 | AGM 16 | 803.13 | 33.74 | 40.24 | 39.16 | 33.74 | 40.24 | 15510 | 41.84 | 40.07 | 33.7939 | -118.0109 | 49.741
GWD 15520 | Girth Weld |  | 48428.12 | 41.84 | 0.25 | 35000 | SMLS | 8.625 | 600 | [10 empty] | AGM 15 | 2279.83 | AGM 16 | 762.89 | 40.24 | 41.84 | 33.74 | 40.24 | 41.84 | 15520 | 40.07 | 40.79 | 33.794 | -118.0109 | 49.791
GWD 15530 | Girth Weld |  | 48469.96 | 40.07 | 0.25 | 35000 | ERW | 8.625 | 600 | [10 empty] | AGM 15 | 2321.67 | AGM 16 | 721.04 | 41.84 | 40.07 | 40.24 | 41.84 | 40.07 | 15530 | 40.79 | 41.03 | 33.7941 | -118.0109 | 50.02
GWD 15540 | Girth Weld |  | 48510.03 | 40.79 | 0.25 | 35000 | ERW | 8.625 | 600 | [10 empty] | AGM 15 | 2361.74 | AGM 16 | 680.98 | 40.07 | 40.79 | 41.84 | 40.07 | 40.79 | 15540 | 41.03 | 42.33 | 33.7942 | -118.0109 | 50.128
GWD 15550 | Girth Weld |  | 48550.82 | 41.03 | 0.25 | 35000 | ERW | 8.625 | 600 | [10 empty] | AGM 15 | 2402.53 | AGM 16 | 640.19 | 40.79 | 41.03 | 40.07 | 40.79 | 41.03 | 15550 | 42.33 | 40.78 | 33.7943 | -118.0109 | 50.449
GWD 15560 | Girth Weld |  | 48591.84 | 42.33 | 0.25 | 35000 | ERW | 8.625 | 600 | [10 empty] | AGM 15 | 2443.56 | AGM 16 | 599.16 | 41.03 | 42.33 | 40.79 | 41.03 | 42.33 | 15560 | 40.78 | 41.54 | 33.7944 | -118.0109 | 50.477
GWD 15570 | Girth Weld |  | 48634.18 | 40.78 | 0.25 | 35000 | ERW | 8.625 | 600 | [10 empty] | AGM 15 | 2485.89 | AGM 16 | 556.83 | 42.33 | 40.78 | 41.03 | 42.33 | 40.78 | 15570 | 41.54 | 41.1 | 33.7945 | -118.0109 | 50.814
GWD 15580 | Girth Weld |  | 48674.96 | 41.54 | 0.25 | 35000 | ERW | 8.625 | 600 | [10 empty] | AGM 15 | 2526.67 | AGM 16 | 516.05 | 40.78 | 41.54 | 42.33 | 40.78 | 41.54 | 15580 | 41.1 | 40.28 | 33.7947 | -118.0109 | 50.794
GWD 15590 | Girth Weld |  | 48716.5 | 41.1 | 0.25 | 35000 | ERW | 8.625 | 600 | [10 empty] | AGM 15 | 2568.21 | AGM 16 | 474.51 | 41.54 | 41.1 | 40.78 | 41.54 | 41.1 | 15590 | 40.28 | 42.17 | 33.7948 | -118.0109 | 50.993
GWD 15600 | Girth Weld |  | 48757.6 | 40.28 | 0.25 | 35000 | ERW | 8.625 | 600 | [10 empty] | AGM 15 | 2609.31 | AGM 16 | 433.4 | 41.1 | 40.28 | 41.54 | 41.1 | 40.28 | 15600 | 42.17 | 40.58 | 33.7949 | -118.0109 | 51.401
GWD 15610 | Girth Weld |  | 48797.88 | 42.17 | 0.25 | 35000 | ERW | 8.625 | 600 | [10 empty] | AGM 15 | 2649.6 | AGM 16 | 393.12 | 40.28 | 42.17 | 41.1 | 40.28 | 42.17 | 15610 | 40.58 | 40.67 | 33.795 | -118.0109 | 51.663
GWD 15620 | Girth Weld |  | 48840.05 | 40.58 | 0.25 | 35000 | ERW | 8.625 | 600 | [10 empty] | AGM 15 | 2691.76 | AGM 16 | 350.95 | 42.17 | 40.58 | 40.28 | 42.17 | 40.58 | 15620 | 40.67 | 42.39 | 33.7951 | -118.0109 | 51.987
GWD 15630 | Girth Weld |  | 48880.63 | 40.67 | 0.25 | 35000 | ERW | 8.625 | 600 | [10 empty] | AGM 15 | 2732.34 | AGM 16 | 310.38 | 40.58 | 40.67 | 42.17 | 40.58 | 40.67 | 15630 | 42.39 | 41.37 | 33.7952 | -118.0109 | 51.958
GWD 15640 | Girth Weld |  | 48921.3 | 42.39 | 0.25 | 35000 | ERW | 8.625 | 600 | [10 empty] | AGM 15 | 2773.01 | AGM 16 | 269.71 | 40.67 | 42.39 | 40.58 | 40.67 | 42.39 | 15640 | 41.37 | 41.13 | 33.7953 | -118.0109 | 51.898
GWD 15650 | Girth Weld |  | 48963.69 | 41.37 | 0.25 | 35000 | ERW | 8.625 | 600 | [10 empty] | AGM 15 | 2815.4 | AGM 16 | 227.31 | 42.39 | 41.37 | 40.67 | 42.39 | 41.37 | 15650 | 41.13 | 39.41 | 33.7955 | -118.0109 | 51.9
GWD 15660 | Girth Weld |  | 49005.06 | 41.13 | 0.25 | 35000 | ERW | 8.625 | 600 | [10 empty] | AGM 15 | 2856.78 | AGM 16 | 185.94 | 41.37 | 41.13 | 42.39 | 41.37 | 41.13 | 15660 | 39.41 | 40.82 | 33.7956 | -118.0109 | 52.104
GWD 15670 | Girth Weld |  | 49046.2 | 39.41 | 0.25 | 35000 | ERW | 8.625 | 600 | [10 empty] | AGM 15 | 2897.91 | AGM 16 | 144.81 | 41.13 | 39.41 | 41.37 | 41.13 | 39.41 | 15670 | 40.82 | 39.01 | 33.7957 | -118.0109 | 52.281
GWD 15680 | Girth Weld |  | 49085.6 | 40.82 | 0.25 | 35000 | ERW | 8.625 | 600 | [10 empty] | AGM 15 | 2937.32 | AGM 16 | 105.4 | 39.41 | 40.82 | 41.13 | 39.41 | 40.82 | 15680 | 39.01 | 41.12 | 33.7958 | -118.0109 | 52.249
GWD 15690 | Girth Weld |  | 49126.42 | 39.01 | 0.25 | 35000 | ERW | 8.625 | 600 | [10 empty] | AGM 15 | 2978.14 | AGM 16 | 64.58 | 40.82 | 39.01 | 39.41 | 40.82 | 39.01 | 15690 | 41.12 | 42.79 | 33.7959 | -118.0109 | 51.788
GWD 15700 | Girth Weld |  | 49165.44 | 25.57 | 0.25 | 35000 | ERW | 8.625 | 600 | [10 empty] | AGM 15 | 3017.15 | AGM 16 | 25.57 | 39.01 | 41.12 | 40.82 | 39.01 | 41.12 | 15700 | 42.79 | 42.44 | 33.796 | -118.0109 | 51.182
MRK 14 | Marker |  | 49191 | 15.55 | 0.25 | 35000 | ERW | 8.625 | 600 |  |  |  |  | 11:29 | [5 empty] | AGM 15 | 3042.72 | AGM 17 | 2794.95 | 25.57 | 15.55 | 40.82 | 39.01 | 41.12 | 15700 | 42.79 | 42.44 | 33.7961 | -118.0109 | 51.336 | AGM 16 2' East of Knott St Curb on Sidewalk
GWD 15710 | Girth Weld |  | 49206.55 | 42.79 | 0.25 | 35000 | ERW | 8.625 | 600 | [10 empty] | AGM 16 | 15.55 | AGM 17 | 2779.4 | 41.12 | 42.79 | 39.01 | 41.12 | 42.79 | 15710 | 42.44 | 40.56 | 33.7961 | -118.0109 | 51.503
GWD 15720 | Girth Weld |  | 49249.34 | 42.44 | 0.25 | 35000 | ERW | 8.625 | 600 | [10 empty] | AGM 16 | 58.34 | AGM 17 | 2736.61 | 42.79 | 42.44 | 41.12 | 42.79 | 42.44 | 15720 | 40.56 | 33.63 | 33.7962 | -118.0109 | 51.211
GWD 15730 | Girth Weld |  | 49291.78 | 40.56 | 0.25 | 35000 | ERW | 8.625 | 600 | [10 empty] | AGM 16 | 100.78 | AGM 17 | 2694.17 | 42.44 | 40.56 | 42.79 | 42.44 | 40.56 | 15730 | 33.63 | 41.64 | 33.7964 | -118.0109 | 51.249
GWD 15740 | Girth Weld |  | 49332.35 | 33.63 | 0.25 | 35000 | ERW | 8.625 | 600 | [10 empty] | AGM 16 | 141.34 | AGM 17 | 2653.6 | 40.56 | 33.63 | 42.44 | 40.56 | 33.63 | 15740 | 41.64 | 42.23 | 33.7965 | -118.0109 | 51.273
GWD 15750 | Girth Weld |  | 49365.98 | 41.64 | 0.25 | 35000 | ERW | 8.625 | 600 | [10 empty] | AGM 16 | 174.98 | AGM 17 | 2619.97 | 33.63 | 41.64 | 40.56 | 33.63 | 41.64 | 15750 | 42.23 | 40.77 | 33.7966 | -118.0109 | 50.769
GWD 15760 | Girth Weld |  | 49407.62 | 42.23 | 0.25 | 35000 | ERW | 8.625 | 600 | [10 empty] | AGM 16 | 216.62 | AGM 17 | 2578.33 | 41.64 | 42.23 | 33.63 | 41.64 | 42.23 | 15760 | 40.77 | 41.18 | 33.7967 | -118.0109 | 50.342
GWD 15770 | Girth Weld |  | 49449.85 | 40.77 | 0.25 | 35000 | ERW | 8.625 | 600 | [10 empty] | AGM 16 | 258.85 | AGM 17 | 2536.1 | 42.23 | 40.77 | 41.64 | 42.23 | 40.77 | 15770 | 41.18 | 42.2 | 33.7968 | -118.0109 | 49.886
GWD 15780 | Girth Weld |  | 49490.62 | 41.18 | 0.25 | 35000 | ERW | 8.625 | 600 | [10 empty] | AGM 16 | 299.62 | AGM 17 | 2495.33 | 40.77 | 41.18 | 42.23 | 40.77 | 41.18 | 15780 | 42.2 | 41.93 | 33.7969 | -118.0109 | 50.202
GWD 15790 | Girth Weld |  | 49531.8 | 42.2 | 0.25 | 35000 | ERW | 8.625 | 600 | [10 empty] | AGM 16 | 340.79 | AGM 17 | 2454.15 | 41.18 | 42.2 | 40.77 | 41.18 | 42.2 | 15790 | 41.93 | 39.82 | 33.797 | -118.0109 | 49.834
GWD 15800 | Girth Weld |  | 49574 | 41.93 | 0.25 | 35000 | ERW | 8.625 | 600 | [10 empty] | AGM 16 | 383 | AGM 17 | 2411.95 | 42.2 | 41.93 | 41.18 | 42.2 | 41.93 | 15800 | 39.82 | 41.61 | 33.7971 | -118.0109 | 49.732
GWD 15810 | Girth Weld |  | 49615.94 | 39.82 | 0.25 | 35000 | ERW | 8.625 | 600 | [10 empty] | AGM 16 | 424.93 | AGM 17 | 2370.02 | 41.93 | 39.82 | 42.2 | 41.93 | 39.82 | 15810 | 41.61 | 40.85 | 33.7973 | -118.0109 | 49.802
GWD 15820 | Girth Weld |  | 49655.76 | 41.61 | 0.25 | 35000 | ERW | 8.625 | 600 | [10 empty] | AGM 16 | 464.75 | AGM 17 | 2330.2 | 39.82 | 41.61 | 41.93 | 39.82 | 41.61 | 15820 | 40.85 | 40.43 | 33.7974 | -118.0109 | 49.741
GWD 15830 | Girth Weld |  | 49697.37 | 40.85 | 0.25 | 35000 | ERW | 8.625 | 600 | [10 empty] | AGM 16 | 506.37 | AGM 17 | 2288.58 | 41.61 | 40.85 | 39.82 | 41.61 | 40.85 | 15830 | 40.43 | 40.95 | 33.7975 | -118.0109 | 49.46
GWD 15840 | Girth Weld |  | 49738.22 | 40.43 | 0.25 | 35000 | ERW | 8.625 | 600 | [10 empty] | AGM 16 | 547.22 | AGM 17 | 2247.73 | 40.85 | 40.43 | 41.61 | 40.85 | 40.43 | 15840 | 40.95 | 38.17 | 33.7976 | -118.0109 | 49.373
GWD 15850 | Girth Weld |  | 49778.65 | 40.95 | 0.25 | 35000 | ERW | 8.625 | 600 | [10 empty] | AGM 16 | 587.65 | AGM 17 | 2207.3 | 40.43 | 40.95 | 40.85 | 40.43 | 40.95 | 15850 | 38.17 | 41.18 | 33.7977 | -118.0109 | 49.343
GWD 15860 | Girth Weld |  | 49819.59 | 38.17 | 0.25 | 35000 | ERW | 8.625 | 600 | [10 empty] | AGM 16 | 628.59 | AGM 17 | 2166.36 | 40.95 | 38.17 | 40.43 | 40.95 | 38.17 | 15860 | 41.18 | 42.69 | 33.7978 | -118.0109 | 49.133
GWD 15870 | Girth Weld |  | 49857.76 | 41.18 | 0.25 | 35000 | ERW | 8.625 | 600 | [10 empty] | AGM 16 | 666.76 | AGM 17 | 2128.19 | 38.17 | 41.18 | 40.95 | 38.17 | 41.18 | 15870 | 42.69 | 41.96 | 33.7979 | -118.0109 | 49.14
GWD 15880 | Girth Weld |  | 49898.94 | 42.69 | 0.25 | 35000 | ERW | 8.625 | 600 | [10 empty] | AGM 16 | 707.94 | AGM 17 | 2087.01 | 41.18 | 42.69 | 38.17 | 41.18 | 42.69 | 15880 | 41.96 | 40.96 | 33.798 | -118.0109 | 48.911
GWD 15890 | Girth Weld |  | 49941.63 | 41.96 | 0.25 | 35000 | ERW | 8.625 | 600 | [10 empty] | AGM 16 | 750.63 | AGM 17 | 2044.32 | 42.69 | 41.96 | 41.18 | 42.69 | 41.96 | 15890 | 40.96 | 42.09 | 33.7981 | -118.0109 | 48.938
GWD 15900 | Girth Weld |  | 49983.59 | 40.96 | 0.25 | 35000 | ERW | 8.625 | 600 | [10 empty] | AGM 16 | 792.58 | AGM 17 | 2002.36 | 41.96 | 40.96 | 42.69 | 41.96 | 40.96 | 15900 | 42.09 | 41.2 | 33.7983 | -118.0109 | 48.709
GWD 15910 | Girth Weld |  | 50024.55 | 42.09 | 0.25 | 35000 | ERW | 8.625 | 600 | [10 empty] | AGM 16 | 833.54 | AGM 17 | 1961.4 | 40.96 | 42.09 | 41.96 | 40.96 | 42.09 | 15910 | 41.2 | 40.23 | 33.7984 | -118.0109 | 48.869
GWD 15920 | Girth Weld |  | 50066.64 | 41.2 | 0.25 | 35000 | ERW | 8.625 | 600 | [10 empty] | AGM 16 | 875.63 | AGM 17 | 1919.32 | 42.09 | 41.2 | 40.96 | 42.09 | 41.2 | 15920 | 40.23 | 38.73 | 33.7985 | -118.0109 | 48.748
GWD 15930 | Girth Weld |  | 50107.84 | 40.23 | 0.25 | 35000 | ERW | 8.625 | 600 | [10 empty] | AGM 16 | 916.83 | AGM 17 | 1878.11 | 41.2 | 40.23 | 42.09 | 41.2 | 40.23 | 15930 | 38.73 | 40.26 | 33.7986 | -118.0109 | 48.721
GWD 15940 | Girth Weld |  | 50148.07 | 38.73 | 0.25 | 35000 | ERW | 8.625 | 600 | [10 empty] | AGM 16 | 957.07 | AGM 17 | 1837.88 | 40.23 | 38.73 | 41.2 | 40.23 | 38.73 | 15940 | 40.26 | 39.14 | 33.7987 | -118.0109 | 48.718
GWD 15950 | Girth Weld |  | 50186.8 | 40.26 | 0.25 | 35000 | ERW | 8.625 | 600 | [10 empty] | AGM 16 | 995.8 | AGM 17 | 1799.15 | 38.73 | 40.26 | 40.23 | 38.73 | 40.26 | 15950 | 39.14 | 41.5 | 33.7988 | -118.0109 | 48.736
GWD 15960 | Girth Weld |  | 50227.06 | 39.14 | 0.25 | 35000 | ERW | 8.625 | 600 | [10 empty] | AGM 16 | 1036.06 | AGM 17 | 1758.89 | 40.26 | 39.14 | 38.73 | 40.26 | 39.14 | 15960 | 41.5 | 41.27 | 33.7989 | -118.0109 | 48.235
GWD 15970 | Girth Weld |  | 50266.2 | 41.5 | 0.25 | 35000 | ERW | 8.625 | 600 | [10 empty] | AGM 16 | 1075.2 | AGM 17 | 1719.75 | 39.14 | 41.5 | 40.26 | 39.14 | 41.5 | 15970 | 41.27 | 40.47 | 33.799 | -118.0109 | 49.195
GWD 15980 | Girth Weld |  | 50307.7 | 16.78 | 0.25 | 35000 | ERW | 8.625 | 600 | [10 empty] | AGM 16 | 1116.7 | AGM 17 | 1678.25 | 41.5 | 41.27 | 39.14 | 41.5 | 41.27 | 15980 | 40.47 | 31.36 | 33.7992 | -118.0109 | 50.005
CSG 10 | Casing Start |  | 50324.49 | 15.91 | 0.25 | 35000 | ERW | 8.625 | 600 |  |  | 190.876 | [7 empty] | AGM 16 | 1133.48 | AGM 17 | 1661.46 | 16.78 | 24.49 | 39.14 | 41.5 | 41.27 | 15980 | 40.47 | 31.36 | 33.7992 | -118.0109 | 50.454 | Casing - Start
CSG 10 | Casing End |  | 50340.39 | 8.58 | 0.25 | 35000 | ERW | 8.625 | 600 | [10 empty] | AGM 16 | 1149.39 | AGM 17 | 1645.56 | 32.69 | 8.58 | 39.14 | 41.5 | 41.27 | 15980 | 40.47 | 31.36 | 33.7992 | -118.0109 | 50.466 | Casing - End
GWD 15990 | Girth Weld |  | 50348.98 | 40.47 | 0.25 | 35000 | ERW | 8.625 | 600 | [10 empty] | AGM 16 | 1157.97 | AGM 17 | 1636.97 | 41.27 | 40.47 | 41.5 | 41.27 | 40.47 | 15990 | 31.36 | 1.46 | 33.7993 | -118.0109 | 50.236
GWD 16000 | Girth Weld |  | 50389.45 | 31.36 | 0.25 | 35000 | ERW | 8.625 | 600 | [10 empty] | AGM 16 | 1198.45 | AGM 17 | 1596.5 | 40.47 | 31.36 | 41.27 | 40.47 | 31.36 | 16000 | 1.46 | 1.56 | 33.7994 | -118.0109 | 49.26
GWD 16010 | Girth Weld |  | 50420.81 | 0.17 | 0.25 | 35000 | ERW | 8.625 | 600 | [10 empty] | AGM 16 | 1229.8 | AGM 17 | 1565.14 | 31.36 | 1.46 | 40.47 | 31.36 | 1.46 | 16010 | 1.56 | 1 | 33.7995 | -118.0109 | 49.491
BND 147 | Bend |  | 50420.98 | 1.28 | 0.25 | 35000 | ERW | 8.625 | 600 |  |  | 16.761 | [7 empty] | AGM 16 | 1229.98 | AGM 17 | 1564.97 | 0.17 | 1.28 | 40.47 | 31.36 | 1.46 | 16010 | 1.56 | 1 | 33.7995 | -118.0109 | 49.521 | 3.0D 41.4 deg right turn sag bend
GWD 16020 | Girth Weld |  | 50422.27 | 0.79 | 0.25 | 35000 | ERW | 8.625 | 600 | [10 empty] | AGM 16 | 1231.26 | AGM 17 | 1563.69 | 1.46 | 1.56 | 31.36 | 1.46 | 1.56 | 16020 | 1 | 19.5 | 33.7995 | -118.0109 | 50.152
BND 148 | Bend |  | 50423.05 | 0.77 | 0.25 | 35000 | ERW | 8.625 | 600 |  |  | 18.528 | [7 empty] | AGM 16 | 1232.05 | AGM 17 | 1562.9 | 0.79 | 0.77 | 31.36 | 1.46 | 1.56 | 16020 | 1 | 19.5 | 33.7995 | -118.0109 | 50.472 | 3.0D 37.9 deg left turn over bend
GWD 16030 | Girth Weld |  | 50423.82 | 1 | 0.28 | 35000 | ERW | 8.625 | 600 | [10 empty] | AGM 16 | 1232.82 | AGM 17 | 1562.13 | 1.56 | 1 | 1.46 | 1.56 | 1 | 16030 | 19.5 | 0.95 | 33.7995 | -118.0109 | 50.58
GWD 16040 | Girth Weld |  | 50424.82 | 19.5 | 0.25 | 35000 | ERW | 8.625 | 600 | [10 empty] | AGM 16 | 1233.81 | AGM 17 | 1561.13 | 1 | 19.5 | 1.56 | 1 | 19.5 | 16040 | 0.95 | 1.61 | 33.7995 | -118.0109 | 50.588 | Estimated WT 0.250
GWD 16050 | Girth Weld |  | 50444.32 | 0.95 | 0.28 | 35000 | ERW | 8.625 | 600 | [10 empty] | AGM 16 | 1253.32 | AGM 17 | 1541.63 | 19.5 | 0.95 | 1 | 19.5 | 0.95 | 16050 | 1.61 | 0.96 | 33.7995 | -118.0109 | 50.546
GWD 16060 | Girth Weld |  | 50445.28 | 0.69 | 0.28 | 35000 | ERW | 8.625 | 600 | [10 empty] | AGM 16 | 1254.27 | AGM 17 | 1540.67 | 0.95 | 1.61 | 19.5 | 0.95 | 1.61 | 16060 | 0.96 | 1.51 | 33.7995 | -118.0109 | 50.582
BND 149 | Bend |  | 50445.97 | 0.92 | 0.28 | 35000 | ERW | 8.625 | 600 |  |  | 19.331 | [7 empty] | AGM 16 | 1254.97 | AGM 17 | 1539.98 | 0.69 | 0.92 | 19.5 | 0.95 | 1.61 | 16060 | 0.96 | 1.51 | 33.7995 | -118.0109 | 50.466 | 3.0D 49.0 deg right turn over bend
GWD 16070 | Girth Weld |  | 50446.89 | 0.96 | 0.28 | 35000 | ERW | 8.625 | 600 | [10 empty] | AGM 16 | 1255.88 | AGM 17 | 1539.06 | 1.61 | 0.96 | 0.95 | 1.61 | 0.96 | 16070 | 1.51 | 4.57 | 33.7995 | -118.0109 | 50.012
GWD 16080 | Girth Weld |  | 50447.84 | 0.76 | 0.28 | 35000 | ERW | 8.625 | 600 | [10 empty] | AGM 16 | 1256.84 | AGM 17 | 1538.11 | 0.96 | 1.51 | 1.61 | 0.96 | 1.51 | 16080 | 4.57 | 9.05 | 33.7995 | -118.0109 | 49.383
BND 150 | Bend |  | 50448.6 | 0.76 | 0.28 | 35000 | ERW | 8.625 | 600 |  |  | 18.189 | [7 empty] | AGM 16 | 1257.6 | AGM 17 | 1537.35 | 0.76 | 0.76 | 1.61 | 0.96 | 1.51 | 16080 | 4.57 | 9.05 | 33.7995 | -118.0109 | 49.024 | 3.0D 46.6 deg left turn sag bend
GWD 16090 | Girth Weld |  | 50449.36 | 4.57 | 0.28 | 35000 | ERW | 8.625 | 600 | [10 empty] | AGM 16 | 1258.36 | AGM 17 | 1536.59 | 1.51 | 4.57 | 0.96 | 1.51 | 4.57 | 16090 | 9.05 | 47.21 | 33.7995 | -118.0109 | 48.897
GWD 16100 | Girth Weld |  | 50453.93 | 9.05 | 0.28 | 35000 | ERW | 8.625 | 600 | [10 empty] | AGM 16 | 1262.93 | AGM 17 | 1532.02 | 4.57 | 9.05 | 1.51 | 4.57 | 9.05 | 16100 | 47.21 | 46.89 | 33.7996 | -118.0109 | 49.047
GWD 16110 | Girth Weld |  | 50462.99 | 47.21 | 0.28 | 35000 | ERW | 8.625 | 600 | [10 empty] | AGM 16 | 1271.98 | AGM 17 | 1522.97 | 9.05 | 47.21 | 4.57 | 9.05 | 47.21 | 16110 | 46.89 | 46.58 | 33.7996 | -118.0109 | 49.416
GWD 16120 | Girth Weld |  | 50510.2 | 46.89 | 0.28 | 35000 | ERW | 8.625 | 600 | [10 empty] | AGM 16 | 1319.2 | AGM 17 | 1475.75 | 47.21 | 46.89 | 9.05 | 47.21 | 46.89 | 16120 | 46.58 | 46.85 | 33.7997 | -118.0109 | 50.215
GWD 16130 | Girth Weld |  | 50557.09 | 46.58 | 0.28 | 35000 | ERW | 8.625 | 600 | [10 empty] | AGM 16 | 1366.08 | AGM 17 | 1428.86 | 46.89 | 46.58 | 47.21 | 46.89 | 46.58 | 16130 | 46.85 | 47.1 | 33.7998 | -118.0109 | 50.199
GWD 16140 | Girth Weld |  | 50603.67 | 46.85 | 0.28 | 35000 | ERW | 8.625 | 600 | [10 empty] | AGM 16 | 1412.67 | AGM 17 | 1382.28 | 46.58 | 46.85 | 46.89 | 46.58 | 46.85 | 16140 | 47.1 | 46.24 | 33.8 | -118.0109 | 50.25
GWD 16150 | Girth Weld |  | 50650.52 | 47.1 | 0.28 | 35000 | ERW | 8.625 | 600 | [10 empty] | AGM 16 | 1459.51 | AGM 17 | 1335.43 | 46.85 | 47.1 | 46.58 | 46.85 | 47.1 | 16150 | 46.24 | 47.22 | 33.8001 | -118.0109 | 50.975
GWD 16160 | Girth Weld |  | 50697.62 | 46.24 | 0.28 | 35000 | ERW | 8.625 | 600 | [10 empty] | AGM 16 | 1506.61 | AGM 17 | 1288.34 | 47.1 | 46.24 | 46.85 | 47.1 | 46.24 | 16160 | 47.22 | 46.09 | 33.8002 | -118.0109 | 51.113
GWD 16170 | Girth Weld |  | 50743.86 | 47.22 | 0.28 | 35000 | ERW | 8.625 | 600 | [10 empty] | AGM 16 | 1552.85 | AGM 17 | 1242.1 | 46.24 | 47.22 | 47.1 | 46.24 | 47.22 | 16170 | 46.09 | 46.12 | 33.8004 | -118.0109 | 51.24
GWD 16180 | Girth Weld |  | 50791.07 | 46.09 | 0.28 | 35000 | ERW | 8.625 | 600 | [10 empty] | AGM 16 | 1600.07 | AGM 17 | 1194.88 | 47.22 | 46.09 | 46.24 | 47.22 | 46.09 | 16180 | 46.12 | 45.73 | 33.8005 | -118.0109 | 51.513
GWD 16190 | Girth Weld |  | 50837.17 | 46.12 | 0.28 | 35000 | ERW | 8.625 | 600 | [10 empty] | AGM 16 | 1646.17 | AGM 17 | 1148.78 | 46.09 | 46.12 | 47.22 | 46.09 | 46.12 | 16190 | 45.73 | 13.18 | 33.8006 | -118.0109 | 51.84
GWD 16200 | Girth Weld |  | 50883.29 | 45.73 | 0.28 | 35000 | ERW | 8.625 | 600 | [10 empty] | AGM 16 | 1692.29 | AGM 17 | 1102.66 | 46.12 | 45.73 | 46.09 | 46.12 | 45.73 | 16200 | 13.18 | 39.45 | 33.8007 | -118.0109 | 52.441
GWD 16210 | Girth Weld |  | 50929.02 | 13.18 | 0.28 | 35000 | ERW | 8.625 | 600 | [10 empty] | AGM 16 | 1738.02 | AGM 17 | 1056.93 | 45.73 | 13.18 | 46.12 | 45.73 | 13.18 | 16210 | 39.45 | 42.43 | 33.8009 | -118.0109 | 53.113
GWD 16220 | Girth Weld |  | 50942.2 | 39.45 | 0.28 | 35000 | ERW | 8.625 | 600 | [10 empty] | AGM 16 | 1751.19 | AGM 17 | 1043.75 | 13.18 | 39.45 | 45.73 | 13.18 | 39.45 | 16220 | 42.43 | 43.54 | 33.8009 | -118.0109 | 53.526
GWD 16230 | Girth Weld |  | 50981.64 | 31.59 | 0.28 | 35000 | ERW | 8.625 | 600 | [10 empty] | AGM 16 | 1790.64 | AGM 17 | 1004.31 | 39.45 | 42.43 | 13.18 | 39.45 | 42.43 | 16230 | 43.54 | 42.86 | 33.801 | -118.0109 | 53.845
DNT 7 | Deformation |  | 51013.23 | 10.84 | 0.28 | 35000 | ERW | 8.625 | 600 | 2.5659 | 0.221 | 6.554 | 3.409 | 6:55 | [5 empty] | AGM 16 | 1822.23 | AGM 17 | 972.72 | 31.59 | 10.84 | 13.18 | 39.45 | 42.43 | 16230 | 43.54 | 42.86 | 33.8011 | -118.0109 | 54.03
GWD 16240 | Girth Weld |  | 51024.08 | 43.54 | 0.28 | 35000 | ERW | 8.625 | 600 | [10 empty] | AGM 16 | 1833.07 | AGM 17 | 961.88 | 42.43 | 43.54 | 39.45 | 42.43 | 43.54 | 16240 | 42.86 | 43.02 | 33.8011 | -118.0109 | 54.018
GWD 16250 | Girth Weld |  | 51067.61 | 42.86 | 0.28 | 35000 | ERW | 8.625 | 600 | [10 empty] | AGM 16 | 1876.61 | AGM 17 | 918.34 | 43.54 | 42.86 | 42.43 | 43.54 | 42.86 | 16250 | 43.02 | 41.77 | 33.8012 | -118.0109 | 54.484
GWD 16260 | Girth Weld |  | 51110.48 | 43.02 | 0.28 | 35000 | ERW | 8.625 | 600 | [10 empty] | AGM 16 | 1919.47 | AGM 17 | 875.47 | 42.86 | 43.02 | 43.54 | 42.86 | 43.02 | 16260 | 41.77 | 42.38 | 33.8014 | -118.0109 | 54.537
GWD 16270 | Girth Weld |  | 51153.5 | 41.77 | 0.28 | 35000 | ERW | 8.625 | 600 | [10 empty] | AGM 16 | 1962.49 | AGM 17 | 832.45 | 43.02 | 41.77 | 42.86 | 43.02 | 41.77 | 16270 | 42.38 | 42.9 | 33.8015 | -118.0109 | 54.892
GWD 16280 | Girth Weld |  | 51195.26 | 42.38 | 0.28 | 35000 | ERW | 8.625 | 600 | [10 empty] | AGM 16 | 2004.26 | AGM 17 | 790.69 | 41.77 | 42.38 | 43.02 | 41.77 | 42.38 | 16280 | 42.9 | 41.93 | 33.8016 | -118.0109 | 54.877
GWD 16290 | Girth Weld |  | 51237.64 | 42.9 | 0.28 | 35000 | ERW | 8.625 | 600 | [10 empty] | AGM 16 | 2046.64 | AGM 17 | 748.31 | 42.38 | 42.9 | 41.77 | 42.38 | 42.9 | 16290 | 41.93 | 42.55 | 33.8017 | -118.0109 | 54.922
GWD 16300 | Girth Weld |  | 51280.54 | 41.93 | 0.28 | 35000 | ERW | 8.625 | 600 | [10 empty] | AGM 16 | 2089.54 | AGM 17 | 705.41 | 42.9 | 41.93 | 42.38 | 42.9 | 41.93 | 16300 | 42.55 | 42.78 | 33.8018 | -118.0109 | 54.808
GWD 16310 | Girth Weld |  | 51322.47 | 42.55 | 0.28 | 35000 | ERW | 8.625 | 600 | [10 empty] | AGM 16 | 2131.46 | AGM 17 | 663.48 | 41.93 | 42.55 | 42.9 | 41.93 | 42.55 | 16310 | 42.78 | 41.12 | 33.8019 | -118.0109 | 54.362
GWD 16320 | Girth Weld |  | 51365.02 | 42.78 | 0.28 | 35000 | ERW | 8.625 | 600 | [10 empty] | AGM 16 | 2174.01 | AGM 17 | 620.93 | 42.55 | 42.78 | 41.93 | 42.55 | 42.78 | 16320 | 41.12 | 42.17 | 33.8021 | -118.0109 | 54.157
GWD 16330 | Girth Weld |  | 51407.8 | 41.12 | 0.28 | 35000 | ERW | 8.625 | 600 | [10 empty] | AGM 16 | 2216.8 | AGM 17 | 578.15 | 42.78 | 41.12 | 42.55 | 42.78 | 41.12 | 16330 | 42.17 | 28.29 | 33.8022 | -118.0109 | 53.863
GWD 16340 | Girth Weld |  | 51448.92 | 42.17 | 0.28 | 35000 | ERW | 8.625 | 600 | [10 empty] | AGM 16 | 2257.91 | AGM 17 | 537.03 | 41.12 | 42.17 | 42.78 | 41.12 | 42.17 | 16340 | 28.29 | 41.42 | 33.8023 | -118.0109 | 54.446
GWD 16350 | Girth Weld |  | 51491.08 | 28.29 | 0.28 | 35000 | ERW | 8.625 | 600 | [10 empty] | AGM 16 | 2300.08 | AGM 17 | 494.87 | 42.17 | 28.29 | 41.12 | 42.17 | 28.29 | 16350 | 41.42 | 41.91 | 33.8024 | -118.0109 | 54.733
GWD 16360 | Girth Weld |  | 51519.38 | 41.42 | 0.28 | 35000 | ERW | 8.625 | 600 | [10 empty] | AGM 16 | 2328.37 | AGM 17 | 466.57 | 28.29 | 41.42 | 42.17 | 28.29 | 41.42 | 16360 | 41.91 | 42.26 | 33.8025 | -118.0109 | 54.598
GWD 16370 | Girth Weld |  | 51560.8 | 41.91 | 0.28 | 35000 | ERW | 8.625 | 600 | [10 empty] | AGM 16 | 2369.79 | AGM 17 | 425.16 | 41.42 | 41.91 | 28.29 | 41.42 | 41.91 | 16370 | 42.26 | 42.87 | 33.8026 | -118.0109 | 54.72
GWD 16380 | Girth Weld |  | 51602.71 | 28.77 | 0.28 | 35000 | ERW | 8.625 | 600 | [10 empty] | AGM 16 | 2411.7 | AGM 17 | 383.24 | 41.91 | 42.26 | 41.42 | 41.91 | 42.26 | 16380 | 42.87 | 0.59 | 33.8027 | -118.0109 | 54.612
CSG 11 | Casing Start |  | 51631.48 | 13.49 | 0.28 | 35000 | ERW | 8.625 | 600 |  |  | 643.178 | [7 empty] | AGM 16 | 2440.48 | AGM 17 | 354.47 | 28.77 | 13.49 | 41.42 | 41.91 | 42.26 | 16380 | 42.87 | 0.59 | 33.8028 | -118.0109 | 54.36 | Casing - Start
GWD 16390 | Girth Weld |  | 51644.97 | 40.11 | 0.28 | 35000 | ERW | 8.625 | 600 | [10 empty] | AGM 16 | 2453.97 | AGM 17 | 340.98 | 42.26 | 42.87 | 41.91 | 42.26 | 42.87 | 16390 | 0.59 | 22.69 | 33.8028 | -118.0109 | 54.407
CSG 11 | Casing End |  | 51685.08 | 2.76 | 0.28 | 35000 | ERW | 8.625 | 600 | [10 empty] | AGM 16 | 2494.07 | AGM 17 | 300.87 | 40.11 | 2.76 | 41.91 | 42.26 | 42.87 | 16390 | 0.59 | 22.69 | 33.8029 | -118.0109 | 53.744 | Casing - End
GWD 16400 | Girth Weld |  | 51687.83 | 0.17 | 0.28 | 35000 | ERW | 8.625 | 600 | [10 empty] | AGM 16 | 2496.83 | AGM 17 | 298.12 | 42.87 | 0.59 | 42.26 | 42.87 | 0.59 | 16400 | 22.69 | 0.59 | 33.8029 | -118.0109 | 53.712
BND 151 | Bend |  | 51688 | 0.42 | 0.28 | 35000 | ERW | 8.625 | 600 |  |  | 7.087 | [7 empty] | AGM 16 | 2497 | AGM 17 | 297.95 | 0.17 | 0.42 | 42.26 | 42.87 | 0.59 | 16400 | 22.69 | 0.59 | 33.8029 | -118.0109 | 53.714 | 3.0D 23.7 deg right turn sag bend
GWD 16410 | Girth Weld |  | 51688.42 | 22.69 | 0.28 | 35000 | ERW | 8.625 | 600 | [10 empty] | AGM 16 | 2497.42 | AGM 17 | 297.53 | 0.59 | 22.69 | 42.87 | 0.59 | 22.69 | 16410 | 0.59 | 2.03 | 33.803 | -118.0109 | 53.722
GWD 16420 | Girth Weld |  | 51711.11 | 0.12 | 0.28 | 35000 | ERW | 8.625 | 600 | [10 empty] | AGM 16 | 2520.11 | AGM 17 | 274.84 | 22.69 | 0.59 | 0.59 | 22.69 | 0.59 | 16420 | 2.03 | 7.84 | 33.803 | -118.0109 | 54.632
BND 152 | Bend |  | 51711.23 | 0.47 | 0.28 | 35000 | ERW | 8.625 | 600 |  |  | 7.126 | [7 empty] | AGM 16 | 2520.23 | AGM 17 | 274.72 | 0.12 | 0.47 | 0.59 | 22.69 | 0.59 | 16420 | 2.03 | 7.84 | 33.803 | -118.0109 | 54.635 | 3.0D 20.8 deg left turn over bend
GWD 16430 | Girth Weld |  | 51711.71 | 2.03 | 0.28 | 35000 | ERW | 8.625 | 600 | [10 empty] | AGM 16 | 2520.7 | AGM 17 | 274.24 | 0.59 | 2.03 | 22.69 | 0.59 | 2.03 | 16430 | 7.84 | 21.13 | 33.803 | -118.0109 | 54.642
GWD 16440 | Girth Weld |  | 51713.73 | 7.84 | 0.28 | 35000 | ERW | 8.625 | 600 | [10 empty] | AGM 16 | 2522.73 | AGM 17 | 272.22 | 2.03 | 7.84 | 0.59 | 2.03 | 7.84 | 16440 | 21.13 | 22.27 | 33.803 | -118.0109 | 54.636
GWD 16450 | Girth Weld |  | 51721.58 | 21.13 | 0.28 | 35000 | ERW | 8.625 | 600 | [10 empty] | AGM 16 | 2530.57 | AGM 17 | 264.37 | 7.84 | 21.13 | 2.03 | 7.84 | 21.13 | 16450 | 22.27 | 21.37 | 33.803 | -118.0109 | 54.648 | Reinforced
GWD 16460 | Girth Weld |  | 51742.71 | 22.27 | 0.28 | 35000 | ERW | 8.625 | 600 | [10 empty] | AGM 16 | 2551.71 | AGM 17 | 243.24 | 21.13 | 22.27 | 7.84 | 21.13 | 22.27 | 16460 | 21.37 | 21.42 | 33.8031 | -118.0108 | 54.447 | Reinforced
GWD 16470 | Girth Weld |  | 51764.98 | 21.37 | 0.28 | 35000 | ERW | 8.625 | 600 | [10 empty] | AGM 16 | 2573.98 | AGM 17 | 220.97 | 22.27 | 21.37 | 21.13 | 22.27 | 21.37 | 16470 | 21.42 | 21.82 | 33.8032 | -118.0108 | 54.274 | Reinforced
GWD 16480 | Girth Weld |  | 51786.35 | 21.42 | 0.28 | 35000 | ERW | 8.625 | 600 | [10 empty] | AGM 16 | 2595.35 | AGM 17 | 199.6 | 21.37 | 21.42 | 22.27 | 21.37 | 21.42 | 16480 | 21.82 | 21.04 | 33.8032 | -118.0108 | 54.32 | Reinforced
GWD 16490 | Girth Weld |  | 51807.77 | 21.82 | 0.28 | 35000 | ERW | 8.625 | 600 | [10 empty] | AGM 16 | 2616.77 | AGM 17 | 178.18 | 21.42 | 21.82 | 21.37 | 21.42 | 21.82 | 16490 | 21.04 | 21.18 | 33.8033 | -118.0108 | 54.374 | Reinforced
GWD 16500 | Girth Weld |  | 51829.6 | 21.04 | 0.28 | 35000 | ERW | 8.625 | 600 | [10 empty] | AGM 16 | 2638.59 | AGM 17 | 156.35 | 21.82 | 21.04 | 21.42 | 21.82 | 21.04 | 16500 | 21.18 | 21.32 | 33.8033 | -118.0108 | 54.235 | Reinforced
GWD 16510 | Girth Weld |  | 51850.64 | 21.18 | 0.28 | 35000 | ERW | 8.625 | 600 | [10 empty] | AGM 16 | 2659.63 | AGM 17 | 135.31 | 21.04 | 21.18 | 21.82 | 21.04 | 21.18 | 16510 | 21.32 | 19.66 | 33.8034 | -118.0108 | 54.235 | Reinforced
GWD 16520 | Girth Weld |  | 51871.81 | 21.32 | 0.28 | 35000 | ERW | 8.625 | 600 | [10 empty] | AGM 16 | 2680.81 | AGM 17 | 114.14 | 21.18 | 21.32 | 21.04 | 21.18 | 21.32 | 16520 | 19.66 | 21.56 | 33.8034 | -118.0108 | 54.168 | Reinforced
GWD 16530 | Girth Weld |  | 51893.14 | 19.66 | 0.28 | 35000 | ERW | 8.625 | 600 | [10 empty] | AGM 16 | 2702.13 | AGM 17 | 92.82 | 21.32 | 19.66 | 21.18 | 21.32 | 19.66 | 16530 | 21.56 | 20.73 | 33.8035 | -118.0108 | 54.096 | Reinforced
GWD 16540 | Girth Weld |  | 51912.79 | 21.56 | 0.28 | 35000 | ERW | 8.625 | 600 | [10 empty] | AGM 16 | 2721.79 | AGM 17 | 73.16 | 19.66 | 21.56 | 21.32 | 19.66 | 21.56 | 16540 | 20.73 | 19.16 | 33.8036 | -118.0108 | 53.809 | Reinforced
GWD 16550 | Girth Weld |  | 51934.35 | 20.73 | 0.28 | 35000 | ERW | 8.625 | 600 | [10 empty] | AGM 16 | 2743.35 | AGM 17 | 51.6 | 21.56 | 20.73 | 19.66 | 21.56 | 20.73 | 16550 | 19.16 | 8.33 | 33.8036 | -118.0108 | 53.495 | Reinforced
GWD 16560 | Girth Weld |  | 51955.08 | 19.16 | 0.28 | 35000 | ERW | 8.625 | 600 | [10 empty] | AGM 16 | 2764.07 | AGM 17 | 30.88 | 20.73 | 19.16 | 21.56 | 20.73 | 19.16 | 16560 | 8.33 | 4.59 | 33.8037 | -118.0108 | 53.334 | Reinforced
GWD 16570 | Girth Weld |  | 51974.24 | 8.33 | 0.28 | 35000 | ERW | 8.625 | 600 | [10 empty] | AGM 16 | 2783.23 | AGM 17 | 11.71 | 19.16 | 8.33 | 20.73 | 19.16 | 8.33 | 16570 | 4.59 | 37.54 | 33.8037 | -118.0108 | 53.133 | Reinforced
GWD 16580 | Girth Weld |  | 51982.56 | 3.39 | 0.28 | 35000 | ERW | 8.625 | 600 | [10 empty] | AGM 16 | 2791.56 | AGM 17 | 3.39 | 8.33 | 4.59 | 19.16 | 8.33 | 4.59 | 16580 | 37.54 | 37.28 | 33.8038 | -118.0108 | 53.015
MRK 15 | Marker |  | 51985.95 | 1.21 | 0.28 | 35000 | ERW | 8.625 | 600 |  |  |  |  | 11:37 | [5 empty] | AGM 16 | 2794.95 | AGM 18 | 2532.64 | 3.39 | 1.21 | 19.16 | 8.33 | 4.59 | 16580 | 37.54 | 37.28 | 33.8038 | -118.0108 | 52.966 | AGM 17 12' East of Knott St Curb - 4' U/S of Fence
GWD 16590 | Girth Weld |  | 51987.16 | 37.54 | 0.28 | 35000 | ERW | 8.625 | 600 | [10 empty] | AGM 17 | 1.21 | AGM 18 | 2531.44 | 4.59 | 37.54 | 8.33 | 4.59 | 37.54 | 16590 | 37.28 | 24.11 | 33.8038 | -118.0108 | 52.958
GWD 16600 | Girth Weld |  | 52024.7 | 37.28 | 0.28 | 35000 | ERW | 8.625 | 600 | [10 empty] | AGM 17 | 38.75 | AGM 18 | 2493.9 | 37.54 | 37.28 | 4.59 | 37.54 | 37.28 | 16600 | 24.11 | 41.25 | 33.8039 | -118.0108 | 52.869
GWD 16610 | Girth Weld |  | 52061.98 | 24.11 | 0.28 | 35000 | ERW | 8.625 | 600 | [10 empty] | AGM 17 | 76.03 | AGM 18 | 2456.62 | 37.28 | 24.11 | 37.54 | 37.28 | 24.11 | 16610 | 41.25 | 38.25 | 33.804 | -118.0108 | 53.482
GWD 16620 | Girth Weld |  | 52086.09 | 20.29 | 0.28 | 35000 | ERW | 8.625 | 600 | [10 empty] | AGM 17 | 100.14 | AGM 18 | 2432.51 | 24.11 | 41.25 | 37.28 | 24.11 | 41.25 | 16620 | 38.25 | 36.83 | 33.804 | -118.0108 | 53.81
BND 153 | Bend |  | 52106.37 | 20.96 | 0.28 | 35000 | ERW | 8.625 | 600 |  |  | 30.337 | [7 empty] | AGM 17 | 120.42 | AGM 18 | 2412.22 | 20.29 | 20.96 | 37.28 | 24.11 | 41.25 | 16620 | 38.25 | 36.83 | 33.8041 | -118.0107 | 53.851 | 30.2D 6.3 deg left turn over bend
GWD 16630 | Girth Weld |  | 52127.33 | 38.25 | 0.28 | 35000 | ERW | 8.625 | 600 | [10 empty] | AGM 17 | 141.38 | AGM 18 | 2391.26 | 41.25 | 38.25 | 24.11 | 41.25 | 38.25 | 16630 | 36.83 | 42.74 | 33.8041 | -118.0107 | 53.925
GWD 16640 | Girth Weld |  | 52165.58 | 36.83 | 0.28 | 35000 | ERW | 8.625 | 600 | [10 empty] | AGM 17 | 179.63 | AGM 18 | 2353.01 | 38.25 | 36.83 | 41.25 | 38.25 | 36.83 | 16640 | 42.74 | 38.12 | 33.8043 | -118.0107 | 52.783
GWD 16650 | Girth Weld |  | 52202.41 | 42.74 | 0.28 | 35000 | ERW | 8.625 | 600 | [10 empty] | AGM 17 | 216.46 | AGM 18 | 2316.19 | 36.83 | 42.74 | 38.25 | 36.83 | 42.74 | 16650 | 38.12 | 9.21 | 33.8044 | -118.0108 | 52.871
GWD 16660 | Girth Weld |  | 52245.14 | 38.12 | 0.28 | 35000 | ERW | 8.625 | 600 | [10 empty] | AGM 17 | 259.19 | AGM 18 | 2273.45 | 42.74 | 38.12 | 36.83 | 42.74 | 38.12 | 16660 | 9.21 | 6.14 | 33.8045 | -118.0108 | 54.136
GWD 16670 | Girth Weld |  | 52283.27 | 9.21 | 0.28 | 35000 | ERW | 8.625 | 600 | [10 empty] | AGM 17 | 297.31 | AGM 18 | 2235.33 | 38.12 | 9.21 | 42.74 | 38.12 | 9.21 | 16670 | 6.14 | 29.21 | 33.8046 | -118.0108 | 54.315
GWD 16680 | Girth Weld |  | 52292.47 | 6.14 | 0.28 | 35000 | ERW | 8.625 | 600 | [10 empty] | AGM 17 | 306.52 | AGM 18 | 2226.12 | 9.21 | 6.14 | 38.12 | 9.21 | 6.14 | 16680 | 29.21 | 30.83 | 33.8046 | -118.0108 | 54.316
GWD 16690 | Girth Weld |  | 52298.62 | 29.21 | 0.219 | 35000 | ERW | 8.625 | 600 | [10 empty] | AGM 17 | 312.67 | AGM 18 | 2219.98 | 6.14 | 29.21 | 9.21 | 6.14 | 29.21 | 16690 | 30.83 | 38.96 | 33.8046 | -118.0108 | 54.277
GWD 16700 | Girth Weld |  | 52327.83 | 30.83 | 0.219 | 35000 | ERW | 8.625 | 600 | [10 empty] | AGM 17 | 341.87 | AGM 18 | 2190.77 | 29.21 | 30.83 | 6.14 | 29.21 | 30.83 | 16700 | 38.96 | 38.15 | 33.8047 | -118.0108 | 54.14
GWD 16710 | Girth Weld |  | 52358.65 | 38.96 | 0.219 | 35000 | ERW | 8.625 | 600 | [10 empty] | AGM 17 | 372.7 | AGM 18 | 2159.94 | 30.83 | 38.96 | 29.21 | 30.83 | 38.96 | 16710 | 38.15 | 41.93 | 33.8048 | -118.0108 | 54.289
GWD 16720 | Girth Weld |  | 52397.61 | 38.15 | 0.219 | 35000 | ERW | 8.625 | 600 | [10 empty] | AGM 17 | 411.66 | AGM 18 | 2120.99 | 38.96 | 38.15 | 30.83 | 38.96 | 38.15 | 16720 | 41.93 | 40.28 | 33.8049 | -118.0108 | 54.519
GWD 16730 | Girth Weld |  | 52435.76 | 41.93 | 0.219 | 35000 | ERW | 8.625 | 600 | [10 empty] | AGM 17 | 449.81 | AGM 18 | 2082.84 | 38.15 | 41.93 | 38.96 | 38.15 | 41.93 | 16730 | 40.28 | 43.12 | 33.805 | -118.0108 | 54.75
GWD 16740 | Girth Weld |  | 52477.69 | 40.28 | 0.219 | 35000 | ERW | 8.625 | 600 | [10 empty] | AGM 17 | 491.74 | AGM 18 | 2040.9 | 41.93 | 40.28 | 38.15 | 41.93 | 40.28 | 16740 | 43.12 | 36.59 | 33.8051 | -118.0108 | 54.887
GWD 16750 | Girth Weld |  | 52517.97 | 43.12 | 0.219 | 35000 | ERW | 8.625 | 600 | [10 empty] | AGM 17 | 532.02 | AGM 18 | 2000.62 | 40.28 | 43.12 | 41.93 | 40.28 | 43.12 | 16750 | 36.59 | 31.24 | 33.8052 | -118.0108 | 55.134
GWD 16760 | Girth Weld |  | 52561.09 | 36.59 | 0.219 | 35000 | ERW | 8.625 | 600 | [10 empty] | AGM 17 | 575.14 | AGM 18 | 1957.51 | 43.12 | 36.59 | 40.28 | 43.12 | 36.59 | 16760 | 31.24 | 39.79 | 33.8053 | -118.0108 | 55.551
GWD 16770 | Girth Weld |  | 52597.68 | 31.24 | 0.219 | 35000 | ERW | 8.625 | 600 | [10 empty] | AGM 17 | 611.73 | AGM 18 | 1920.91 | 36.59 | 31.24 | 43.12 | 36.59 | 31.24 | 16770 | 39.79 | 40.31 | 33.8054 | -118.0108 | 55.819
GWD 16780 | Girth Weld |  | 52628.92 | 39.79 | 0.219 | 35000 | ERW | 8.625 | 600 | [10 empty] | AGM 17 | 642.97 | AGM 18 | 1889.68 | 31.24 | 39.79 | 36.59 | 31.24 | 39.79 | 16780 | 40.31 | 39.9 | 33.8055 | -118.0108 | 56.134
GWD 16790 | Girth Weld |  | 52668.71 | 40.31 | 0.219 | 35000 | ERW | 8.625 | 600 | [10 empty] | AGM 17 | 682.76 | AGM 18 | 1849.89 | 39.79 | 40.31 | 31.24 | 39.79 | 40.31 | 16790 | 39.9 | 33.3 | 33.8056 | -118.0108 | 56.295
GWD 16800 | Girth Weld |  | 52709.02 | 39.9 | 0.219 | 35000 | ERW | 8.625 | 600 | [10 empty] | AGM 17 | 723.07 | AGM 18 | 1809.58 | 40.31 | 39.9 | 39.79 | 40.31 | 39.9 | 16800 | 33.3 | 38.91 | 33.8057 | -118.0108 | 56.671
GWD 16810 | Girth Weld |  | 52748.92 | 33.3 | 0.219 | 35000 | ERW | 8.625 | 600 | [10 empty] | AGM 17 | 762.97 | AGM 18 | 1769.68 | 39.9 | 33.3 | 40.31 | 39.9 | 33.3 | 16810 | 38.91 | 35.27 | 33.8059 | -118.0108 | 56.96
GWD 16820 | Girth Weld |  | 52782.22 | 38.91 | 0.219 | 35000 | ERW | 8.625 | 600 | [10 empty] | AGM 17 | 796.27 | AGM 18 | 1736.38 | 33.3 | 38.91 | 39.9 | 33.3 | 38.91 | 16820 | 35.27 | 38.9 | 33.8059 | -118.0108 | 57.133
GWD 16830 | Girth Weld |  | 52821.13 | 35.27 | 0.219 | 35000 | ERW | 8.625 | 600 | [10 empty] | AGM 17 | 835.17 | AGM 18 | 1697.47 | 38.91 | 35.27 | 33.3 | 38.91 | 35.27 | 16830 | 38.9 | 2.47 | 33.8061 | -118.0108 | 57.293
GWD 16840 | Girth Weld |  | 52856.4 | 38.9 | 0.219 | 35000 | ERW | 8.625 | 600 | [10 empty] | AGM 17 | 870.45 | AGM 18 | 1662.2 | 35.27 | 38.9 | 38.91 | 35.27 | 38.9 | 16840 | 2.47 | 40.76 | 33.8062 | -118.0108 | 57.122
GWD 16850 | Girth Weld |  | 52895.29 | 2.47 | 0.28 | 35000 | ERW | 8.625 | 600 | [10 empty] | AGM 17 | 909.34 | AGM 18 | 1623.3 | 38.9 | 2.47 | 35.27 | 38.9 | 2.47 | 16850 | 40.76 | 3.11 | 33.8063 | -118.0108 | 57.131
GWD 16860 | Girth Weld |  | 52897.76 | 4.4 | 0.28 | 35000 | ERW | 8.625 | 600 | [10 empty] | AGM 17 | 911.81 | AGM 18 | 1620.84 | 2.47 | 40.76 | 38.9 | 2.47 | 40.76 | 16860 | 3.11 | 3.61 | 33.8063 | -118.0108 | 57.158
CSG 12 | Casing Start |  | 52902.16 | 34.21 | 0.28 | 35000 | ERW | 8.625 | 600 |  |  | 410.482 | [7 empty] | AGM 17 | 916.21 | AGM 18 | 1616.44 | 4.4 | 36.36 | 38.9 | 2.47 | 40.76 | 16860 | 3.11 | 3.61 | 33.8063 | -118.0108 | 57.22 | Casing - Start
CSG 12 | Casing End |  | 52936.37 | 2.16 | 0.28 | 35000 | ERW | 8.625 | 600 | [10 empty] | AGM 17 | 950.42 | AGM 18 | 1582.23 | 38.61 | 2.16 | 38.9 | 2.47 | 40.76 | 16860 | 3.11 | 3.61 | 33.8064 | -118.0108 | 57.761 | Casing - End
GWD 16870 | Girth Weld |  | 52938.52 | 1.61 | 0.28 | 35000 | ERW | 8.625 | 600 | [10 empty] | AGM 17 | 952.57 | AGM 18 | 1580.07 | 40.76 | 3.11 | 2.47 | 40.76 | 3.11 | 16870 | 3.61 | 3.24 | 33.8064 | -118.0108 | 57.795
BND 154 | Bend |  | 52940.13 | 1.5 | 0.28 | 35000 | ERW | 8.625 | 600 |  |  | 40.791 | [7 empty] | AGM 17 | 954.18 | AGM 18 | 1578.46 | 1.61 | 1.5 | 2.47 | 40.76 | 3.11 | 16870 | 3.61 | 3.24 | 33.8064 | -118.0108 | 57.196 | 3.0D 89.9 deg over bend
GWD 16880 | Girth Weld |  | 52941.63 | 3.61 | 0.28 | 35000 | ERW | 8.625 | 600 | [10 empty] | AGM 17 | 955.68 | AGM 18 | 1576.96 | 3.11 | 3.61 | 40.76 | 3.11 | 3.61 | 16880 | 3.24 | 17.89 | 33.8064 | -118.0108 | 55.868
GWD 16890 | Girth Weld |  | 52945.24 | 2.09 | 0.28 | 35000 | ERW | 8.625 | 600 | [10 empty] | AGM 17 | 959.29 | AGM 18 | 1573.36 | 3.61 | 3.24 | 3.11 | 3.61 | 3.24 | 16890 | 17.89 | 1.52 | 33.8064 | -118.0108 | 52.204
BND 155 | Bend |  | 52947.33 | 1.15 | 0.28 | 35000 | ERW | 8.625 | 600 |  |  | 42.113 | [7 empty] | AGM 17 | 961.38 | AGM 18 | 1571.27 | 2.09 | 1.15 | 3.11 | 3.61 | 3.24 | 16890 | 17.89 | 1.52 | 33.8064 | -118.0108 | 50.282 | 3.0D 90.6 deg sag bend
GWD 16900 | Girth Weld |  | 52948.48 | 17.89 | 0.28 | 35000 | ERW | 8.625 | 600 | [10 empty] | AGM 17 | 962.53 | AGM 18 | 1570.12 | 3.24 | 17.89 | 3.61 | 3.24 | 17.89 | 16900 | 1.52 | 3.2 | 33.8064 | -118.0108 | 49.735
GWD 16910 | Girth Weld |  | 52966.37 | 0.64 | 0.28 | 35000 | ERW | 8.625 | 600 | [10 empty] | AGM 17 | 980.42 | AGM 18 | 1552.22 | 17.89 | 1.52 | 3.24 | 17.89 | 1.52 | 16910 | 3.2 | 1.58 | 33.8064 | -118.0108 | 50.476
BND 156 | Bend |  | 52967.02 | 0.88 | 0.28 | 35000 | ERW | 8.625 | 600 |  |  | 24.78 | [7 empty] | AGM 17 | 981.07 | AGM 18 | 1551.58 | 0.64 | 0.88 | 3.24 | 17.89 | 1.52 | 16910 | 3.2 | 1.58 | 33.8064 | -118.0108 | 50.644 | 3.0D 45.8 deg sag bend
GWD 16920 | Girth Weld |  | 52967.9 | 3.2 | 0.28 | 35000 | ERW | 8.625 | 600 | [10 empty] | AGM 17 | 981.95 | AGM 18 | 1550.7 | 1.52 | 3.2 | 17.89 | 1.52 | 3.2 | 16920 | 1.58 | 21.36 | 33.8064 | -118.0108 | 51.133
GWD 16930 | Girth Weld |  | 52971.1 | 1.03 | 0.28 | 35000 | ERW | 8.625 | 600 | [10 empty] | AGM 17 | 985.15 | AGM 18 | 1547.5 | 3.2 | 1.58 | 1.52 | 3.2 | 1.58 | 16930 | 21.36 | 29.69 | 33.8064 | -118.0108 | 53.482
BND 157 | Bend |  | 52972.13 | 0.55 | 0.28 | 35000 | ERW | 8.625 | 600 |  |  | 25.471 | [7 empty] | AGM 17 | 986.18 | AGM 18 | 1546.47 | 1.03 | 0.55 | 1.52 | 3.2 | 1.58 | 16930 | 21.36 | 29.69 | 33.8065 | -118.0108 | 54.123 | 3.0D 47.8 deg left turn over bend
GWD 16940 | Girth Weld |  | 52972.68 | 21.36 | 0.28 | 35000 | ERW | 8.625 | 600 | [10 empty] | AGM 17 | 986.72 | AGM 18 | 1545.92 | 1.58 | 21.36 | 3.2 | 1.58 | 21.36 | 16940 | 29.69 | 43.12 | 33.8065 | -118.0108 | 54.301
GWD 16950 | Girth Weld |  | 52994.04 | 29.69 | 0.28 | 35000 | ERW | 8.625 | 600 | [10 empty] | AGM 17 | 1008.09 | AGM 18 | 1524.56 | 21.36 | 29.69 | 1.58 | 21.36 | 29.69 | 16950 | 43.12 | 39.17 | 33.8065 | -118.0108 | 54.806
GWD 16960 | Girth Weld |  | 53023.73 | 43.12 | 0.28 | 35000 | ERW | 8.625 | 600 | [10 empty] | AGM 17 | 1037.78 | AGM 18 | 1494.87 | 29.69 | 43.12 | 21.36 | 29.69 | 43.12 | 16960 | 39.17 | 39.89 | 33.8066 | -118.0108 | 54.978
GWD 16970 | Girth Weld |  | 53066.85 | 39.17 | 0.28 | 35000 | ERW | 8.625 | 600 | [10 empty] | AGM 17 | 1080.89 | AGM 18 | 1451.75 | 43.12 | 39.17 | 29.69 | 43.12 | 39.17 | 16970 | 39.89 | 41.86 | 33.8067 | -118.0108 | 55.564
GWD 16980 | Girth Weld |  | 53106.02 | 39.89 | 0.28 | 35000 | ERW | 8.625 | 600 | [10 empty] | AGM 17 | 1120.07 | AGM 18 | 1412.58 | 39.17 | 39.89 | 43.12 | 39.17 | 39.89 | 16980 | 41.86 | 40.76 | 33.8068 | -118.0108 | 55.319
GWD 16990 | Girth Weld |  | 53145.91 | 41.86 | 0.28 | 35000 | ERW | 8.625 | 600 | [10 empty] | AGM 17 | 1159.95 | AGM 18 | 1372.69 | 39.89 | 41.86 | 39.17 | 39.89 | 41.86 | 16990 | 40.76 | 39.54 | 33.8069 | -118.0108 | 54.478
GWD 17000 | Girth Weld |  | 53187.77 | 40.76 | 0.28 | 35000 | ERW | 8.625 | 600 | [10 empty] | AGM 17 | 1201.82 | AGM 18 | 1330.83 | 41.86 | 40.76 | 39.89 | 41.86 | 40.76 | 17000 | 39.54 | 41.57 | 33.807 | -118.0108 | 54.549
GWD 17010 | Girth Weld |  | 53228.53 | 39.54 | 0.28 | 35000 | ERW | 8.625 | 600 | [10 empty] | AGM 17 | 1242.58 | AGM 18 | 1290.07 | 40.76 | 39.54 | 41.86 | 40.76 | 39.54 | 17010 | 41.57 | 41.67 | 33.8072 | -118.0108 | 54.06
GWD 17020 | Girth Weld |  | 53268.07 | 41.57 | 0.28 | 35000 | ERW | 8.625 | 600 | [10 empty] | AGM 17 | 1282.12 | AGM 18 | 1250.52 | 39.54 | 41.57 | 40.76 | 39.54 | 41.57 | 17020 | 41.67 | 40 | 33.8073 | -118.0108 | 53.108
GWD 17030 | Girth Weld |  | 53309.64 | 41.67 | 0.28 | 35000 | ERW | 8.625 | 600 | [10 empty] | AGM 17 | 1323.69 | AGM 18 | 1208.95 | 41.57 | 41.67 | 39.54 | 41.57 | 41.67 | 17030 | 40 | 39.62 | 33.8074 | -118.0108 | 52.531
GWD 17040 | Girth Weld |  | 53351.31 | 40 | 0.28 | 35000 | ERW | 8.625 | 600 | [10 empty] | AGM 17 | 1365.36 | AGM 18 | 1167.29 | 41.67 | 40 | 41.57 | 41.67 | 40 | 17040 | 39.62 | 41.31 | 33.8075 | -118.0108 | 52.398
GWD 17050 | Girth Weld |  | 53391.31 | 39.62 | 0.28 | 35000 | ERW | 8.625 | 600 | [10 empty] | AGM 17 | 1405.36 | AGM 18 | 1127.29 | 40 | 39.62 | 41.67 | 40 | 39.62 | 17050 | 41.31 | 41.6 | 33.8076 | -118.0108 | 51.996
GWD 17060 | Girth Weld |  | 53430.93 | 41.31 | 0.28 | 35000 | ERW | 8.625 | 600 | [10 empty] | AGM 17 | 1444.98 | AGM 18 | 1087.67 | 39.62 | 41.31 | 40 | 39.62 | 41.31 | 17060 | 41.6 | 42.86 | 33.8077 | -118.0108 | 51.659
GWD 17070 | Girth Weld |  | 53472.24 | 41.6 | 0.28 | 35000 | ERW | 8.625 | 600 | [10 empty] | AGM 17 | 1486.29 | AGM 18 | 1046.36 | 41.31 | 41.6 | 39.62 | 41.31 | 41.6 | 17070 | 42.86 | 41.98 | 33.8078 | -118.0108 | 51.223
GWD 17080 | Girth Weld |  | 53513.84 | 42.86 | 0.28 | 35000 | ERW | 8.625 | 600 | [10 empty] | AGM 17 | 1527.88 | AGM 18 | 1004.76 | 41.6 | 42.86 | 41.31 | 41.6 | 42.86 | 17080 | 41.98 | 41.4 | 33.8079 | -118.0108 | 50.896
GWD 17090 | Girth Weld |  | 53556.7 | 41.98 | 0.28 | 35000 | ERW | 8.625 | 600 | [10 empty] | AGM 17 | 1570.75 | AGM 18 | 961.9 | 42.86 | 41.98 | 41.6 | 42.86 | 41.98 | 17090 | 41.4 | 42.67 | 33.8081 | -118.0108 | 50.441
GWD 17100 | Girth Weld |  | 53598.68 | 41.4 | 0.28 | 35000 | ERW | 8.625 | 600 | [10 empty] | AGM 17 | 1612.73 | AGM 18 | 919.92 | 41.98 | 41.4 | 42.86 | 41.98 | 41.4 | 17100 | 42.67 | 41.42 | 33.8082 | -118.0108 | 50.188
GWD 17110 | Girth Weld |  | 53640.08 | 42.67 | 0.28 | 35000 | ERW | 8.625 | 600 | [10 empty] | AGM 17 | 1654.13 | AGM 18 | 878.52 | 41.4 | 42.67 | 41.98 | 41.4 | 42.67 | 17110 | 41.42 | 42.47 | 33.8083 | -118.0108 | 49.685
GWD 17120 | Girth Weld |  | 53682.75 | 41.42 | 0.28 | 35000 | ERW | 8.625 | 600 | [10 empty] | AGM 17 | 1696.79 | AGM 18 | 835.85 | 42.67 | 41.42 | 41.4 | 42.67 | 41.42 | 17120 | 42.47 | 37.12 | 33.8084 | -118.0108 | 49.568
GWD 17130 | Girth Weld |  | 53724.17 | 42.47 | 0.28 | 35000 | ERW | 8.625 | 600 | [10 empty] | AGM 17 | 1738.21 | AGM 18 | 794.43 | 41.42 | 42.47 | 42.67 | 41.42 | 42.47 | 17130 | 37.12 | 35.42 | 33.8085 | -118.0108 | 49.203
GWD 17140 | Girth Weld |  | 53766.64 | 37.12 | 0.28 | 35000 | ERW | 8.625 | 600 | [10 empty] | AGM 17 | 1780.69 | AGM 18 | 751.96 | 42.47 | 37.12 | 41.42 | 42.47 | 37.12 | 17140 | 35.42 | 36.87 | 33.8086 | -118.0108 | 49.384
GWD 17150 | Girth Weld |  | 53803.76 | 35.42 | 0.28 | 35000 | ERW | 8.625 | 600 | [10 empty] | AGM 17 | 1817.8 | AGM 18 | 714.84 | 37.12 | 35.42 | 42.47 | 37.12 | 35.42 | 17150 | 36.87 | 41.73 | 33.8087 | -118.0108 | 49.014
GWD 17160 | Girth Weld |  | 53839.18 | 36.87 | 0.28 | 35000 | ERW | 8.625 | 600 | [10 empty] | AGM 17 | 1853.22 | AGM 18 | 679.42 | 35.42 | 36.87 | 37.12 | 35.42 | 36.87 | 17160 | 41.73 | 42.09 | 33.8088 | -118.0108 | 49.021
GWD 17170 | Girth Weld |  | 53876.04 | 41.73 | 0.28 | 35000 | ERW | 8.625 | 600 | [10 empty] | AGM 17 | 1890.09 | AGM 18 | 642.55 | 36.87 | 41.73 | 35.42 | 36.87 | 41.73 | 17170 | 42.09 | 42.94 | 33.8089 | -118.0108 | 48.728
GWD 17180 | Girth Weld |  | 53917.78 | 42.09 | 0.28 | 35000 | ERW | 8.625 | 600 | [10 empty] | AGM 17 | 1931.82 | AGM 18 | 600.82 | 41.73 | 42.09 | 36.87 | 41.73 | 42.09 | 17180 | 42.94 | 6.21 | 33.8091 | -118.0108 | 48.523
GWD 17190 | Girth Weld |  | 53959.86 | 42.94 | 0.28 | 35000 | ERW | 8.625 | 600 | [10 empty] | AGM 17 | 1973.91 | AGM 18 | 558.73 | 42.09 | 42.94 | 41.73 | 42.09 | 42.94 | 17190 | 6.21 | 1.5 | 33.8092 | -118.0108 | 48.446
GWD 17200 | Girth Weld |  | 54002.81 | 6.21 | 0.28 | 35000 | ERW | 8.625 | 600 | [10 empty] | AGM 17 | 2016.85 | AGM 18 | 515.79 | 42.94 | 6.21 | 42.09 | 42.94 | 6.21 | 17200 | 1.5 | 0.79 | 33.8093 | -118.0108 | 47.722
GWD 17210 | Girth Weld |  | 54009.02 | 0.51 | 0.28 | 35000 | ERW | 8.625 | 600 | [10 empty] | AGM 17 | 2023.07 | AGM 18 | 509.58 | 6.21 | 1.5 | 42.94 | 6.21 | 1.5 | 17210 | 0.79 | 1.61 | 33.8093 | -118.0108 | 47.424
BND 158 | Bend |  | 54009.53 | 0.99 | 0.28 | 35000 | ERW | 8.625 | 600 |  |  | 21.239 | [7 empty] | AGM 17 | 2023.58 | AGM 18 | 509.06 | 0.51 | 0.99 | 42.94 | 6.21 | 1.5 | 17210 | 0.79 | 1.61 | 33.8093 | -118.0108 | 47.511 | 3.0D 50.6 deg left turn sag bend
GWD 17220 | Girth Weld |  | 54010.52 | 0.79 | 0.28 | 35000 | ERW | 8.625 | 600 | [10 empty] | AGM 17 | 2024.57 | AGM 18 | 508.08 | 1.5 | 0.79 | 6.21 | 1.5 | 0.79 | 17220 | 1.61 | 8.19 | 33.8093 | -118.0108 | 48.026
GWD 17230 | Girth Weld |  | 54011.31 | 0.74 | 0.28 | 35000 | ERW | 8.625 | 600 | [10 empty] | AGM 17 | 2025.36 | AGM 18 | 507.29 | 0.79 | 1.61 | 1.5 | 0.79 | 1.61 | 17230 | 8.19 | 1.69 | 33.8093 | -118.0108 | 48.569
BND 159 | Bend |  | 54012.05 | 0.87 | 0.28 | 35000 | ERW | 8.625 | 600 |  |  | 21.384 | [7 empty] | AGM 17 | 2026.1 | AGM 18 | 506.55 | 0.74 | 0.87 | 1.5 | 0.79 | 1.61 | 17230 | 8.19 | 1.69 | 33.8093 | -118.0108 | 48.935 | 3.0D 45.7 deg right turn over bend
GWD 17240 | Girth Weld |  | 54012.92 | 8.19 | 0.28 | 35000 | ERW | 8.625 | 600 | [10 empty] | AGM 17 | 2026.96 | AGM 18 | 505.68 | 1.61 | 8.19 | 0.79 | 1.61 | 8.19 | 17240 | 1.69 | 0.87 | 33.8093 | -118.0108 | 49.092
GWD 17250 | Girth Weld |  | 54021.11 | 0.8 | 0.28 | 35000 | ERW | 8.625 | 600 | [10 empty] | AGM 17 | 2035.15 | AGM 18 | 497.49 | 8.19 | 1.69 | 1.61 | 8.19 | 1.69 | 17250 | 0.87 | 1.52 | 33.8093 | -118.0108 | 49.002
BND 160 | Bend |  | 54021.9 | 0.89 | 0.28 | 35000 | ERW | 8.625 | 600 |  |  | 22.141 | [7 empty] | AGM 17 | 2035.95 | AGM 18 | 496.69 | 0.8 | 0.89 | 1.61 | 8.19 | 1.69 | 17250 | 0.87 | 1.52 | 33.8093 | -118.0108 | 48.867 | 3.0D 47.2 deg right turn over bend
GWD 17260 | Girth Weld |  | 54022.79 | 0.87 | 0.28 | 35000 | ERW | 8.625 | 600 | [10 empty] | AGM 17 | 2036.84 | AGM 18 | 495.8 | 1.69 | 0.87 | 8.19 | 1.69 | 0.87 | 17260 | 1.52 | 22.11 | 33.8093 | -118.0108 | 48.397
GWD 17270 | Girth Weld |  | 54023.66 | 0.84 | 0.28 | 35000 | ERW | 8.625 | 600 | [10 empty] | AGM 17 | 2037.71 | AGM 18 | 494.93 | 0.87 | 1.52 | 1.69 | 0.87 | 1.52 | 17270 | 22.11 | 41.5 | 33.8093 | -118.0108 | 47.792
BND 161 | Bend |  | 54024.5 | 0.68 | 0.28 | 35000 | ERW | 8.625 | 600 |  |  | 22.485 | [7 empty] | AGM 17 | 2038.55 | AGM 18 | 494.09 | 0.84 | 0.68 | 1.69 | 0.87 | 1.52 | 17270 | 22.11 | 41.5 | 33.8093 | -118.0108 | 47.368 | 3.0D 45.9 deg left turn sag bend
GWD 17280 | Girth Weld |  | 54025.18 | 22.11 | 0.28 | 35000 | ERW | 8.625 | 600 | [10 empty] | AGM 17 | 2039.23 | AGM 18 | 493.41 | 1.52 | 22.11 | 0.87 | 1.52 | 22.11 | 17280 | 41.5 | 40.94 | 33.8093 | -118.0108 | 47.235
GWD 17290 | Girth Weld |  | 54047.29 | 41.5 | 0.28 | 35000 | ERW | 8.625 | 600 | [10 empty] | AGM 17 | 2061.34 | AGM 18 | 471.31 | 22.11 | 41.5 | 1.52 | 22.11 | 41.5 | 17290 | 40.94 | 41.16 | 33.8094 | -118.0108 | 47.803
GWD 17300 | Girth Weld |  | 54088.79 | 40.94 | 0.28 | 35000 | ERW | 8.625 | 600 | [10 empty] | AGM 17 | 2102.83 | AGM 18 | 429.81 | 41.5 | 40.94 | 22.11 | 41.5 | 40.94 | 17300 | 41.16 | 40.84 | 33.8095 | -118.0108 | 48.183
GWD 17310 | Girth Weld |  | 54129.72 | 41.16 | 0.28 | 35000 | ERW | 8.625 | 600 | [10 empty] | AGM 17 | 2143.77 | AGM 18 | 388.87 | 40.94 | 41.16 | 41.5 | 40.94 | 41.16 | 17310 | 40.84 | 14.12 | 33.8096 | -118.0108 | 48.851
GWD 17320 | Girth Weld |  | 54170.89 | 40.84 | 0.28 | 35000 | ERW | 8.625 | 600 | [10 empty] | AGM 17 | 2184.94 | AGM 18 | 347.71 | 41.16 | 40.84 | 40.94 | 41.16 | 40.84 | 17320 | 14.12 | 43.66 | 33.8097 | -118.0108 | 49.999
GWD 17330 | Girth Weld |  | 54211.72 | 14.12 | 0.28 | 35000 | ERW | 8.625 | 600 | [10 empty] | AGM 17 | 2225.77 | AGM 18 | 306.87 | 40.84 | 14.12 | 41.16 | 40.84 | 14.12 | 17330 | 43.66 | 43.72 | 33.8099 | -118.0108 | 50.883
GWD 17340 | Girth Weld |  | 54225.84 | 43.66 | 0.28 | 35000 | ERW | 8.625 | 600 | [10 empty] | AGM 17 | 2239.89 | AGM 18 | 292.75 | 14.12 | 43.66 | 40.84 | 14.12 | 43.66 | 17340 | 43.72 | 42.51 | 33.8099 | -118.0108 | 51.327
GWD 17350 | Girth Weld |  | 54269.5 | 43.72 | 0.28 | 35000 | ERW | 8.625 | 600 | [10 empty] | AGM 17 | 2283.55 | AGM 18 | 249.1 | 43.66 | 43.72 | 14.12 | 43.66 | 43.72 | 17350 | 42.51 | 40.25 | 33.81 | -118.0108 | 51.018
GWD 17360 | Girth Weld |  | 54313.22 | 42.51 | 0.28 | 35000 | ERW | 8.625 | 600 | [10 empty] | AGM 17 | 2327.26 | AGM 18 | 205.38 | 43.72 | 42.51 | 43.66 | 43.72 | 42.51 | 17360 | 40.25 | 43.88 | 33.8101 | -118.0108 | 51.902
GWD 17370 | Girth Weld |  | 54355.73 | 40.25 | 0.28 | 35000 | ERW | 8.625 | 600 | [10 empty] | AGM 17 | 2369.77 | AGM 18 | 162.87 | 42.51 | 40.25 | 43.72 | 42.51 | 40.25 | 17370 | 43.88 | 7.58 | 33.8103 | -118.0108 | 52.437
GWD 17380 | Girth Weld |  | 54395.97 | 43.88 | 0.28 | 35000 | ERW | 8.625 | 600 | [10 empty] | AGM 17 | 2410.02 | AGM 18 | 122.62 | 40.25 | 43.88 | 42.51 | 40.25 | 43.88 | 17380 | 7.58 | 1.57 | 33.8104 | -118.0108 | 52.645
GWD 17390 | Girth Weld |  | 54439.85 | 7.58 | 0.28 | 35000 | ERW | 8.625 | 600 | [10 empty] | AGM 17 | 2453.9 | AGM 18 | 78.75 | 43.88 | 7.58 | 40.25 | 43.88 | 7.58 | 17390 | 1.57 | 3.34 | 33.8105 | -118.0108 | 52.736
GWD 17400 | Girth Weld |  | 54447.43 | 0.7 | 0.28 | 35000 | ERW | 8.625 | 600 | [10 empty] | AGM 17 | 2461.48 | AGM 18 | 71.17 | 7.58 | 1.57 | 43.88 | 7.58 | 1.57 | 17400 | 3.34 | 1.53 | 33.8105 | -118.0108 | 52.712
BND 162 | Bend |  | 54448.13 | 0.87 | 0.28 | 35000 | ERW | 8.625 | 600 |  |  | 24.314 | [7 empty] | AGM 17 | 2462.17 | AGM 18 | 70.47 | 0.7 | 0.87 | 43.88 | 7.58 | 1.57 | 17400 | 3.34 | 1.53 | 33.8105 | -118.0108 | 52.648 | 3.0D 46.6 deg left turn over bend
GWD 17410 | Girth Weld |  | 54449 | 3.34 | 0.28 | 35000 | ERW | 8.625 | 600 | [10 empty] | AGM 17 | 2463.05 | AGM 18 | 69.6 | 1.57 | 3.34 | 7.58 | 1.57 | 3.34 | 17410 | 1.53 | 1.08 | 33.8105 | -118.0108 | 52.464
GWD 17420 | Girth Weld |  | 54452.34 | 0.61 | 0.28 | 35000 | ERW | 8.625 | 600 | [10 empty] | AGM 17 | 2466.39 | AGM 18 | 66.26 | 3.34 | 1.53 | 1.57 | 3.34 | 1.53 | 17420 | 1.08 | 46.78 | 33.8105 | -118.0108 | 51.545
BND 163 | Bend |  | 54452.95 | 0.92 | 0.28 | 35000 | ERW | 8.625 | 600 |  |  | 24.429 | [7 empty] | AGM 17 | 2467 | AGM 18 | 65.64 | 0.61 | 0.92 | 1.57 | 3.34 | 1.53 | 17420 | 1.08 | 46.78 | 33.8105 | -118.0108 | 51.419 | 3.0D 46.3 deg right turn sag bend
GWD 17430 | Girth Weld |  | 54453.87 | 1.08 | 0.28 | 35000 | ERW | 8.625 | 600 | [10 empty] | AGM 17 | 2467.92 | AGM 18 | 64.73 | 1.53 | 1.08 | 3.34 | 1.53 | 1.08 | 17430 | 46.78 | 45.89 | 33.8105 | -118.0108 | 51.348
GWD 17440 | Girth Weld |  | 54454.95 | 46.78 | 0.28 | 35000 | ERW | 8.625 | 600 | [10 empty] | AGM 17 | 2469 | AGM 18 | 63.65 | 1.08 | 46.78 | 1.53 | 1.08 | 46.78 | 17440 | 45.89 | 46.22 | 33.8105 | -118.0108 | 51.358
GWD 17450 | Girth Weld |  | 54501.73 | 16.87 | 0.28 | 35000 | ERW | 8.625 | 600 | [10 empty] | AGM 17 | 2515.78 | AGM 18 | 16.87 | 46.78 | 45.89 | 1.08 | 46.78 | 45.89 | 17450 | 46.22 | 43.26 | 33.8107 | -118.0108 | 52.156
MRK 16 | Marker |  | 54518.6 | 29.03 | 0.28 | 35000 | ERW | 8.625 | 600 |  |  |  |  | 11:38 | [5 empty] | AGM 17 | 2532.64 | Estimated Valve 109 | 28622.55 | 16.87 | 29.03 | 1.08 | 46.78 | 45.89 | 17450 | 46.22 | 43.26 | 33.8107 | -118.0108 | 52.568 | AGM 18 6' East of Curb - Located in Knott St
GWD 17460 | Girth Weld |  | 54547.62 | 46.22 | 0.28 | 35000 | ERW | 8.625 | 600 | [10 empty] | AGM 18 | 29.03 | Estimated Valve 109 | 28593.52 | 45.89 | 46.22 | 46.78 | 45.89 | 46.22 | 17460 | 43.26 | 7.86 | 33.8108 | -118.0108 | 53.067
GWD 17470 | Girth Weld |  | 54593.85 | 43.26 | 0.28 | 35000 | ERW | 8.625 | 600 | [10 empty] | AGM 18 | 75.25 | Estimated Valve 109 | 28547.29 | 46.22 | 43.26 | 45.89 | 46.22 | 43.26 | 17470 | 7.86 | 29.33 | 33.8109 | -118.0108 | 53.429
GWD 17480 | Girth Weld |  | 54637.1 | 7.86 | 0.28 | 35000 | ERW | 8.625 | 600 | [10 empty] | AGM 18 | 118.51 | Estimated Valve 109 | 28504.04 | 43.26 | 7.86 | 46.22 | 43.26 | 7.86 | 17480 | 29.33 | 46.67 | 33.8111 | -118.0108 | 53.604
GWD 17490 | Girth Weld |  | 54644.97 | 29.33 | 0.28 | 35000 | ERW | 8.625 | 600 | [10 empty] | AGM 18 | 126.37 | Estimated Valve 109 | 28496.17 | 7.86 | 29.33 | 43.26 | 7.86 | 29.33 | 17490 | 46.67 | 23.87 | 33.8111 | -118.0108 | 53.672
GWD 17500 | Girth Weld |  | 54674.3 | 46.67 | 0.28 | 35000 | ERW | 8.625 | 600 | [10 empty] | AGM 18 | 155.7 | Estimated Valve 109 | 28466.84 | 29.33 | 46.67 | 7.86 | 29.33 | 46.67 | 17500 | 23.87 | 41.57 | 33.8112 | -118.0108 | 53.955
GWD 17510 | Girth Weld |  | 54720.97 | 23.87 | 0.28 | 35000 | ERW | 8.625 | 600 | [10 empty] | AGM 18 | 202.38 | Estimated Valve 109 | 28420.17 | 46.67 | 23.87 | 29.33 | 46.67 | 23.87 | 17510 | 41.57 | 41.95 | 33.8113 | -118.0108 | 53.495
GWD 17520 | Girth Weld |  | 54744.85 | 41.57 | 0.28 | 35000 | ERW | 8.625 | 600 | [10 empty] | AGM 18 | 226.25 | Estimated Valve 109 | 28396.29 | 23.87 | 41.57 | 46.67 | 23.87 | 41.57 | 17520 | 41.95 | 46.58 | 33.8114 | -118.0108 | 52.642
GWD 17530 | Girth Weld |  | 54786.42 | 41.95 | 0.28 | 35000 | ERW | 8.625 | 600 | [10 empty] | AGM 18 | 267.82 | Estimated Valve 109 | 28354.72 | 41.57 | 41.95 | 23.87 | 41.57 | 41.95 | 17530 | 46.58 | 42.48 | 33.8115 | -118.0108 | 52.21
GWD 17540 | Girth Weld |  | 54828.37 | 46.58 | 0.28 | 35000 | ERW | 8.625 | 600 | [10 empty] | AGM 18 | 309.77 | Estimated Valve 109 | 28312.78 | 41.95 | 46.58 | 41.57 | 41.95 | 46.58 | 17540 | 42.48 | 7.82 | 33.8116 | -118.0108 | 53.04
GWD 17550 | Girth Weld |  | 54874.94 | 42.48 | 0.28 | 35000 | ERW | 8.625 | 600 | [10 empty] | AGM 18 | 356.35 | Estimated Valve 109 | 28266.2 | 46.58 | 42.48 | 41.95 | 46.58 | 42.48 | 17550 | 7.82 | 48.52 | 33.8118 | -118.0108 | 53.166
GWD 17560 | Girth Weld |  | 54917.42 | 7.82 | 0.28 | 35000 | ERW | 8.625 | 600 | [10 empty] | AGM 18 | 398.83 | Estimated Valve 109 | 28223.72 | 42.48 | 7.82 | 46.58 | 42.48 | 7.82 | 17560 | 48.52 | 49.62 | 33.8119 | -118.0108 | 52.913
GWD 17570 | Girth Weld |  | 54925.24 | 48.52 | 0.28 | 35000 | ERW | 8.625 | 600 | [10 empty] | AGM 18 | 406.64 | Estimated Valve 109 | 28215.9 | 7.82 | 48.52 | 42.48 | 7.82 | 48.52 | 17570 | 49.62 | 48.51 | 33.8119 | -118.0108 | 53.158
GWD 17580 | Girth Weld |  | 54973.75 | 49.62 | 0.28 | 35000 | ERW | 8.625 | 600 | [10 empty] | AGM 18 | 455.16 | Estimated Valve 109 | 28167.39 | 48.52 | 49.62 | 7.82 | 48.52 | 49.62 | 17580 | 48.51 | 43.83 | 33.8121 | -118.0108 | 54.074
GWD 17590 | Girth Weld |  | 55023.37 | 48.51 | 0.28 | 35000 | ERW | 8.625 | 600 | [10 empty] | AGM 18 | 504.78 | Estimated Valve 109 | 28117.77 | 49.62 | 48.51 | 48.52 | 49.62 | 48.51 | 17590 | 43.83 | 45.02 | 33.8122 | -118.0108 | 53.979
GWD 17600 | Girth Weld |  | 55071.88 | 43.83 | 0.28 | 35000 | ERW | 8.625 | 600 | [10 empty] | AGM 18 | 553.29 | Estimated Valve 109 | 28069.26 | 48.51 | 43.83 | 49.62 | 48.51 | 43.83 | 17600 | 45.02 | 37.02 | 33.8124 | -118.0108 | 53.807
GWD 17610 | Girth Weld |  | 55115.72 | 45.02 | 0.28 | 35000 | ERW | 8.625 | 600 | [10 empty] | AGM 18 | 597.12 | Estimated Valve 109 | 28025.43 | 43.83 | 45.02 | 48.51 | 43.83 | 45.02 | 17610 | 37.02 | 34.17 | 33.8125 | -118.0108 | 54.251
GWD 17620 | Girth Weld |  | 55160.73 | 37.02 | 0.28 | 35000 | ERW | 8.625 | 600 | [10 empty] | AGM 18 | 642.14 | Estimated Valve 109 | 27980.41 | 45.02 | 37.02 | 43.83 | 45.02 | 37.02 | 17620 | 34.17 | 34.28 | 33.8127 | -118.0108 | 54.525
GWD 17630 | Girth Weld |  | 55197.76 | 34.17 | 0.28 | 35000 | ERW | 8.625 | 600 | [10 empty] | AGM 18 | 679.16 | Estimated Valve 109 | 27943.39 | 37.02 | 34.17 | 45.02 | 37.02 | 34.17 | 17630 | 34.28 | 28.47 | 33.8128 | -118.0108 | 54.263
GWD 17640 | Girth Weld |  | 55231.93 | 34.28 | 0.28 | 35000 | ERW | 8.625 | 600 | [10 empty] | AGM 18 | 713.33 | Estimated Valve 109 | 27909.22 | 34.17 | 34.28 | 37.02 | 34.17 | 34.28 | 17640 | 28.47 | 37.55 | 33.8129 | -118.0108 | 54.152
GWD 17650 | Girth Weld |  | 55266.21 | 28.47 | 0.28 | 35000 | ERW | 8.625 | 600 | [10 empty] | AGM 18 | 747.61 | Estimated Valve 109 | 27874.93 | 34.28 | 28.47 | 34.17 | 34.28 | 28.47 | 17650 | 37.55 | 35.16 | 33.813 | -118.0108 | 54.157
GWD 17660 | Girth Weld |  | 55294.68 | 37.55 | 0.28 | 35000 | ERW | 8.625 | 600 | [10 empty] | AGM 18 | 776.09 | Estimated Valve 109 | 27846.46 | 28.47 | 37.55 | 34.28 | 28.47 | 37.55 | 17660 | 35.16 | 40.06 | 33.8131 | -118.0108 | 54.236
GWD 17670 | Girth Weld |  | 55332.23 | 35.16 | 0.28 | 35000 | ERW | 8.625 | 600 | [10 empty] | AGM 18 | 813.64 | Estimated Valve 109 | 27808.91 | 37.55 | 35.16 | 28.47 | 37.55 | 35.16 | 17670 | 40.06 | 34.85 | 33.8132 | -118.0108 | 54.048
GWD 17680 | Girth Weld |  | 55367.39 | 40.06 | 0.28 | 35000 | ERW | 8.625 | 600 | [10 empty] | AGM 18 | 848.8 | Estimated Valve 109 | 27773.75 | 35.16 | 40.06 | 37.55 | 35.16 | 40.06 | 17680 | 34.85 | 32.11 | 33.8133 | -118.0108 | 54.173
GWD 17690 | Girth Weld |  | 55407.45 | 34.85 | 0.28 | 35000 | ERW | 8.625 | 600 | [10 empty] | AGM 18 | 888.85 | Estimated Valve 109 | 27733.69 | 40.06 | 34.85 | 35.16 | 40.06 | 34.85 | 17690 | 32.11 | 36.52 | 33.8134 | -118.0108 | 53.687
GWD 17700 | Girth Weld |  | 55442.29 | 32.11 | 0.28 | 35000 | ERW | 8.625 | 600 | [10 empty] | AGM 18 | 923.7 | Estimated Valve 109 | 27698.85 | 34.85 | 32.11 | 40.06 | 34.85 | 32.11 | 17700 | 36.52 | 33.22 | 33.8135 | -118.0108 | 54.216
GWD 17710 | Girth Weld |  | 55474.4 | 36.52 | 0.28 | 35000 | ERW | 8.625 | 600 | [10 empty] | AGM 18 | 955.8 | Estimated Valve 109 | 27666.74 | 32.11 | 36.52 | 34.85 | 32.11 | 36.52 | 17710 | 33.22 | 37.59 | 33.8136 | -118.0108 | 54.194
GWD 17720 | Girth Weld |  | 55510.92 | 33.22 | 0.28 | 35000 | ERW | 8.625 | 600 | [10 empty] | AGM 18 | 992.32 | Estimated Valve 109 | 27630.22 | 36.52 | 33.22 | 32.11 | 36.52 | 33.22 | 17720 | 37.59 | 42.9 | 33.8137 | -118.0108 | 53.878
GWD 17730 | Girth Weld |  | 55544.14 | 37.59 | 0.28 | 35000 | ERW | 8.625 | 600 | [10 empty] | AGM 18 | 1025.54 | Estimated Valve 109 | 27597 | 33.22 | 37.59 | 36.52 | 33.22 | 37.59 | 17730 | 42.9 | 38.6 | 33.8138 | -118.0108 | 54.299
GWD 17740 | Girth Weld |  | 55581.72 | 42.9 | 0.28 | 35000 | ERW | 8.625 | 600 | [10 empty] | AGM 18 | 1063.13 | Estimated Valve 109 | 27559.42 | 37.59 | 42.9 | 33.22 | 37.59 | 42.9 | 17740 | 38.6 | 38.35 | 33.8139 | -118.0108 | 54.644
GWD 17750 | Girth Weld |  | 55624.63 | 38.6 | 0.28 | 35000 | ERW | 8.625 | 600 | [10 empty] | AGM 18 | 1106.03 | Estimated Valve 109 | 27516.52 | 42.9 | 38.6 | 37.59 | 42.9 | 38.6 | 17750 | 38.35 | 37.13 | 33.8141 | -118.0108 | 55
GWD 17760 | Girth Weld |  | 55663.23 | 38.35 | 0.28 | 35000 | ERW | 8.625 | 600 | [10 empty] | AGM 18 | 1144.63 | Estimated Valve 109 | 27477.91 | 38.6 | 38.35 | 42.9 | 38.6 | 38.35 | 17760 | 37.13 | 40.89 | 33.8142 | -118.0108 | 55.394
GWD 17770 | Girth Weld |  | 55701.58 | 37.13 | 0.28 | 35000 | ERW | 8.625 | 600 | [10 empty] | AGM 18 | 1182.99 | Estimated Valve 109 | 27439.56 | 38.35 | 37.13 | 38.6 | 38.35 | 37.13 | 17770 | 40.89 | 35.96 | 33.8143 | -118.0108 | 55.339
GWD 17780 | Girth Weld |  | 55738.71 | 40.89 | 0.28 | 35000 | ERW | 8.625 | 600 | [10 empty] | AGM 18 | 1220.11 | Estimated Valve 109 | 27402.43 | 37.13 | 40.89 | 38.35 | 37.13 | 40.89 | 17780 | 35.96 | 31.27 | 33.8144 | -118.0108 | 55.52
GWD 17790 | Girth Weld |  | 55779.6 | 35.96 | 0.28 | 35000 | ERW | 8.625 | 600 | [10 empty] | AGM 18 | 1261 | Estimated Valve 109 | 27361.54 | 40.89 | 35.96 | 37.13 | 40.89 | 35.96 | 17790 | 31.27 | 37.13 | 33.8145 | -118.0109 | 55.891
GWD 17800 | Girth Weld |  | 55815.55 | 31.27 | 0.28 | 35000 | ERW | 8.625 | 600 | [10 empty] | AGM 18 | 1296.96 | Estimated Valve 109 | 27325.59 | 35.96 | 31.27 | 40.89 | 35.96 | 31.27 | 17800 | 37.13 | 37.4 | 33.8147 | -118.0109 | 56.12
GWD 17810 | Girth Weld |  | 55846.83 | 37.13 | 0.28 | 35000 | ERW | 8.625 | 600 | [10 empty] | AGM 18 | 1328.23 | Estimated Valve 109 | 27294.31 | 31.27 | 37.13 | 35.96 | 31.27 | 37.13 | 17810 | 37.4 | 6347.96 | 33.8148 | -118.0109 | 56.057
GWD 17820 | Girth Weld |  | 55883.96 | 37.4 | 0.28 | 35000 | ERW | 8.625 | 600 | [10 empty] | AGM 18 | 1365.36 | Estimated Valve 109 | 27257.18 | 37.13 | 37.4 | 31.27 | 37.13 | 37.4 | 17820 | 6347.96 | 27.66 | 33.8149 | -118.0109 | 56.543
GWD 17830 | Girth Weld |  | 55921.36 | 6347.96 | 0.28 | 35000 | ERW | 8.625 | 600 | [10 empty] | AGM 18 | 1402.76 | Estimated Valve 109 | 27219.79 | 37.4 | 6347.96 | 37.13 | 37.4 | 6347.96 | 17830 | 27.66 | 33.65 | 33.815 | -118.0109 | 56.861 | Start Bad Data
GWD 17840 | Girth Weld |  | 62269.32 | 27.66 | 0.219 | 35000 | ERW | 8.625 | 600 | [10 empty] | AGM 18 | 7750.72 | Estimated Valve 109 | 20871.82 | 6347.96 | 27.66 | 37.4 | 6347.96 | 27.66 | 17840 | 33.65 | 18.37 | 33.8327 | -118.011 | 58.629 | End Bad Data
GWD 17850 | Girth Weld |  | 62296.98 | 33.65 | 0.219 | 35000 | ERW | 8.625 | 600 | [10 empty] | AGM 18 | 7778.39 | Estimated Valve 109 | 20844.16 | 27.66 | 33.65 | 6347.96 | 27.66 | 33.65 | 17850 | 18.37 | 42.17 | 33.8328 | -118.011 | 59.356
GWD 17860 | Girth Weld |  | 62330.63 | 18.37 | 0.219 | 35000 | ERW | 8.625 | 600 | [10 empty] | AGM 18 | 7812.03 | Estimated Valve 109 | 20810.51 | 33.65 | 18.37 | 27.66 | 33.65 | 18.37 | 17860 | 42.17 | 28.83 | 33.8329 | -118.011 | 59.878
GWD 17870 | Girth Weld |  | 62349 | 42.17 | 0.219 | 35000 | ERW | 8.625 | 600 | [10 empty] | AGM 18 | 7830.4 | Estimated Valve 109 | 20792.14 | 18.37 | 42.17 | 33.65 | 18.37 | 42.17 | 17870 | 28.83 | 35.39 | 33.8329 | -118.011 | 60.354
GWD 17880 | Girth Weld |  | 62391.17 | 28.83 | 0.219 | 35000 | ERW | 8.625 | 600 | [10 empty] | AGM 18 | 7872.58 | Estimated Valve 109 | 20749.97 | 42.17 | 28.83 | 18.37 | 42.17 | 28.83 | 17880 | 35.39 | 20.78 | 33.8331 | -118.011 | 61.669
GWD 17890 | Girth Weld |  | 62420 | 35.39 | 0.219 | 35000 | ERW | 8.625 | 600 | [10 empty] | AGM 18 | 7901.4 | Estimated Valve 109 | 20721.14 | 28.83 | 35.39 | 42.17 | 28.83 | 35.39 | 17890 | 20.78 | 43.4 | 33.8331 | -118.011 | 62.339
GWD 17900 | Girth Weld |  | 62455.38 | 20.78 | 0.219 | 35000 | ERW | 8.625 | 600 | [10 empty] | AGM 18 | 7936.79 | Estimated Valve 109 | 20685.76 | 35.39 | 20.78 | 28.83 | 35.39 | 20.78 | 17900 | 43.4 | 44.34 | 33.8332 | -118.011 | 62.765
GWD 17910 | Girth Weld |  | 62476.16 | 43.4 | 0.219 | 35000 | ERW | 8.625 | 600 | [10 empty] | AGM 18 | 7957.57 | Estimated Valve 109 | 20664.98 | 20.78 | 43.4 | 35.39 | 20.78 | 43.4 | 17910 | 44.34 | 44.67 | 33.8333 | -118.011 | 63.093
GWD 17920 | Girth Weld |  | 62519.56 | 44.34 | 0.219 | 35000 | ERW | 8.625 | 600 | [10 empty] | AGM 18 | 8000.97 | Estimated Valve 109 | 20621.58 | 43.4 | 44.34 | 20.78 | 43.4 | 44.34 | 17920 | 44.67 | 46.3 | 33.8334 | -118.011 | 64.087
GWD 17930 | Girth Weld |  | 62563.9 | 44.67 | 0.219 | 35000 | ERW | 8.625 | 600 | [10 empty] | AGM 18 | 8045.31 | Estimated Valve 109 | 20577.24 | 44.34 | 44.67 | 43.4 | 44.34 | 44.67 | 17930 | 46.3 | 47.2 | 33.8335 | -118.011 | 64.308
GWD 17940 | Girth Weld |  | 62608.58 | 46.3 | 0.219 | 35000 | ERW | 8.625 | 600 | [10 empty] | AGM 18 | 8089.98 | Estimated Valve 109 | 20532.56 | 44.67 | 46.3 | 44.34 | 44.67 | 46.3 | 17940 | 47.2 | 47.2 | 33.8337 | -118.011 | 65.629
GWD 17950 | Girth Weld |  | 62654.87 | 47.2 | 0.219 | 35000 | ERW | 8.625 | 600 | [10 empty] | AGM 18 | 8136.28 | Estimated Valve 109 | 20486.27 | 46.3 | 47.2 | 44.67 | 46.3 | 47.2 | 17950 | 47.2 | 47.68 | 33.8338 | -118.011 | 66.544
GWD 17960 | Girth Weld |  | 62702.07 | 47.2 | 0.219 | 35000 | ERW | 8.625 | 600 | [10 empty] | AGM 18 | 8183.48 | Estimated Valve 109 | 20439.07 | 47.2 | 47.2 | 46.3 | 47.2 | 47.2 | 17960 | 47.68 | 47.8 | 33.8339 | -118.011 | 67.757
GWD 17970 | Girth Weld |  | 62749.27 | 47.68 | 0.219 | 35000 | ERW | 8.625 | 600 | [10 empty] | AGM 18 | 8230.67 | Estimated Valve 109 | 20391.87 | 47.2 | 47.68 | 47.2 | 47.2 | 47.68 | 17970 | 47.8 | 47.81 | 33.8341 | -118.011 | 68.978
GWD 17980 | Girth Weld |  | 62796.95 | 47.8 | 0.219 | 35000 | ERW | 8.625 | 600 | [10 empty] | AGM 18 | 8278.35 | Estimated Valve 109 | 20344.19 | 47.68 | 47.8 | 47.2 | 47.68 | 47.8 | 17980 | 47.81 | 20.48 | 33.8342 | -118.011 | 69.814
GWD 17990 | Girth Weld |  | 62844.74 | 47.81 | 0.219 | 35000 | ERW | 8.625 | 600 | [10 empty] | AGM 18 | 8326.15 | Estimated Valve 109 | 20296.4 | 47.8 | 47.81 | 47.68 | 47.8 | 47.81 | 17990 | 20.48 | 40.97 | 33.8343 | -118.011 | 71.046
GWD 18000 | Girth Weld |  | 62892.55 | 20.48 | 0.219 | 35000 | ERW | 8.625 | 600 | [10 empty] | AGM 18 | 8373.95 | Estimated Valve 109 | 20248.59 | 47.81 | 20.48 | 47.8 | 47.81 | 20.48 | 18000 | 40.97 | 43.56 | 33.8344 | -118.011 | 71.596
GWD 18010 | Girth Weld |  | 62913.03 | 40.97 | 0.28 | 35000 | ERW | 8.625 | 600 | [10 empty] | AGM 18 | 8394.43 | Estimated Valve 109 | 20228.11 | 20.48 | 40.97 | 47.81 | 20.48 | 40.97 | 18010 | 43.56 | 42.81 | 33.8345 | -118.011 | 72.053
GWD 18020 | Girth Weld |  | 62954 | 43.56 | 0.28 | 35000 | ERW | 8.625 | 600 | [10 empty] | AGM 18 | 8435.41 | Estimated Valve 109 | 20187.14 | 40.97 | 43.56 | 20.48 | 40.97 | 43.56 | 18020 | 42.81 | 20.44 | 33.8346 | -118.011 | 72.6
GWD 18030 | Girth Weld |  | 62997.56 | 42.81 | 0.28 | 35000 | ERW | 8.625 | 600 | [10 empty] | AGM 18 | 8478.96 | Estimated Valve 109 | 20143.58 | 43.56 | 42.81 | 40.97 | 43.56 | 42.81 | 18030 | 20.44 | 44.59 | 33.8347 | -118.011 | 73.098
GWD 18040 | Girth Weld |  | 63040.37 | 20.44 | 0.28 | 35000 | ERW | 8.625 | 600 | [10 empty] | AGM 18 | 8521.77 | Estimated Valve 109 | 20100.77 | 42.81 | 20.44 | 43.56 | 42.81 | 20.44 | 18040 | 44.59 | 25.21 | 33.8349 | -118.011 | 73.505
GWD 18050 | Girth Weld |  | 63060.81 | 44.59 | 0.28 | 35000 | ERW | 8.625 | 600 | [10 empty] | AGM 18 | 8542.22 | Estimated Valve 109 | 20080.33 | 20.44 | 44.59 | 42.81 | 20.44 | 44.59 | 18050 | 25.21 | 48.45 | 33.8349 | -118.011 | 74.066
GWD 18060 | Girth Weld |  | 63105.41 | 25.21 | 0.28 | 35000 | ERW | 8.625 | 600 | [10 empty] | AGM 18 | 8586.81 | Estimated Valve 109 | 20035.73 | 44.59 | 25.21 | 20.44 | 44.59 | 25.21 | 18060 | 48.45 | 47.93 | 33.835 | -118.0111 | 74.813
GWD 18070 | Girth Weld |  | 63130.62 | 48.45 | 0.28 | 35000 | ERW | 8.625 | 600 | [10 empty] | AGM 18 | 8612.02 | Estimated Valve 109 | 20010.52 | 25.21 | 48.45 | 44.59 | 25.21 | 48.45 | 18070 | 47.93 | 1.08 | 33.8351 | -118.0111 | 75.132
GWD 18080 | Girth Weld |  | 63179.07 | 47.93 | 0.28 | 35000 | ERW | 8.625 | 600 | [10 empty] | AGM 18 | 8660.47 | Estimated Valve 109 | 19962.08 | 48.45 | 47.93 | 25.21 | 48.45 | 47.93 | 18080 | 1.08 | 0.8 | 33.8352 | -118.0111 | 75.642
GWD 18090 | Girth Weld |  | 63226.99 | 1.08 | 0.28 | 35000 | ERW | 8.625 | 600 | [10 empty] | AGM 18 | 8708.4 | Estimated Valve 109 | 19914.15 | 47.93 | 1.08 | 48.45 | 47.93 | 1.08 | 18090 | 0.8 | 6.97 | 33.8354 | -118.0111 | 75.667
GWD 18100 | Girth Weld |  | 63228.07 | 0.8 | 0.28 | 35000 | ERW | 8.625 | 600 | [10 empty] | AGM 18 | 8709.47 | Estimated Valve 109 | 19913.07 | 1.08 | 0.8 | 47.93 | 1.08 | 0.8 | 18100 | 6.97 | 19.61 | 33.8354 | -118.0111 | 75.89
GWD 18110 | Girth Weld |  | 63228.87 | 6.97 | 0.28 | 35000 | ERW | 8.625 | 600 | [10 empty] | AGM 18 | 8710.27 | Estimated Valve 109 | 19912.27 | 0.8 | 6.97 | 1.08 | 0.8 | 6.97 | 18110 | 19.61 | 21.76 | 33.8354 | -118.0111 | 75.902
GWD 18120 | Girth Weld |  | 63235.83 | 19.61 | 0.28 | 35000 | ERW | 8.625 | 600 | [10 empty] | AGM 18 | 8717.24 | Estimated Valve 109 | 19905.31 | 6.97 | 19.61 | 0.8 | 6.97 | 19.61 | 18120 | 21.76 | 19.72 | 33.8354 | -118.0111 | 76.003 | Reinforced
GWD 18130 | Girth Weld |  | 63255.45 | 21.76 | 0.28 | 35000 | ERW | 8.625 | 600 | [10 empty] | AGM 18 | 8736.85 | Estimated Valve 109 | 19885.7 | 19.61 | 21.76 | 6.97 | 19.61 | 21.76 | 18130 | 19.72 | 21.25 | 33.8355 | -118.0111 | 76.149 | Reinforced
GWD 18140 | Girth Weld |  | 63277.2 | 19.72 | 0.28 | 35000 | ERW | 8.625 | 600 | [10 empty] | AGM 18 | 8758.61 | Estimated Valve 109 | 19863.94 | 21.76 | 19.72 | 19.61 | 21.76 | 19.72 | 18140 | 21.25 | 22.32 | 33.8355 | -118.0111 | 75.782 | Reinforced
GWD 18150 | Girth Weld |  | 63296.92 | 21.25 | 0.28 | 35000 | ERW | 8.625 | 600 | [10 empty] | AGM 18 | 8778.33 | Estimated Valve 109 | 19844.22 | 19.72 | 21.25 | 21.76 | 19.72 | 21.25 | 18150 | 22.32 | 21.38 | 33.8356 | -118.0111 | 75.111 | Reinforced
GWD 18160 | Girth Weld |  | 63318.18 | 22.32 | 0.28 | 35000 | ERW | 8.625 | 600 | [10 empty] | AGM 18 | 8799.58 | Estimated Valve 109 | 19822.97 | 21.25 | 22.32 | 19.72 | 21.25 | 22.32 | 18160 | 21.38 | 19.96 | 33.8356 | -118.0111 | 74.262 | Reinforced
GWD 18170 | Girth Weld |  | 63340.5 | 21.38 | 0.28 | 35000 | ERW | 8.625 | 600 | [10 empty] | AGM 18 | 8821.9 | Estimated Valve 109 | 19800.64 | 22.32 | 21.38 | 21.25 | 22.32 | 21.38 | 18170 | 19.96 | 15.41 | 33.8357 | -118.0111 | 73.605 | Reinforced
GWD 18180 | Girth Weld |  | 63361.88 | 19.96 | 0.28 | 35000 | ERW | 8.625 | 600 | [10 empty] | AGM 18 | 8843.29 | Estimated Valve 109 | 19779.26 | 21.38 | 19.96 | 22.32 | 21.38 | 19.96 | 18180 | 15.41 | 20.88 | 33.8357 | -118.0111 | 73.288 | Reinforced
GWD 18190 | Girth Weld |  | 63381.84 | 15.41 | 0.28 | 35000 | ERW | 8.625 | 600 | [10 empty] | AGM 18 | 8863.24 | Estimated Valve 109 | 19759.3 | 19.96 | 15.41 | 21.38 | 19.96 | 15.41 | 18190 | 20.88 | 19.75 | 33.8358 | -118.0111 | 73.256 | Reinforced
GWD 18200 | Girth Weld |  | 63397.25 | 20.88 | 0.28 | 35000 | ERW | 8.625 | 600 | [10 empty] | AGM 18 | 8878.66 | Estimated Valve 109 | 19743.89 | 15.41 | 20.88 | 19.96 | 15.41 | 20.88 | 18200 | 19.75 | 20.12 | 33.8358 | -118.0111 | 72.977 | Reinforced
GWD 18210 | Girth Weld |  | 63418.14 | 19.75 | 0.28 | 35000 | ERW | 8.625 | 600 | [10 empty] | AGM 18 | 8899.54 | Estimated Valve 109 | 19723 | 20.88 | 19.75 | 15.41 | 20.88 | 19.75 | 18210 | 20.12 | 19.91 | 33.8359 | -118.0111 | 72.675 | Reinforced
GWD 18220 | Girth Weld |  | 63437.89 | 20.12 | 0.28 | 35000 | ERW | 8.625 | 600 | [10 empty] | AGM 18 | 8919.29 | Estimated Valve 109 | 19703.25 | 19.75 | 20.12 | 20.88 | 19.75 | 20.12 | 18220 | 19.91 | 21.58 | 33.836 | -118.0111 | 72.503 | Reinforced
GWD 18230 | Girth Weld |  | 63458 | 19.91 | 0.28 | 35000 | ERW | 8.625 | 600 | [10 empty] | AGM 18 | 8939.41 | Estimated Valve 109 | 19683.14 | 20.12 | 19.91 | 19.75 | 20.12 | 19.91 | 18230 | 21.58 | 20.41 | 33.836 | -118.0111 | 72.279 | Reinforced
GWD 18240 | Girth Weld |  | 63477.91 | 21.58 | 0.28 | 35000 | ERW | 8.625 | 600 | [10 empty] | AGM 18 | 8959.32 | Estimated Valve 109 | 19663.23 | 19.91 | 21.58 | 20.12 | 19.91 | 21.58 | 18240 | 20.41 | 21.44 | 33.8361 | -118.0111 | 71.943 | Reinforced
GWD 18250 | Girth Weld |  | 63499.49 | 20.41 | 0.28 | 35000 | ERW | 8.625 | 600 | [10 empty] | AGM 18 | 8980.9 | Estimated Valve 109 | 19641.65 | 21.58 | 20.41 | 19.91 | 21.58 | 20.41 | 18250 | 21.44 | 21.35 | 33.8361 | -118.0111 | 71.36 | Reinforced
GWD 18260 | Girth Weld |  | 63519.9 | 21.44 | 0.28 | 35000 | ERW | 8.625 | 600 | [10 empty] | AGM 18 | 9001.3 | Estimated Valve 109 | 19621.24 | 20.41 | 21.44 | 21.58 | 20.41 | 21.44 | 18260 | 21.35 | 20.86 | 33.8362 | -118.0111 | 70.812 | Reinforced
GWD 18270 | Girth Weld |  | 63541.34 | 21.35 | 0.28 | 35000 | ERW | 8.625 | 600 | [10 empty] | AGM 18 | 9022.75 | Estimated Valve 109 | 19599.8 | 21.44 | 21.35 | 20.41 | 21.44 | 21.35 | 18270 | 20.86 | 21.49 | 33.8362 | -118.0111 | 70.477 | Reinforced
GWD 18280 | Girth Weld |  | 63562.69 | 20.86 | 0.28 | 35000 | ERW | 8.625 | 600 | [10 empty] | AGM 18 | 9044.09 | Estimated Valve 109 | 19578.45 | 21.35 | 20.86 | 21.44 | 21.35 | 20.86 | 18280 | 21.49 | 21.61 | 33.8363 | -118.0111 | 70.271 | Reinforced
GWD 18290 | Girth Weld |  | 63583.55 | 21.49 | 0.28 | 35000 | ERW | 8.625 | 600 | [10 empty] | AGM 18 | 9064.96 | Estimated Valve 109 | 19557.59 | 20.86 | 21.49 | 21.35 | 20.86 | 21.49 | 18290 | 21.61 | 20.8 | 33.8364 | -118.0111 | 69.984 | Reinforced
GWD 18300 | Girth Weld |  | 63605.04 | 21.61 | 0.28 | 35000 | ERW | 8.625 | 600 | [10 empty] | AGM 18 | 9086.45 | Estimated Valve 109 | 19536.1 | 21.49 | 21.61 | 20.86 | 21.49 | 21.61 | 18300 | 20.8 | 19.66 | 33.8364 | -118.0111 | 69.569 | Reinforced
GWD 18310 | Girth Weld |  | 63626.66 | 20.8 | 0.28 | 35000 | ERW | 8.625 | 600 | [10 empty] | AGM 18 | 9108.06 | Estimated Valve 109 | 19514.48 | 21.61 | 20.8 | 21.49 | 21.61 | 20.8 | 18310 | 19.66 | 21.16 | 33.8365 | -118.0111 | 69.168 | Reinforced
GWD 18320 | Girth Weld |  | 63647.46 | 19.66 | 0.28 | 35000 | ERW | 8.625 | 600 | [10 empty] | AGM 18 | 9128.87 | Estimated Valve 109 | 19493.68 | 20.8 | 19.66 | 21.61 | 20.8 | 19.66 | 18320 | 21.16 | 21.39 | 33.8365 | -118.0111 | 68.843 | Reinforced
GWD 18330 | Girth Weld |  | 63667.12 | 21.16 | 0.28 | 35000 | ERW | 8.625 | 600 | [10 empty] | AGM 18 | 9148.52 | Estimated Valve 109 | 19474.02 | 19.66 | 21.16 | 20.8 | 19.66 | 21.16 | 18330 | 21.39 | 22.13 | 33.8366 | -118.0111 | 68.662 | Reinforced
GWD 18340 | Girth Weld |  | 63688.28 | 21.39 | 0.28 | 35000 | ERW | 8.625 | 600 | [10 empty] | AGM 18 | 9169.69 | Estimated Valve 109 | 19452.86 | 21.16 | 21.39 | 19.66 | 21.16 | 21.39 | 18340 | 22.13 | 20.85 | 33.8367 | -118.0111 | 68.488 | Reinforced
GWD 18350 | Girth Weld |  | 63709.67 | 22.13 | 0.28 | 35000 | ERW | 8.625 | 600 | [10 empty] | AGM 18 | 9191.07 | Estimated Valve 109 | 19431.47 | 21.39 | 22.13 | 21.16 | 21.39 | 22.13 | 18350 | 20.85 | 19.8 | 33.8367 | -118.0111 | 68.297 | Reinforced
GWD 18360 | Girth Weld |  | 63731.79 | 20.85 | 0.28 | 35000 | ERW | 8.625 | 600 | [10 empty] | AGM 18 | 9213.2 | Estimated Valve 109 | 19409.35 | 22.13 | 20.85 | 21.39 | 22.13 | 20.85 | 18360 | 19.8 | 20.46 | 33.8368 | -118.0111 | 67.904 | Reinforced
GWD 18370 | Girth Weld |  | 63752.64 | 19.8 | 0.28 | 35000 | ERW | 8.625 | 600 | [10 empty] | AGM 18 | 9234.05 | Estimated Valve 109 | 19388.5 | 20.85 | 19.8 | 22.13 | 20.85 | 19.8 | 18370 | 20.46 | 22.09 | 33.8368 | -118.0111 | 67.763 | Reinforced
GWD 18380 | Girth Weld |  | 63772.44 | 20.46 | 0.28 | 35000 | ERW | 8.625 | 600 | [10 empty] | AGM 18 | 9253.85 | Estimated Valve 109 | 19368.7 | 19.8 | 20.46 | 20.85 | 19.8 | 20.46 | 18380 | 22.09 | 21.19 | 33.8369 | -118.0111 | 67.678 | Reinforced
GWD 18390 | Girth Weld |  | 63792.91 | 22.09 | 0.28 | 35000 | ERW | 8.625 | 600 | [10 empty] | AGM 18 | 9274.31 | Estimated Valve 109 | 19348.24 | 20.46 | 22.09 | 19.8 | 20.46 | 22.09 | 18390 | 21.19 | 20.66 | 33.8369 | -118.0111 | 67.299 | Reinforced
GWD 18400 | Girth Weld |  | 63815 | 21.19 | 0.28 | 35000 | ERW | 8.625 | 600 | [10 empty] | AGM 18 | 9296.4 | Estimated Valve 109 | 19326.14 | 22.09 | 21.19 | 20.46 | 22.09 | 21.19 | 18400 | 20.66 | 20 | 33.837 | -118.0111 | 66.944 | Reinforced
GWD 18410 | Girth Weld |  | 63836.18 | 20.66 | 0.28 | 35000 | ERW | 8.625 | 600 | [10 empty] | AGM 18 | 9317.59 | Estimated Valve 109 | 19304.96 | 21.19 | 20.66 | 22.09 | 21.19 | 20.66 | 18410 | 20 | 20 | 33.8371 | -118.0111 | 66.655 | Reinforced
GWD 18420 | Girth Weld |  | 63856.85 | 20 | 0.28 | 35000 | ERW | 8.625 | 600 | [10 empty] | AGM 18 | 9338.25 | Estimated Valve 109 | 19284.29 | 20.66 | 20 | 21.19 | 20.66 | 20 | 18420 | 20 | 46.54 | 33.8371 | -118.0111 | 66.227 | Reinforced
GWD 18430 | Girth Weld |  | 63876.85 | 20 | 0.28 | 35000 | ERW | 8.625 | 600 | [10 empty] | AGM 18 | 9358.25 | Estimated Valve 109 | 19264.29 | 20 | 20 | 20.66 | 20 | 20 | 18430 | 46.54 | 46.39 | 33.8372 | -118.0111 | 65.625 | Reinforced
GWD 18440 | Girth Weld |  | 63896.85 | 46.54 | 0.28 | 35000 | ERW | 8.625 | 600 | [10 empty] | AGM 18 | 9378.25 | Estimated Valve 109 | 19244.29 | 20 | 46.54 | 20 | 20 | 46.54 | 18440 | 46.39 | 46.64 | 33.8372 | -118.0111 | 64.808
GWD 18450 | Girth Weld |  | 63943.39 | 46.39 | 0.28 | 35000 | ERW | 8.625 | 600 | [10 empty] | AGM 18 | 9424.79 | Estimated Valve 109 | 19197.75 | 46.54 | 46.39 | 20 | 46.54 | 46.39 | 18450 | 46.64 | 47.49 | 33.8374 | -118.0111 | 64.54
GWD 18460 | Girth Weld |  | 63989.78 | 46.64 | 0.28 | 35000 | ERW | 8.625 | 600 | [10 empty] | AGM 18 | 9471.18 | Estimated Valve 109 | 19151.36 | 46.39 | 46.64 | 46.54 | 46.39 | 46.64 | 18460 | 47.49 | 26.74 | 33.8375 | -118.0111 | 63.792
GWD 18470 | Girth Weld |  | 64036.42 | 47.49 | 0.28 | 35000 | ERW | 8.625 | 600 | [10 empty] | AGM 18 | 9517.82 | Estimated Valve 109 | 19104.72 | 46.64 | 47.49 | 46.39 | 46.64 | 47.49 | 18470 | 26.74 | 46.48 | 33.8376 | -118.0111 | 63.474
GWD 18480 | Girth Weld |  | 64083.91 | 26.74 | 0.28 | 35000 | ERW | 8.625 | 600 | [10 empty] | AGM 18 | 9565.31 | Estimated Valve 109 | 19057.23 | 47.49 | 26.74 | 46.64 | 47.49 | 26.74 | 18480 | 46.48 | 37.85 | 33.8378 | -118.0111 | 63.659
GWD 18490 | Girth Weld |  | 64110.65 | 46.48 | 0.28 | 35000 | ERW | 8.625 | 600 | [10 empty] | AGM 18 | 9592.05 | Estimated Valve 109 | 19030.49 | 26.74 | 46.48 | 47.49 | 26.74 | 46.48 | 18490 | 37.85 | 40.32 | 33.8378 | -118.0111 | 63.12
GWD 18500 | Girth Weld |  | 64157.13 | 37.85 | 0.28 | 35000 | ERW | 8.625 | 600 | [10 empty] | AGM 18 | 9638.53 | Estimated Valve 109 | 18984.02 | 46.48 | 37.85 | 26.74 | 46.48 | 37.85 | 18500 | 40.32 | 37.19 | 33.838 | -118.0111 | 62.698
GWD 18510 | Girth Weld |  | 64194.98 | 40.32 | 0.28 | 35000 | ERW | 8.625 | 600 | [10 empty] | AGM 18 | 9676.38 | Estimated Valve 109 | 18946.16 | 37.85 | 40.32 | 46.48 | 37.85 | 40.32 | 18510 | 37.19 | 45.39 | 33.8381 | -118.0111 | 62.77
GWD 18520 | Girth Weld |  | 64235.3 | 37.19 | 0.28 | 35000 | ERW | 8.625 | 600 | [10 empty] | AGM 18 | 9716.7 | Estimated Valve 109 | 18905.85 | 40.32 | 37.19 | 37.85 | 40.32 | 37.19 | 18520 | 45.39 | 41.01 | 33.8382 | -118.0111 | 62.344
GWD 18530 | Girth Weld |  | 64272.49 | 45.39 | 0.28 | 35000 | ERW | 8.625 | 600 | [10 empty] | AGM 18 | 9753.89 | Estimated Valve 109 | 18868.65 | 37.19 | 45.39 | 40.32 | 37.19 | 45.39 | 18530 | 41.01 | 47.61 | 33.8383 | -118.0111 | 62.795
GWD 18540 | Girth Weld |  | 64317.88 | 41.01 | 0.28 | 35000 | ERW | 8.625 | 600 | [10 empty] | AGM 18 | 9799.29 | Estimated Valve 109 | 18823.26 | 45.39 | 41.01 | 37.19 | 45.39 | 41.01 | 18540 | 47.61 | 48.62 | 33.8384 | -118.0111 | 63.192
GWD 18550 | Girth Weld |  | 64358.89 | 47.61 | 0.28 | 35000 | ERW | 8.625 | 600 | [10 empty] | AGM 18 | 9840.3 | Estimated Valve 109 | 18782.25 | 41.01 | 47.61 | 45.39 | 41.01 | 47.61 | 18550 | 48.62 | 47.72 | 33.8385 | -118.0111 | 62.894
GWD 18560 | Girth Weld |  | 64406.5 | 48.62 | 0.28 | 35000 | ERW | 8.625 | 600 | [10 empty] | AGM 18 | 9887.9 | Estimated Valve 109 | 18734.65 | 47.61 | 48.62 | 41.01 | 47.61 | 48.62 | 18560 | 47.72 | 42.41 | 33.8386 | -118.0111 | 62.874
GWD 18570 | Girth Weld |  | 64455.11 | 47.72 | 0.28 | 35000 | ERW | 8.625 | 600 | [10 empty] | AGM 18 | 9936.52 | Estimated Valve 109 | 18686.03 | 48.62 | 47.72 | 47.61 | 48.62 | 47.72 | 18570 | 42.41 | 1.5 | 33.8388 | -118.0111 | 62.734
GWD 18580 | Girth Weld |  | 64502.83 | 42.41 | 0.28 | 35000 | ERW | 8.625 | 600 | [10 empty] | AGM 18 | 9984.24 | Estimated Valve 109 | 18638.31 | 47.72 | 42.41 | 48.62 | 47.72 | 42.41 | 18580 | 1.5 | 0.66 | 33.8389 | -118.0111 | 62.363
GWD 18590 | Girth Weld |  | 64545.25 | 1.5 | 0.28 | 35000 | ERW | 8.625 | 600 | [10 empty] | AGM 18 | 10026.65 | Estimated Valve 109 | 18595.9 | 42.41 | 1.5 | 47.72 | 42.41 | 1.5 | 18590 | 0.66 | 1.79 | 33.839 | -118.0111 | 62.096
GWD 18600 | Girth Weld |  | 64546.74 | 0.66 | 0.28 | 35000 | ERW | 8.625 | 600 | [10 empty] | AGM 18 | 10028.15 | Estimated Valve 109 | 18594.4 | 1.5 | 0.66 | 42.41 | 1.5 | 0.66 | 18600 | 1.79 | 38.64 | 33.839 | -118.0111 | 62.853
GWD 18610 | Girth Weld |  | 64547.41 | 1.79 | 0.28 | 35000 | ERW | 8.625 | 600 | [10 empty] | AGM 18 | 10028.81 | Estimated Valve 109 | 18593.73 | 0.66 | 1.79 | 1.5 | 0.66 | 1.79 | 18610 | 38.64 | 39.42 | 33.839 | -118.0111 | 63.334
GWD 18620 | Girth Weld |  | 64549.19 | 4.73 | 0.28 | 35000 | ERW | 8.625 | 600 | [10 empty] | AGM 18 | 10030.6 | Estimated Valve 109 | 18591.95 | 1.79 | 38.64 | 0.66 | 1.79 | 38.64 | 18620 | 39.42 | 3.09 | 33.839 | -118.0111 | 63.887
CSG 13 | Casing Start |  | 64553.93 | 23.11 | 0.28 | 35000 | ERW | 8.625 | 600 |  |  | 277.272 | [7 empty] | AGM 18 | 10035.33 | Estimated Valve 109 | 18587.21 | 4.73 | 33.91 | 0.66 | 1.79 | 38.64 | 18620 | 39.42 | 3.09 | 33.8391 | -118.0111 | 63.868 | Casing - Start
CSG 13 | Casing End |  | 64577.03 | 10.8 | 0.28 | 35000 | ERW | 8.625 | 600 | [10 empty] | AGM 18 | 10058.44 | Estimated Valve 109 | 18564.11 | 27.84 | 10.8 | 0.66 | 1.79 | 38.64 | 18620 | 39.42 | 3.09 | 33.8391 | -118.0111 | 63.616 | Casing - End
GWD 18630 | Girth Weld |  | 64587.84 | 39.42 | 0.28 | 35000 | ERW | 8.625 | 600 | [10 empty] | AGM 18 | 10069.24 | Estimated Valve 109 | 18553.3 | 38.64 | 39.42 | 1.79 | 38.64 | 39.42 | 18630 | 3.09 | 37.65 | 33.8391 | -118.0111 | 63.473
GWD 18640 | Girth Weld |  | 64627.26 | 3.09 | 0.28 | 35000 | ERW | 8.625 | 600 | [10 empty] | AGM 18 | 10108.66 | Estimated Valve 109 | 18513.88 | 39.42 | 3.09 | 38.64 | 39.42 | 3.09 | 18640 | 37.65 | 38.21 | 33.8393 | -118.0111 | 63.245
GWD 18650 | Girth Weld |  | 64630.34 | 37.65 | 0.28 | 35000 | ERW | 8.625 | 600 | [10 empty] | AGM 18 | 10111.75 | Estimated Valve 109 | 18510.8 | 3.09 | 37.65 | 39.42 | 3.09 | 37.65 | 18650 | 38.21 | 38.68 | 33.8393 | -118.0111 | 63.228
GWD 18660 | Girth Weld |  | 64668 | 38.21 | 0.28 | 35000 | ERW | 8.625 | 600 | [10 empty] | AGM 18 | 10149.4 | Estimated Valve 109 | 18473.14 | 37.65 | 38.21 | 3.09 | 37.65 | 38.21 | 18660 | 38.68 | 14398.17 | 33.8394 | -118.0111 | 63.185
GWD 18670 | Girth Weld |  | 64706.2 | 38.68 | 0.28 | 35000 | ERW | 8.625 | 600 | [10 empty] | AGM 18 | 10187.61 | Estimated Valve 109 | 18434.94 | 38.21 | 38.68 | 37.65 | 38.21 | 38.68 | 18670 | 14398.17 | 18.69 | 33.8395 | -118.0111 | 63.118
GWD 18680 | Girth Weld |  | 64744.89 | 14398.17 | 0.28 | 35000 | ERW | 8.625 | 600 | [10 empty] | AGM 18 | 10226.29 | Estimated Valve 109 | 18396.26 | 38.68 | 14398.17 | 38.21 | 38.68 | 14398.17 | 18680 | 18.69 | 20.32 | 33.8396 | -118.0111 | 62.971 | Start Bad Data
GWD 18690 | Girth Weld |  | 79143.05 | 18.69 | 0.28 | 35000 | ERW | 8.625 | 600 | [10 empty] | AGM 18 | 24624.46 | Estimated Valve 109 | 3998.09 | 14398.17 | 18.69 | 38.68 | 14398.17 | 18.69 | 18690 | 20.32 | 20.72 | 33.8772 | -118.0156 | 57.085 | End Bad Data
GWD 18700 | Girth Weld |  | 79161.74 | 20.32 | 0.28 | 35000 | ERW | 8.625 | 600 | [10 empty] | AGM 18 | 24643.15 | Estimated Valve 109 | 3979.4 | 18.69 | 20.32 | 14398.17 | 18.69 | 20.32 | 18700 | 20.72 | 20.85 | 33.8773 | -118.0156 | 56.744
GWD 18710 | Girth Weld |  | 79182.06 | 20.72 | 0.28 | 35000 | ERW | 8.625 | 600 | [10 empty] | AGM 18 | 24663.46 | Estimated Valve 109 | 3959.08 | 20.32 | 20.72 | 18.69 | 20.32 | 20.72 | 18710 | 20.85 | 20.77 | 33.8773 | -118.0155 | 56.383
GWD 18720 | Girth Weld |  | 79202.78 | 20.85 | 0.28 | 35000 | ERW | 8.625 | 600 | [10 empty] | AGM 18 | 24684.18 | Estimated Valve 109 | 3938.37 | 20.72 | 20.85 | 20.32 | 20.72 | 20.85 | 18720 | 20.77 | 20.73 | 33.8774 | -118.0155 | 56.031
GWD 18730 | Girth Weld |  | 79223.63 | 20.77 | 0.28 | 35000 | ERW | 8.625 | 600 | [10 empty] | AGM 18 | 24705.03 | Estimated Valve 109 | 3917.52 | 20.85 | 20.77 | 20.72 | 20.85 | 20.77 | 18730 | 20.73 | 20.99 | 33.8774 | -118.0155 | 55.646
GWD 18740 | Girth Weld |  | 79244.4 | 20.73 | 0.28 | 35000 | ERW | 8.625 | 600 | [10 empty] | AGM 18 | 24725.8 | Estimated Valve 109 | 3896.74 | 20.77 | 20.73 | 20.85 | 20.77 | 20.73 | 18740 | 20.99 | 20.92 | 33.8775 | -118.0154 | 55.346
GWD 18750 | Girth Weld |  | 79265.13 | 20.99 | 0.28 | 35000 | ERW | 8.625 | 600 | [10 empty] | AGM 18 | 24746.53 | Estimated Valve 109 | 3876.01 | 20.73 | 20.99 | 20.77 | 20.73 | 20.99 | 18750 | 20.92 | 20.91 | 33.8775 | -118.0154 | 55.054
GWD 18760 | Girth Weld |  | 79286.12 | 20.92 | 0.28 | 35000 | ERW | 8.625 | 600 | [10 empty] | AGM 18 | 24767.52 | Estimated Valve 109 | 3855.03 | 20.99 | 20.92 | 20.73 | 20.99 | 20.92 | 18760 | 20.91 | 3.01 | 33.8776 | -118.0154 | 54.741
GWD 18770 | Girth Weld |  | 79307.03 | 20.91 | 0.28 | 35000 | ERW | 8.625 | 600 | [10 empty] | AGM 18 | 24788.44 | Estimated Valve 109 | 3834.11 | 20.92 | 20.91 | 20.99 | 20.92 | 20.91 | 18770 | 3.01 | 7.29 | 33.8776 | -118.0153 | 54.454
GWD 18780 | Girth Weld |  | 79327.95 | 3.01 | 0.28 | 35000 | ERW | 8.625 | 600 | [10 empty] | AGM 18 | 24809.35 | Estimated Valve 109 | 3813.19 | 20.91 | 3.01 | 20.92 | 20.91 | 3.01 | 18780 | 7.29 | 1.23 | 33.8777 | -118.0153 | 54.077
GWD 18790 | Girth Weld |  | 79330.96 | 7.29 | 0.25 | 35000 | ERW | 8.625 | 600 | [10 empty] | AGM 18 | 24812.36 | Estimated Valve 109 | 3810.18 | 3.01 | 7.29 | 20.91 | 3.01 | 7.29 | 18790 | 1.23 | 5.67 | 33.8777 | -118.0153 | 53.998 | Estimated WT 0.250
GWD 18800 | Girth Weld |  | 79338.24 | 1.23 | 0.28 | 35000 | ERW | 8.625 | 600 | [10 empty] | AGM 18 | 24819.65 | Estimated Valve 109 | 3802.9 | 7.29 | 1.23 | 3.01 | 7.29 | 1.23 | 18800 | 5.67 | 29.05 | 33.8777 | -118.0153 | 58.695
GWD 18810 | Girth Weld |  | 79339.47 | 5.67 | 0.25 | 35000 | ERW | 8.625 | 600 | [10 empty] | AGM 18 | 24820.88 | Estimated Valve 109 | 3801.67 | 1.23 | 5.67 | 7.29 | 1.23 | 5.67 | 18810 | 29.05 | 29.9 | 33.8777 | -118.0153 | 59.89 | Estimated WT 0.250
GWD 18820 | Girth Weld |  | 79345.14 | 29.05 | 0.25 | 35000 | ERW | 8.625 | 600 | [10 empty] | AGM 18 | 24826.54 | Estimated Valve 109 | 3796 | 5.67 | 29.05 | 1.23 | 5.67 | 29.05 | 18820 | 29.9 | 42.21 | 33.8777 | -118.0153 | 61.982
GWD 18830 | Girth Weld |  | 79374.19 | 29.9 | 0.25 | 35000 | ERW | 8.625 | 600 | [10 empty] | AGM 18 | 24855.59 | Estimated Valve 109 | 3766.95 | 29.05 | 29.9 | 5.67 | 29.05 | 29.9 | 18830 | 42.21 | 3.74 | 33.8777 | -118.0154 | 62.034
GWD 18840 | Girth Weld |  | 79404.09 | 42.21 | 0.25 | 35000 | ERW | 8.625 | 600 | [10 empty] | AGM 18 | 24885.5 | Estimated Valve 109 | 3737.05 | 29.9 | 42.21 | 29.05 | 29.9 | 42.21 | 18840 | 3.74 | 6.88 | 33.8778 | -118.0154 | 62.42
GWD 18850 | Girth Weld |  | 79446.3 | 3.74 | 0.25 | 35000 | ERW | 8.625 | 600 | [10 empty] | AGM 18 | 24927.7 | Estimated Valve 109 | 3694.84 | 42.21 | 3.74 | 29.9 | 42.21 | 3.74 | 18850 | 6.88 | 5.02 | 33.8778 | -118.0156 | 63.779
GWD 18860 | Girth Weld |  | 79450.04 | 6.88 | 0.25 | 35000 | ERW | 8.625 | 600 | [10 empty] | AGM 18 | 24931.44 | Estimated Valve 109 | 3691.1 | 3.74 | 6.88 | 42.21 | 3.74 | 6.88 | 18860 | 5.02 | 19.18 | 33.8779 | -118.0156 | 64.536
GWD 18870 | Girth Weld |  | 79456.92 | 5.02 | 0.25 | 35000 | ERW | 8.625 | 600 | [10 empty] | AGM 18 | 24938.32 | Estimated Valve 109 | 3684.23 | 6.88 | 5.02 | 3.74 | 6.88 | 5.02 | 18870 | 19.18 | 38.46 | 33.8779 | -118.0156 | 69.302
GWD 18880 | Girth Weld |  | 79461.94 | 19.18 | 0.28 | 35000 | ERW | 8.625 | 600 | [10 empty] | AGM 18 | 24943.34 | Estimated Valve 109 | 3679.2 | 5.02 | 19.18 | 6.88 | 5.02 | 19.18 | 18880 | 38.46 | 20.92 | 33.8779 | -118.0156 | 71.516
GWD 18890 | Girth Weld |  | 79481.12 | 38.46 | 0.28 | 35000 | ERW | 8.625 | 600 | [10 empty] | AGM 18 | 24962.52 | Estimated Valve 109 | 3660.02 | 19.18 | 38.46 | 5.02 | 19.18 | 38.46 | 18890 | 20.92 | 20.77 | 33.8779 | -118.0156 | 71.183
GWD 18900 | Girth Weld |  | 79519.58 | 20.92 | 0.28 | 35000 | ERW | 8.625 | 600 | [10 empty] | AGM 18 | 25000.99 | Estimated Valve 109 | 3621.56 | 38.46 | 20.92 | 19.18 | 38.46 | 20.92 | 18900 | 20.77 | 4.74 | 33.878 | -118.0156 | 70.562
GWD 18910 | Girth Weld |  | 79540.5 | 20.77 | 0.28 | 35000 | ERW | 8.625 | 600 | [10 empty] | AGM 18 | 25021.9 | Estimated Valve 109 | 3600.64 | 20.92 | 20.77 | 38.46 | 20.92 | 20.77 | 18910 | 4.74 | 8.16 | 33.8781 | -118.0156 | 70.356
GWD 18920 | Girth Weld |  | 79561.27 | 4.74 | 0.25 | 35000 | ERW | 8.625 | 600 | [10 empty] | AGM 18 | 25042.67 | Estimated Valve 109 | 3579.87 | 20.77 | 4.74 | 20.92 | 20.77 | 4.74 | 18920 | 8.16 | 5.79 | 33.8781 | -118.0157 | 70.209 | Estimated WT 0.250
GWD 18930 | Girth Weld |  | 79566.01 | 8.16 | 0.25 | 35000 | ERW | 8.625 | 600 | [10 empty] | AGM 18 | 25047.41 | Estimated Valve 109 | 3575.13 | 4.74 | 8.16 | 20.77 | 4.74 | 8.16 | 18930 | 5.79 | 42.1 | 33.8782 | -118.0157 | 68.014
GWD 18940 | Girth Weld |  | 79574.17 | 5.79 | 0.25 | 35000 | ERW | 8.625 | 600 | [10 empty] | AGM 18 | 25055.57 | Estimated Valve 109 | 3566.97 | 8.16 | 5.79 | 4.74 | 8.16 | 5.79 | 18940 | 42.1 | 26.36 | 33.8781 | -118.0157 | 61.956
GWD 18950 | Girth Weld |  | 79579.96 | 42.1 | 0.25 | 35000 | ERW | 8.625 | 600 | [10 empty] | AGM 18 | 25061.36 | Estimated Valve 109 | 3561.18 | 5.79 | 42.1 | 8.16 | 5.79 | 42.1 | 18950 | 26.36 | 4.01 | 33.8781 | -118.0157 | 59.69
GWD 18960 | Girth Weld |  | 79622.06 | 26.36 | 0.25 | 35000 | ERW | 8.625 | 600 | [10 empty] | AGM 18 | 25103.47 | Estimated Valve 109 | 3519.08 | 42.1 | 26.36 | 5.79 | 42.1 | 26.36 | 18960 | 4.01 | 5.34 | 33.8781 | -118.0158 | 58.068
GWD 18970 | Girth Weld |  | 79648.43 | 4.01 | 0.25 | 35000 | ERW | 8.625 | 600 | [10 empty] | AGM 18 | 25129.83 | Estimated Valve 109 | 3492.72 | 26.36 | 4.01 | 42.1 | 26.36 | 4.01 | 18970 | 5.34 | 2.88 | 33.8781 | -118.0159 | 57.363
GWD 18980 | Girth Weld |  | 79652.43 | 5.34 | 0.25 | 35000 | ERW | 8.625 | 600 | [10 empty] | AGM 18 | 25133.84 | Estimated Valve 109 | 3488.71 | 4.01 | 5.34 | 26.36 | 4.01 | 5.34 | 18980 | 2.88 | 14.8 | 33.8781 | -118.0159 | 57.25
GWD 18990 | Girth Weld |  | 79657.77 | 2.88 | 0.25 | 35000 | ERW | 8.625 | 600 | [10 empty] | AGM 18 | 25139.18 | Estimated Valve 109 | 3483.37 | 5.34 | 2.88 | 4.01 | 5.34 | 2.88 | 18990 | 14.8 | 4.96 | 33.8781 | -118.0159 | 57.224
GWD 19000 | Girth Weld |  | 79660.66 | 14.8 | 0.25 | 35000 | ERW | 8.625 | 600 | [10 empty] | AGM 18 | 25142.06 | Estimated Valve 109 | 3480.48 | 2.88 | 14.8 | 5.34 | 2.88 | 14.8 | 19000 | 4.96 | 20.99 | 33.8781 | -118.0159 | 57.257
GWD 19010 | Girth Weld |  | 79675.46 | 4.96 | 0.25 | 35000 | ERW | 8.625 | 600 | [10 empty] | AGM 18 | 25156.86 | Estimated Valve 109 | 3465.68 | 14.8 | 4.96 | 2.88 | 14.8 | 4.96 | 19010 | 20.99 | 22.22 | 33.8782 | -118.0159 | 57.241
GWD 19020 | Girth Weld |  | 79680.42 | 20.99 | 0.25 | 35000 | ERW | 8.625 | 600 | [10 empty] | AGM 18 | 25161.82 | Estimated Valve 109 | 3460.73 | 4.96 | 20.99 | 14.8 | 4.96 | 20.99 | 19020 | 22.22 | 7.09 | 33.8782 | -118.0159 | 57.125 | Reinforced
GWD 19030 | Girth Weld |  | 79701.4 | 22.22 | 0.25 | 35000 | ERW | 8.625 | 600 | [10 empty] | AGM 18 | 25182.81 | Estimated Valve 109 | 3439.74 | 20.99 | 22.22 | 4.96 | 20.99 | 22.22 | 19030 | 7.09 | 12.71 | 33.8783 | -118.0159 | 56.774 | Reinforced
GWD 19040 | Girth Weld |  | 79723.62 | 7.09 | 0.25 | 35000 | ERW | 8.625 | 600 | [10 empty] | AGM 18 | 25205.03 | Estimated Valve 109 | 3417.52 | 22.22 | 7.09 | 20.99 | 22.22 | 7.09 | 19040 | 12.71 | 21.16 | 33.8783 | -118.0159 | 56.244 | Reinforced
GWD 19050 | Girth Weld |  | 79730.71 | 12.71 | 0.25 | 35000 | ERW | 8.625 | 600 | [10 empty] | AGM 18 | 25212.12 | Estimated Valve 109 | 3410.43 | 7.09 | 12.71 | 22.22 | 7.09 | 12.71 | 19050 | 21.16 | 15.81 | 33.8783 | -118.0159 | 56.077
GWD 19060 | Girth Weld |  | 79743.42 | 21.16 | 0.25 | 35000 | ERW | 8.625 | 600 | [10 empty] | AGM 18 | 25224.83 | Estimated Valve 109 | 3397.72 | 12.71 | 21.16 | 7.09 | 12.71 | 21.16 | 19060 | 15.81 | 41.12 | 33.8784 | -118.0159 | 55.801 | Reinforced
GWD 19070 | Girth Weld |  | 79764.58 | 15.81 | 0.25 | 35000 | ERW | 8.625 | 600 | [10 empty] | AGM 18 | 25245.98 | Estimated Valve 109 | 3376.56 | 21.16 | 15.81 | 12.71 | 21.16 | 15.81 | 19070 | 41.12 | 39.83 | 33.8784 | -118.0159 | 55.433 | Reinforced
GWD 19080 | Girth Weld |  | 79780.39 | 41.12 | 0.25 | 35000 | ERW | 8.625 | 600 | [10 empty] | AGM 18 | 25261.8 | Estimated Valve 109 | 3360.75 | 15.81 | 41.12 | 21.16 | 15.81 | 41.12 | 19080 | 39.83 | 42.92 | 33.8785 | -118.0159 | 55.109
GWD 19090 | Girth Weld |  | 79821.51 | 39.83 | 0.25 | 35000 | ERW | 8.625 | 600 | [10 empty] | AGM 18 | 25302.91 | Estimated Valve 109 | 3319.63 | 41.12 | 39.83 | 15.81 | 41.12 | 39.83 | 19090 | 42.92 | 19.02 | 33.8786 | -118.0159 | 54.269
GWD 19100 | Girth Weld |  | 79861.34 | 42.92 | 0.25 | 35000 | ERW | 8.625 | 600 | [10 empty] | AGM 18 | 25342.75 | Estimated Valve 109 | 3279.8 | 39.83 | 42.92 | 41.12 | 39.83 | 42.92 | 19100 | 19.02 | 18.18 | 33.8787 | -118.0159 | 53.907
GWD 19110 | Girth Weld |  | 79904.26 | 19.02 | 0.25 | 35000 | ERW | 8.625 | 600 | [10 empty] | AGM 18 | 25385.66 | Estimated Valve 109 | 3236.88 | 42.92 | 19.02 | 39.83 | 42.92 | 19.02 | 19110 | 18.18 | 11.12 | 33.8788 | -118.0159 | 53.475
GWD 19120 | Girth Weld |  | 79923.28 | 18.18 | 0.25 | 35000 | ERW | 8.625 | 600 | [10 empty] | AGM 18 | 25404.68 | Estimated Valve 109 | 3217.86 | 19.02 | 18.18 | 42.92 | 19.02 | 18.18 | 19120 | 11.12 | 17.87 | 33.8789 | -118.0159 | 53.398
GWD 19130 | Girth Weld |  | 79941.45 | 11.12 | 0.25 | 35000 | ERW | 8.625 | 600 | [10 empty] | AGM 18 | 25422.86 | Estimated Valve 109 | 3199.69 | 18.18 | 11.12 | 19.02 | 18.18 | 11.12 | 19130 | 17.87 | 21.55 | 33.8789 | -118.0159 | 53.285
GWD 19140 | Girth Weld |  | 79952.57 | 17.87 | 0.25 | 35000 | ERW | 8.625 | 600 | [10 empty] | AGM 18 | 25433.97 | Estimated Valve 109 | 3188.57 | 11.12 | 17.87 | 18.18 | 11.12 | 17.87 | 19140 | 21.55 | 19.8 | 33.879 | -118.0159 | 53.088
GWD 19150 | Girth Weld |  | 79970.44 | 21.55 | 0.25 | 35000 | ERW | 8.625 | 600 | [10 empty] | AGM 18 | 25451.84 | Estimated Valve 109 | 3170.71 | 17.87 | 21.55 | 11.12 | 17.87 | 21.55 | 19150 | 19.8 | 21.86 | 33.879 | -118.0159 | 52.794 | Reinforced
GWD 19160 | Girth Weld |  | 79991.99 | 19.8 | 0.25 | 35000 | ERW | 8.625 | 600 | [10 empty] | AGM 18 | 25473.4 | Estimated Valve 109 | 3149.15 | 21.55 | 19.8 | 17.87 | 21.55 | 19.8 | 19160 | 21.86 | 21.39 | 33.8791 | -118.0159 | 52.318 | Reinforced
GWD 19170 | Girth Weld |  | 80011.79 | 21.86 | 0.25 | 35000 | ERW | 8.625 | 600 | [10 empty] | AGM 18 | 25493.19 | Estimated Valve 109 | 3129.35 | 19.8 | 21.86 | 21.55 | 19.8 | 21.86 | 19170 | 21.39 | 21.17 | 33.8791 | -118.0159 | 52.155 | Reinforced
GWD 19180 | Girth Weld |  | 80033.65 | 21.39 | 0.25 | 35000 | ERW | 8.625 | 600 | [10 empty] | AGM 18 | 25515.06 | Estimated Valve 109 | 3107.49 | 21.86 | 21.39 | 19.8 | 21.86 | 21.39 | 19180 | 21.17 | 19.82 | 33.8792 | -118.0159 | 52.209 | Reinforced
GWD 19190 | Girth Weld |  | 80055.04 | 21.17 | 0.25 | 35000 | ERW | 8.625 | 600 | [10 empty] | AGM 18 | 25536.45 | Estimated Valve 109 | 3086.1 | 21.39 | 21.17 | 21.86 | 21.39 | 21.17 | 19190 | 19.82 | 20.41 | 33.8792 | -118.0159 | 52.05 | Reinforced
GWD 19200 | Girth Weld |  | 80076.21 | 19.82 | 0.25 | 35000 | ERW | 8.625 | 600 | [10 empty] | AGM 18 | 25557.62 | Estimated Valve 109 | 3064.93 | 21.17 | 19.82 | 21.39 | 21.17 | 19.82 | 19200 | 20.41 | 19.23 | 33.8793 | -118.0159 | 51.681 | Reinforced
GWD 19210 | Girth Weld |  | 80096.03 | 20.41 | 0.25 | 35000 | ERW | 8.625 | 600 | [10 empty] | AGM 18 | 25577.43 | Estimated Valve 109 | 3045.11 | 19.82 | 20.41 | 21.17 | 19.82 | 20.41 | 19210 | 19.23 | 20.77 | 33.8794 | -118.0159 | 51.398 | Reinforced
GWD 19220 | Girth Weld |  | 80116.44 | 19.23 | 0.25 | 35000 | ERW | 8.625 | 600 | [10 empty] | AGM 18 | 25597.84 | Estimated Valve 109 | 3024.7 | 20.41 | 19.23 | 19.82 | 20.41 | 19.23 | 19220 | 20.77 | 20.65 | 33.8794 | -118.0159 | 51.239 | Reinforced
GWD 19230 | Girth Weld |  | 80135.66 | 20.77 | 0.25 | 35000 | ERW | 8.625 | 600 | [10 empty] | AGM 18 | 25617.07 | Estimated Valve 109 | 3005.48 | 19.23 | 20.77 | 20.41 | 19.23 | 20.77 | 19230 | 20.65 | 16.17 | 33.8795 | -118.0159 | 51.083 | Reinforced
GWD 19240 | Girth Weld |  | 80156.44 | 20.65 | 0.25 | 35000 | ERW | 8.625 | 600 | [10 empty] | AGM 18 | 25637.84 | Estimated Valve 109 | 2984.7 | 20.77 | 20.65 | 19.23 | 20.77 | 20.65 | 19240 | 16.17 | 13.65 | 33.8795 | -118.0159 | 50.982 | Reinforced
GWD 19250 | Girth Weld |  | 80177.09 | 16.17 | 0.25 | 35000 | ERW | 8.625 | 600 | [10 empty] | AGM 18 | 25658.49 | Estimated Valve 109 | 2964.05 | 20.65 | 16.17 | 20.77 | 20.65 | 16.17 | 19250 | 13.65 | 14.99 | 33.8796 | -118.0159 | 50.74 | Reinforced
GWD 19260 | Girth Weld |  | 80193.26 | 13.65 | 0.25 | 35000 | ERW | 8.625 | 600 | [10 empty] | AGM 18 | 25674.66 | Estimated Valve 109 | 2947.88 | 16.17 | 13.65 | 20.65 | 16.17 | 13.65 | 19260 | 14.99 | 18.45 | 33.8796 | -118.0159 | 50.622 | Reinforced
GWD 19270 | Girth Weld |  | 80206.91 | 14.99 | 0.25 | 35000 | ERW | 8.625 | 600 | [10 empty] | AGM 18 | 25688.31 | Estimated Valve 109 | 2934.23 | 13.65 | 14.99 | 16.17 | 13.65 | 14.99 | 19270 | 18.45 | 17.2 | 33.8797 | -118.0159 | 50.683 | Reinforced
GWD 19280 | Girth Weld |  | 80221.9 | 18.45 | 0.25 | 35000 | ERW | 8.625 | 600 | [10 empty] | AGM 18 | 25703.31 | Estimated Valve 109 | 2919.24 | 14.99 | 18.45 | 13.65 | 14.99 | 18.45 | 19280 | 17.2 | 20.66 | 33.8797 | -118.0159 | 50.773 | Reinforced
GWD 19290 | Girth Weld |  | 80240.36 | 1.32 | 0.25 | 35000 | ERW | 8.625 | 600 | [10 empty] | AGM 18 | 25721.76 | Estimated Valve 109 | 2900.78 | 18.45 | 17.2 | 14.99 | 18.45 | 17.2 | 19290 | 20.66 | 18.69 | 33.8798 | -118.0159 | 50.615 | Reinforced
DNT 8 | Deformation |  | 80241.68 | 8.79 | 0.25 | 35000 | ERW | 8.625 | 600 | 2.622 | 0.226 | 13.039 | 1.736 | 6:18 | [5 empty] | AGM 18 | 25723.09 | Estimated Valve 109 | 2899.46 | 1.32 | 15.88 | 14.99 | 18.45 | 17.2 | 19290 | 20.66 | 18.69 | 33.8798 | -118.0159 | 50.602
DNT 9 | Deformation |  | 80250.47 | 7.09 | 0.25 | 35000 | ERW | 8.625 | 600 | 2.5539 | 0.22 | 12.151 | 1.797 | 3:29 | [5 empty] | AGM 18 | 25731.87 | Estimated Valve 109 | 2890.67 | 10.11 | 7.09 | 14.99 | 18.45 | 17.2 | 19290 | 20.66 | 18.69 | 33.8798 | -118.0159 | 50.528
GWD 19300 | Girth Weld |  | 80257.56 | 20.66 | 0.25 | 35000 | ERW | 8.625 | 600 | [10 empty] | AGM 18 | 25738.96 | Estimated Valve 109 | 2883.58 | 17.2 | 20.66 | 18.45 | 17.2 | 20.66 | 19300 | 18.69 | 19.29 | 33.8798 | -118.0159 | 50.492 | Reinforced
GWD 19310 | Girth Weld |  | 80278.22 | 18.69 | 0.25 | 35000 | ERW | 8.625 | 600 | [10 empty] | AGM 18 | 25759.63 | Estimated Valve 109 | 2862.92 | 20.66 | 18.69 | 17.2 | 20.66 | 18.69 | 19310 | 19.29 | 20.45 | 33.8799 | -118.0159 | 50.344 | Reinforced
GWD 19320 | Girth Weld |  | 80296.91 | 19.29 | 0.25 | 35000 | ERW | 8.625 | 600 | [10 empty] | AGM 18 | 25778.31 | Estimated Valve 109 | 2844.23 | 18.69 | 19.29 | 20.66 | 18.69 | 19.29 | 19320 | 20.45 | 19.06 | 33.8799 | -118.0159 | 50.323 | Reinforced
GWD 19330 | Girth Weld |  | 80316.2 | 20.45 | 0.25 | 35000 | ERW | 8.625 | 600 | [10 empty] | AGM 18 | 25797.6 | Estimated Valve 109 | 2824.94 | 19.29 | 20.45 | 18.69 | 19.29 | 20.45 | 19330 | 19.06 | 19.8 | 33.88 | -118.0159 | 50.11 | Reinforced
GWD 19340 | Girth Weld |  | 80336.65 | 19.06 | 0.25 | 35000 | ERW | 8.625 | 600 | [10 empty] | AGM 18 | 25818.05 | Estimated Valve 109 | 2804.49 | 20.45 | 19.06 | 19.29 | 20.45 | 19.06 | 19340 | 19.8 | 10.13 | 33.88 | -118.0159 | 50.005 | Reinforced
GWD 19350 | Girth Weld |  | 80355.71 | 19.8 | 0.25 | 35000 | ERW | 8.625 | 600 | [10 empty] | AGM 18 | 25837.11 | Estimated Valve 109 | 2785.43 | 19.06 | 19.8 | 20.45 | 19.06 | 19.8 | 19350 | 10.13 | 9.15 | 33.8801 | -118.0159 | 49.982 | Reinforced
GWD 19360 | Girth Weld |  | 80375.51 | 10.13 | 0.25 | 35000 | ERW | 8.625 | 600 | [10 empty] | AGM 18 | 25856.91 | Estimated Valve 109 | 2765.64 | 19.8 | 10.13 | 19.06 | 19.8 | 10.13 | 19360 | 9.15 | 16.17 | 33.8801 | -118.0159 | 50.029 | Reinforced
GWD 19370 | Girth Weld |  | 80385.63 | 9.15 | 0.25 | 35000 | ERW | 8.625 | 600 | [10 empty] | AGM 18 | 25867.04 | Estimated Valve 109 | 2755.51 | 10.13 | 9.15 | 19.8 | 10.13 | 9.15 | 19370 | 16.17 | 16.51 | 33.8802 | -118.0159 | 50.185 | Reinforced
GWD 19380 | Girth Weld |  | 80394.78 | 16.17 | 0.25 | 35000 | ERW | 8.625 | 600 | [10 empty] | AGM 18 | 25876.19 | Estimated Valve 109 | 2746.36 | 9.15 | 16.17 | 10.13 | 9.15 | 16.17 | 19380 | 16.51 | 21.55 | 33.8802 | -118.0159 | 50.334 | Reinforced
GWD 19390 | Girth Weld |  | 80410.95 | 16.51 | 0.25 | 35000 | ERW | 8.625 | 600 | [10 empty] | AGM 18 | 25892.35 | Estimated Valve 109 | 2730.19 | 16.17 | 16.51 | 9.15 | 16.17 | 16.51 | 19390 | 21.55 | 20.88 | 33.8802 | -118.0159 | 50.421 | Reinforced
GWD 19400 | Girth Weld |  | 80427.46 | 21.55 | 0.25 | 35000 | ERW | 8.625 | 600 | [10 empty] | AGM 18 | 25908.86 | Estimated Valve 109 | 2713.68 | 16.51 | 21.55 | 16.17 | 16.51 | 21.55 | 19400 | 20.88 | 21.59 | 33.8803 | -118.0159 | 50.386 | Reinforced
GWD 19410 | Girth Weld |  | 80449.01 | 20.88 | 0.25 | 35000 | ERW | 8.625 | 600 | [10 empty] | AGM 18 | 25930.41 | Estimated Valve 109 | 2692.13 | 21.55 | 20.88 | 16.51 | 21.55 | 20.88 | 19410 | 21.59 | 19.48 | 33.8803 | -118.0159 | 50.125 | Reinforced
GWD 19420 | Girth Weld |  | 80469.89 | 21.59 | 0.25 | 35000 | ERW | 8.625 | 600 | [10 empty] | AGM 18 | 25951.29 | Estimated Valve 109 | 2671.25 | 20.88 | 21.59 | 21.55 | 20.88 | 21.59 | 19420 | 19.48 | 19.23 | 33.8804 | -118.0159 | 49.866 | Reinforced
GWD 19430 | Girth Weld |  | 80491.48 | 19.48 | 0.25 | 35000 | ERW | 8.625 | 600 | [10 empty] | AGM 18 | 25972.88 | Estimated Valve 109 | 2649.66 | 21.59 | 19.48 | 20.88 | 21.59 | 19.48 | 19430 | 19.23 | 21.04 | 33.8805 | -118.0159 | 49.693 | Reinforced
GWD 19440 | Girth Weld |  | 80510.96 | 19.23 | 0.25 | 35000 | ERW | 8.625 | 600 | [10 empty] | AGM 18 | 25992.36 | Estimated Valve 109 | 2630.18 | 19.48 | 19.23 | 21.59 | 19.48 | 19.23 | 19440 | 21.04 | 15.76 | 33.8805 | -118.0159 | 49.517 | Reinforced
GWD 19450 | Girth Weld |  | 80530.19 | 21.04 | 0.25 | 35000 | ERW | 8.625 | 600 | [10 empty] | AGM 18 | 26011.59 | Estimated Valve 109 | 2610.95 | 19.23 | 21.04 | 19.48 | 19.23 | 21.04 | 19450 | 15.76 | 1.07 | 33.8806 | -118.0159 | 49.071
GWD 19460 | Girth Weld |  | 80551.23 | 15.76 | 0.25 | 35000 | ERW | 8.625 | 600 | [10 empty] | AGM 18 | 26032.63 | Estimated Valve 109 | 2589.91 | 21.04 | 15.76 | 19.23 | 21.04 | 15.76 | 19460 | 1.07 | 20752.14 | 33.8806 | -118.016 | 48.367
GWD 19470 | Girth Weld |  | 80566.99 | 1.07 | 0.25 | 35000 | ERW | 8.625 | 600 | [10 empty] | AGM 18 | 26048.39 | Estimated Valve 109 | 2574.15 | 15.76 | 1.07 | 21.04 | 15.76 | 1.07 | 19470 | 20752.14 | 37.55 | 33.8807 | -118.016 | 47.909
GWD 19480 | Girth Weld |  | 80568.06 | 2573.08 | 0.25 | 35000 | ERW | 8.625 | 600 | [10 empty] | AGM 18 | 26049.47 | Estimated Valve 109 | 2573.08 | 1.07 | 20752.14 | 15.76 | 1.07 | 20752.14 | 19480 | 37.55 | 42.15 | 33.8807 | -118.016 | 47.902 | Start Bad Data¦End Section CSFM 39
VLV 5 | Valve |  | 83141.14 | 18179.06 | 0.25 | 35000 | ERW | 8.625 | 600 | [10 empty] | AGM 18 | 28622.55 | MLV 3 | 18967.68 | 2573.08 | 18179.06 | 15.76 | 1.07 | 20752.14 | 19480 | 37.55 | 42.15 | 33.8847 | -118.0199 | 55.852 | Estimated Valve 109